SAN FRANCISCO | SAN FRANCISCO | SF P-1105 | 22331105 | FUSE | 5681 | 20241214 | 607 | 20241214 | 1252 | 2653194 | 405 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 252 | 102060 | 37.7302 | -122.3746 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0145678 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1998004 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1108 | 22011108 | TRANSFORMER | 314238546939 | 20241214 | 609 | 20241214 | 1753 | 2653221 | 704 | Transformer only | Environmental/External | Water | 24 | 15367 | 37.7722 | -122.4943 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Broken- wire on ground | 24-0145407 | OH | Sus | 0 | BAY AREA | DEC | Open Circuit | 0 | No | No | Yes | 1997729 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF N-0408 | 22280408 | SWITCH | 40085 | 20241214 | 942 | 20241214 | 1932 | 2656658 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 86730 | 37.7527 | -122.4668 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 24-0146052 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1998390 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF L-1102 | 22261102 | FUSE | 97039 | 20241214 | 1006 | 20241214 | 2053 | 2660345 | 647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 327 | 211569 | 37.7586 | -122.508 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0146079 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1998422 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | YOSEMITE-0401 | 22490401 | TRANSFORMER | 100000176050 | 20241214 | 1011 | 20241214 | 2157 | 2657384 | 706 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 7060 | 37.7353 | -122.4019 | Yes | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Broken- wire on object | 24-0146036 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 1998375 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF P-1105 | 22331105 | RECLOSER | 13303 | 20241214 | 1043 | 20241214 | 1758 | 2659590 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 444 | 121536 | 37.7237 | -122.3909 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145829 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 1998162 | 0 | Non-EPSS | N | 2024 | A & GRD
SAN FRANCISCO | SAN FRANCISCO | SF Z-1120 | 22871120 | INTERRUPTER | 18986 | 20241214 | 1129 | 20241215 | 1341 | 2658416 | 1572 | Distribution Circuit | Equipment Failure/Involved | Underground | 747 | 189286 | 37.7898 | -122.3912 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0145749 | UG | Sus | 35605423 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998081 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF H MARTIN-1102 | 22101102 | RECLOSER | 13521 | 20241214 | 1213 | 20241214 | 1720 | 2656191 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1020 | 75486 | 37.7433 | -122.4692 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145643 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | Yes | Yes | 1997968 | 0 | Non-EPSS | N | 2024 | NONE
SAN FRANCISCO | SAN FRANCISCO | SF K-0401 | 22130401 | JUMPER | OJ @ 11TH AVE & BALBOA | 20241214 | 1318 | 20241214 | 1759 | 2659231 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 15736 | 37.7771 | -122.4692 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0145873 | OH | Sus | 0 | BAY AREA | DEC | Force Out | 0 | No | No | No | 1998207 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF L-1102 | 22261102 | TRANSFORMER | 314267246203 | 20241214 | 1503 | 20241214 | 2134 | 2660232 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 7820 | 37.7521 | -122.4837 | Yes | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146094 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1998437 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF L-1102 | 22261102 | TRANSFORMER | 314264046201 | 20241214 | 1505 | 20241215 | 913 | 2660231 | 1088 | Transformer only | Unknown Cause | Patrol - found nothing | 22 | 23936 | 37.7521 | -122.4848 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0146095 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 1998439 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF A-1116 | 22031116 | TRANSFORMER | 314541446349 | 20241215 | 944 | 20241215 | 1413 | 2661078 | 269 | Transformer only | Equipment Failure/Involved | Overhead | 41 | 11029 | 37.7578 | -122.3899 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146212 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998561 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF Z-1120 | 22871120 | SWITCH | 662944 | 20241215 | 1345 | 20241215 | 1351 | 2661691 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 30 | 37.7901 | -122.3889 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0145749 | UG | Sus | 35605423 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998702 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF H MARTIN-1105 | 22101105 | OTHER | BURNED OPEN TAP 1/P/W 548433 | 20241215 | 1734 | 20241216 | 1029 | 2662002 | 1015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4546 | 1598499 | 37.7045 | -122.4259 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146411 | OH | Sus | 46416239 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | Yes | 1998774 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF H MARTIN-1107 | 22101107 | OTHER | WIRE DOWN 159 GUTEENBURG | 20241215 | 1856 | 20241216 | 255 | 2662075 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 65391 | 37.7111 | -122.4435 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146440 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | Yes | 1998801 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF Z-1120 | 22871120 | TRANSFORMER | T3334 | 20241216 | 919 | 20241216 | 2142 | 2662354 | 743 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 5201 | 37.7882 | -122.3889 | No | Overcast-Rain;32-90 F | Transformer (UG) | Broken | 24-0146553 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998939 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1108 | 22011108 | TRANSFORMER | 314283447023 | 20241216 | 1016 | 20241216 | 1516 | 2662777 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 80 | 24000 | 37.7748 | -122.4789 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0146586 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998965 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF G-0403 | 22090403 | TRANSFORMER | 314342247312 | 20241216 | 1039 | 20241216 | 1649 | 2662838 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2960 | 37.7831 | -122.4588 | No | Overcast-Drizzle;32-90 F | Transformer | Deteriorated | 24-0146602 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998985 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF G-0403 | 22090403 | TRANSFORMER | 314342447334 | 20241216 | 1042 | 20241216 | 1656 | 2662880 | 374 | Transformer only | Equipment Failure/Involved | Overhead | 82 | 30668 | 37.7837 | -122.4589 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0146599 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998981 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF Y-1107 | 22801107 | TRANSFORMER | 314338447318 | 20241216 | 1051 | 20241216 | 1655 | 2662860 | 364 | Transformer only | Equipment Failure/Involved | Overhead | 100 | 36400 | 37.7833 | -122.4602 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0146600 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1998983 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF N-1102 | 22281102 | TRANSFORMER | 314316846574 | 20241217 | 1400 | 20241217 | 1600 | 2664344 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 72 | 8640 | 37.7627 | -122.4672 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0146846 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999337 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF J-1107 | 22221107 | OCB | 1107/22 | 20241218 | 318 | 20241218 | 702 | 2664711 | 224 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 224 | 37.7934 | -122.4038 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0146899 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999403 | 0 | Non-EPSS | N | 2024 | UNK
SAN FRANCISCO | SAN FRANCISCO | PORTOLA-0401 | 22610401 | OCB | 401/2 | 20241218 | 326 | 20241218 | 530 | 2664700 | 124 | Distribution Circuit | Equipment Failure/Involved | Underground | 1202 | 95680 | 37.7453 | -122.4534 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0146896 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999399 | 0 | Non-EPSS | N | 2024 | A & GRD
SAN FRANCISCO | SAN FRANCISCO | DALY CITY-1109 | 22641109 | TRANSFORMER | 314377245059 | 20241218 | 1125 | 20241218 | 1609 | 2665151 | 284 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4260 | 37.7215 | -122.4453 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146989 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999626 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF J-1108 | 22221108 | INTERRUPTER | 590788 | 20241219 | 400 | 20241219 | 1146 | 2665640 | 384 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1678 | 37.7906 | -122.406 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0147069 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 1999724 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1124 | 22011124 | INTERRUPTER | 99871 | 20241221 | 251 | 20241221 | 1748 | 2667150 | 753 | Distribution Circuit | Equipment Failure/Involved | Underground | 719 | 276687 | 37.7632 | -122.424 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 24-0147285 | UG | Sus | 46423590 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000198 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1128 | 22011128 | FUSE | 11924 | 20241221 | 553 | 20241221 | 2016 | 2667179 | 599 | Distribution Circuit | Equipment Failure/Involved | Underground | 235 | 76996 | 37.7742 | -122.4202 | No | Overcast-Drizzle;32-90 F | Conductor- Underground | Deteriorated | 24-0147307 | UG | Sus | 35606980 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000246 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF P-1105 | 22331105 | TRANSFORMER | 314541945192 | 20241222 | 1230 | 20241222 | 1528 | 2667759 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2314 | 37.7261 | -122.3885 | No | Overcast;32-90 F | Transformer | Leaking | 24-0147391 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000375 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF K-1101 | 22131101 | FUSE | 48893 | 20241223 | 40 | 20241223 | 758 | 2667965 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 18305 | 37.7741 | -122.4939 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147436 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2000420 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF L SUB | 2226 | OCB | 403/12 | 20241223 | 612 | 20241223 | 2153 | 2667990 | 941 | Distribution Circuit | Equipment Failure/Involved | Underground | 442 | 106232 | 37.73 | -122.4712 | No | Overcast-Fog;32-90 F | Conductor- Underground | Broken | 24-0147442 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000428 | 0 | Non-EPSS | N | 2024 | & GRD
SAN FRANCISCO | SAN FRANCISCO | DALY CITY-1106 | 22641106 | TRANSFORMER | 314228645777 | 20241223 | 1837 | 20241223 | 1859 | 2668576 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 220 | 37.7402 | -122.4966 | No | Overcast;32-90 F | Fuse | Broken | 24-0147512 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000560 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF Y-1127 | 22801127 | TRANSFORMER | 314461247705 | 20241224 | 232 | 20241224 | 623 | 2668717 | 231 | Transformer only | Equipment Failure/Involved | Overhead | 195 | 45045 | 37.7947 | -122.418 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147556 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2000609 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1110 | 22011110 | TRANSFORMER | 314234646487 | 20241224 | 338 | 20241224 | 739 | 2668772 | 241 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 4579 | 37.7598 | -122.495 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0147554 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000606 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1128 | 22011128 | TRANSFORMER | MTR#MH5912 | 20241224 | 455 | 20241224 | 505 | 2668811 | 10 | Transformer only | Company Initiated | Return Circuit Normal | 9 | 90 | 37.7737 | -122.4213 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0147307 | UG | Sus | 35606980 | BAY AREA | DEC | None | 0 | No | No | No | 2000607 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF N-1102 | 22281102 | TRANSFORMER | 314295047232 | 20241224 | 845 | 20241224 | 944 | 2668981 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 34 | 2006 | 37.7807 | -122.475 | No | Overcast-Rain;32-90 F |  |  | 24-0147609 | OH | Sus | 0 | BAY AREA | DEC | None | 0 | No | No | No | 2000665 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF X-1110 | 22011110 | TRANSFORMER | 314247246375 | 20241224 | 1126 | 20241224 | 1437 | 2669185 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 6876 | 37.7566 | -122.4907 | No | Partly Cloudy-Drizzle;32-90 F | Other | Broken | 24-0147656 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000715 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF E-0409 | 22070409 | OCB | E409/2 | 20241224 | 1217 | 20241224 | 1942 | 2669225 | 445 | Distribution Circuit | Equipment Failure/Involved | Underground | 938 | 54610 | 37.7595 | -122.4203 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0147651 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000710 | 0 | Non-EPSS | N | 2024 | NONE
SAN FRANCISCO | SAN FRANCISCO | SF Y-1120 | 22801120 | TRANSFORMER | 314417447880 | 20241225 | 1003 | 20241225 | 1433 | 2669604 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 9450 | 37.7992 | -122.4335 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0147722 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000783 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF H MARTIN-1108 | 22101108 | TRANSFORMER | 314464345108 | 20241225 | 2104 | 20241226 | 822 | 2669764 | 678 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 20340 | 37.7232 | -122.415 | No | Overcast-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0147755 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2000815 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | FY-4 (SF Y-1254) TIE | 22801254 | TRANSFORMER | T1321 | 20241227 | 1704 | 20241227 | 1856 | 2670941 | 112 | Transformer only | Equipment Failure/Involved | Underground | 49 | 5488 | 37.802 | -122.4197 | No | Overcast-Drizzle;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0147982 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001113 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF G-0406 | 22090406 | OCB | 0406/22 | 20241227 | 2142 | 20241229 | 149 | 2671097 | 1687 | Distribution Circuit | 3rd Party | Vehicle | 1172 | 334722 | 37.782 | -122.4401 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147993 | OH | Sus | 35607761 | BAY AREA | DEC | Line to Ground | 0 | No | Yes | No | 2001124 | 0 | Non-EPSS | N | 2024 | UNKNOWN
SAN FRANCISCO | SAN FRANCISCO | SF A-1103 | 22031103 | FUSE | 12679 | 20241228 | 912 | 20241228 | 1332 | 2671362 | 260 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 260 | 37.7506 | -122.3824 | No | Overcast-Fog;32-90 F |  |  | 24-0148044 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2001182 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF K-0411 | 22130411 | TRANSFORMER | 314214147068 | 20241228 | 935 | 20241228 | 1705 | 2671246 | 450 | Transformer only | Equipment Failure/Involved | Overhead | 47 | 21150 | 37.7756 | -122.5028 | No | Overcast-Fog;32-90 F | Transformer | Broken | 24-0148031 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001168 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF K-0410 | 22130410 | TRANSFORMER | 314354647036 | 20241228 | 1142 | 20241229 | 144 | 2671312 | 842 | Transformer only | 3rd Party | Vehicle | 34 | 28628 | 37.7756 | -122.4544 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0148037 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001176 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF H MARTIN-1109 | 22101109 | OCB | 1109/22 | 20241228 | 1632 | 20241228 | 2222 | 2671451 | 210 | Distribution Circuit | Equipment Failure/Involved | Underground | 4875 | 259488 | 37.7041 | -122.4088 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0148057 | UG | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001198 | 0 | Non-EPSS | N | 2024 | B & GRD INST
SAN FRANCISCO | SAN FRANCISCO | SF A-1103 | 22031103 | FUSE | 12679 | 20241229 | 856 | 20241229 | 1330 | 2671811 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 274 | 37.7506 | -122.3824 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0148124 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2001272 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF P-1101 | 22331101 | FUSE | 5563 | 20241229 | 1017 | 20241229 | 1415 | 2671749 | 238 | Distribution Circuit | Animal | Bird found | 34 | 8092 | 37.7472 | -122.3966 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0148133 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2001281 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF A-1103 | 22031103 | FUSE | 12679 | 20241230 | 846 | 20241230 | 935 | 2672302 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 49 | 37.7506 | -122.3824 | No | Partly Cloudy;32-90 F |  |  | 24-0148193 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 2001407 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF L-0403 | 22260403 | OTHER | TEMP GEN FEEDING M7145 | 20241230 | 926 | 20241230 | 1317 | 2672586 | 24 | Distribution Circuit | Company Initiated | Return Circuit Normal | 109 | 2035 | 37.7198 | -122.4744 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0147482 | UG | Sus | 31720734 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001466 | 0 | Non-EPSS | N | 2024
SAN FRANCISCO | SAN FRANCISCO | SF K-1101 | 22131101 | OCB | 1101/2 | 20241231 | 1517 | 20241231 | 1713 | 2673362 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4428 | 366276 | 37.777 | -122.4839 | No | Partly Cloudy;32-90 F | Switch (OH) | Failed/Faulted | 24-0148316 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001614 | 0 | Non-EPSS | N | 2024 | C & GRD TIME
SAN FRANCISCO | SAN FRANCISCO | SF K-1101 | 22131101 | TRANSFORMER | 314246047059 | 20241231 | 2030 | 20241231 | 2140 | 2673514 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 1400 | 37.7755 | -122.4918 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0148346 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001643 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS 2105 | 83182105 | FUSE | 62846 | 20230101 | 126 | 20230102 | 1609 | 1907647 | 1491 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 6400 | 36.9892 | -121.5604 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0004445 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795044 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 15077 | 20230101 | 506 | 20230102 | 138 | 1907811 | 1232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 188496 | 37.3054 | -121.8455 | No | Clear;32-90F | Pole-Wood | Broken | 23-0004286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1794881 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 31166 | 20230101 | 1044 | 20230103 | 129 | 1908262 | 346 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 52293 | 37.0134 | -121.5889 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0004443 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795042 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE 1107 | 83531107 | TRANSFORMER | 316176032400 | 20230101 | 1237 | 20230101 | 1302 | 1907564 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 125 | 37.3823 | -121.817 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0004397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1794992 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2110 | 83242110 | FUSE | 26625 | 20230101 | 1245 | 20230103 | 1945 | 1908505 | 3300 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 3300 | 37.0898 | -121.591 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0004521 | UG | Sus | 35419521 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795121 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS 2107 | 83182107 | TRANSFORMER | 316655018915 | 20230101 | 1826 | 20230103 | 405 | 1910914 | 2019 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 10095 | 37.0136 | -121.6465 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0004948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795555 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2111 | 83242111 | FUSE | 25447 | 20230101 | 1953 | 20230102 | 1335 | 1909120 | 1062 | Distribution Circuit | 3rd Party | Vehicle | 9 | 9558 | 37.1539 | -121.687 | No | Clear;32-90F | Pole-Wood | Broken | 23-0004569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795171 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | SWITCH | 5562 | 20230101 | 2310 | 20230101 | 2318 | 1909361 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 119 | 952 | 37.2377 | -121.8561 | No | Clear;32-90F | Switch (UG) | Normal | 22-0142753 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1795238 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1102 | 82921102 | SWITCH | 63378SW | 20230102 | 1115 | 20230102 | 2132 | 1910017 | 617 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1434 | 37.3207 | -121.9492 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0004747 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795350 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS 2111 | 83432111 | FUSE | 26021 | 20230102 | 1742 | 20230102 | 2042 | 1910468 | 180 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1666 | 163402 | 37.2475 | -121.8556 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0004842 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795444 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT 2110 | 83392110 | TRANSFORMER | 316278931086 | 20230103 | 51 | 20230103 | 1336 | 1910857 | 765 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 4590 | 37.3465 | -121.7808 | No | Clear;32-90 F |  |  | 23-0004944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1795549 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS 1108 | 82831108 | FUSE | 1100SW | 20230103 | 713 | 20230103 | 2025 | s1795626 | 792 | Distribution Circuit | Equipment Failure/Involved | Underground | 184 | 145728 | 37.4196 | -121.856 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0005065 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795626 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE 1108 | 83531108 | TRANSFORMER | T8352 | 20230104 | 44 | 20230104 | 927 | 1912208 | 523 | Transformer only | Unknown Cause | Patrol - found nothing | 13 | 6799 | 37.3696 | -121.8455 | Yes | Clear;32-90F |  |  | 23-0005506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1795984 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315958529183 | 20230104 | 226 | 20230104 | 602 | 1912209 | 216 | Transformer only | Unknown Cause | Patrol - found nothing | 36 | 7776 | 37.2932 | -121.8906 | Yes | Clear;32-90F |  |  | 23-0005517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1795992 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2104 | 83242104 | FUSE | 31430 | 20230104 | 505 | 20230104 | 2223 | 1912238 | 1038 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 34881 | 37.144 | -121.6272 | Yes | Clear;32-90F | Conductor- Underground | Deteriorated | 23-0005670 | UG | Sus | 35419598 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796094 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 41791 | 20230104 | 736 | 20230104 | 1946 | 1912481 | 730 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 27280 | 37.3189 | -121.9634 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0005662 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796087 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS 1109 | 82831109 | RECLOSER | 903328 | 20230104 | 803 | 20230105 | 1743 | 1912610 | 1968 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 235948 | 37.4483 | -121.8461 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0005603 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796051 | 0 | EPSS Ckt | N | 2023 | A- C- GRD & TIME
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | OCB | 2102/2 | 20230104 | 822 | 20230104 | 1510 | 1912645 | 408 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 5874 | 233782 | 37.3036 | -121.8398 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0005602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796050 | 0 | Non-EPSS | N | 2023 | A- B- C- PHASE TIME
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 26345 | 20230104 | 845 | 20230104 | 957 | 1912771 | 72 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 6186 | 37.0179 | -121.5864 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0005704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796119 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 44826 | 20230104 | 920 | 20230105 | 1152 | 1912920 | 1468 | Distribution Circuit | Equipment Failure/Involved | Underground | 271 | 181211 | 37.3208 | -121.842 | Yes | Clear;32-90F | Conductor- Underground | Broken | 23-0005752 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796156 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316078931188 | 20230104 | 938 | 20230104 | 1256 | 1913034 | 198 | Transformer only | Vegetation | Tree - branch fell on line | 24 | 4752 | 37.3487 | -121.8496 | Yes | Clear;32-90F | Secondary | Contaminated | 23-0005717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796128 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316129132830 | 20230104 | 954 | 20230104 | 2144 | 1913083 | 710 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 4260 | 37.394 | -121.8334 | Yes | Clear;32-90F |  |  | 23-0006771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797073 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316091430732 | 20230104 | 958 | 20230105 | 2256 | 1913097 | 2218 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 62104 | 37.3363 | -121.8454 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0007925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798066 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12537 | 20230104 | 1001 | 20230104 | 1515 | 1913123 | 314 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 125 | 39250 | 37.3269 | -121.8307 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796427 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 315989334154 | 20230104 | 1002 | 20230105 | 1407 | 1913115 | 1685 | Transformer only | Equipment Failure/Involved | Overhead | 40 | 67400 | 37.4299 | -121.8838 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0006280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | Yes | 1796585 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2108 | 83242108 | FUSE | 3069 | 20230104 | 1037 | 20230104 | 1507 | 1913266 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 9990 | 37.1606 | -121.6814 | Yes | Clear;32-90F |  |  | 23-0006096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796422 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 405/2 | 20230104 | 1038 | 20230104 | 1526 | 1913282 | 234 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 592 | 164576 | 37.3281 | -121.9025 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796165 | 0 | Non-EPSS | N | 2023 | TIME OC
SAN JOSE | SAN JOSE | SAN JOSE B-1114 | 82261114 | OCB | 1114/2 | 20230104 | 1039 | 20230104 | 1142 | 1913310 | 63 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2431 | 153153 | 37.341 | -121.9017 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796164 | 0 | Non-EPSS | N | 2023 | A B PHSAE
SAN JOSE | SAN JOSE | MC KEE 1112 | 83531112 | TRANSFORMER | 316214731359 | 20230104 | 1043 | 20230105 | 1249 | 1913283 | 1566 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 12528 | 37.3539 | -121.8033 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0007265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797532 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 26883 | 20230104 | 1050 | 20230104 | 1923 | 1917523 | 513 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 12312 | 37.2843 | -121.8352 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796762 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 13053 | 20230104 | 1118 | 20230104 | 1543 | 1913479 | 265 | Distribution Circuit | 3rd Party | Metallic Balloon | 488 | 129320 | 37.2455 | -121.8926 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796434 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE 1103 | 83531103 | TRANSFORMER | 316123032830 | 20230104 | 1141 | 20230104 | 2028 | 1913565 | 527 | Transformer only | Vegetation | Tree - grew into line | 8 | 4216 | 37.394 | -121.8354 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0006520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796817 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS 2103 | 83432103 | TRANSFORMER | C63 | 20230104 | 1155 | 20230104 | 1316 | 1913634 | 81 | Transformer only | Equipment Failure/Involved | Underground | 9 | 729 | 37.2094 | -121.8665 | Yes | Clear;32-90F | Secondary | Broken | 23-0005857 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796241 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | SWITCH | X1902 | 20230104 | 1212 | 20230104 | 1806 | 1913386 | 354 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 1480 | 135165 | 37.397 | -121.872 | Yes | Clear;32-90F | Secondary | Arcing | 23-0005887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1796259 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE 1111 | 83531111 | TRANSFORMER | 316188831797 | 20230104 | 1240 | 20230104 | 1719 | 1913534 | 279 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 3069 | 37.3658 | -121.8124 | Yes | Clear;32-90 F |  |  | 23-0005913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1796279 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316141832725 | 20230104 | 1321 | 20230105 | 1236 | 1914041 | 1395 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 13950 | 37.3911 | -121.829 | Yes | Clear;32-90F | Secondary | Normal | 23-0007174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797458 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 65735 | 20230104 | 1523 | 20230106 | 45 | 1914781 | 2002 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 4004 | 37.307 | -121.8577 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1796445 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS 2106 | 83182106 | INTERRUPTER | 32358 | 20230104 | 1635 | 20230106 | 1040 | 1915336 | 2525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 6975 | 36.9853 | -121.5469 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796604 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316188831797 | 20230104 | 1719 | 20230105 | 1815 | 1915895 | 1496 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 11 | 16456 | 37.3658 | -121.8124 | Yes | Clear;32-90 F | Transformer | Together | 23-0006543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796841 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS 2101 | 83182101 | FUSE | 25341 | 20230104 | 1742 | 20230105 | 1443 | 1916861 | 1261 | Distribution Circuit | Vegetation | Tree - branch fell on line | 307 | 86039 | 37.0618 | -121.5875 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796706 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS 2101 | 83432101 | FUSE | 40690 | 20230104 | 1751 | 20230104 | 2027 | 1916379 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 6298 | 37.2093 | -121.8461 | Yes | Clear;32-90F |  |  | 23-0006474 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796771 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 12179 | 20230104 | 1815 | 20230104 | 2135 | 1916750 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 14800 | 37.3022 | -121.8905 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796880 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6927 | 20230104 | 1916 | 20230104 | 2108 | 1917601 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 336 | 37.267 | -121.8786 | Yes | Clear;32-90F |  |  | 23-0006599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1796900 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12537 | 20230104 | 1916 | 20230104 | 2015 | 1917534 | 59 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 125 | 7375 | 37.3269 | -121.8307 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0006539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796837 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2109 | 83242109 | FUSE | 43067 | 20230104 | 1942 | 20230104 | 2150 | 1917795 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 384 | 37.1027 | -121.5858 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797000 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | JUMPER | OPEN JUMPERS HS OF 922177 & 894413 | 20230104 | 2027 | 20230105 | 1431 | 1918219 | 1084 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 28184 | 37.4042 | -121.8373 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0007296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797558 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS SUB | 8343 | OCB | 1113/2 | 20230104 | 2126 | 20230105 | 6 | 1918832 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3342 | 422314 | 37.2332 | -121.9012 | Yes | Clear;32-90F |  |  | 23-0006693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1796994 | 0 | Non-EPSS | N | 2023 | A & B PHASE TIME OC
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 40690 | 20230104 | 2246 | 20230108 | 1536 | s1797771 | 904 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 61261 | 37.2093 | -121.8461 | Yes | Clear;32-90 F | Elbow | Failed/Faulted | 23-0007549 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797771 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 17733 | 20230105 | 48 | 20230105 | 932 | 1920089 | 524 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 6288 | 37.2227 | -121.8748 | Yes | Clear;32-90F |  |  | 23-0007153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797437 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 40333 | 20230105 | 52 | 20230105 | 1420 | 1920098 | 808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 25048 | 37.2317 | -121.8715 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0007543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797758 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17557 | 20230105 | 111 | 20230105 | 437 | 1920172 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 8436 | 37.3808 | -121.809 | Yes | Clear;32-90F |  |  | 23-0006979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1797282 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1101 | 82261101 | FUSE | 72123 | 20230105 | 129 | 20230105 | 653 | 1920237 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 10368 | 37.3353 | -121.8979 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797217 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE 2113 | 82952113 | FUSE | 33856 | 20230105 | 300 | 20230106 | 545 | 1920441 | 1605 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 41085 | 37.2384 | -121.8309 | Yes | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0006998 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797300 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230105 | 340 | 20230105 | 1311 | 1921114 | 571 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 16559 | 37.1602 | -121.666 | Yes | Clear;32-90 F |  |  | 23-0007300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797563 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2105 | 83242105 | OTHER | WIRE DOWN 15155 SYCAMORE DR | 20230105 | 405 | 20230106 | 1946 | 1920555 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 38257 | 37.0894 | -121.6615 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797868 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR332 | 20230105 | 516 | 20230107 | 1005 | 1920637 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 264488 | 37.3494 | -121.6124 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797296 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20230105 | 714 | 20230106 | 219 | 1920243 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 125696 | 37.1869 | -121.8177 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0007031 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797332 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 6813 | 20230105 | 720 | 20230106 | 549 | 1922212 | 1349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2698 | 37.1562 | -121.8444 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797657 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315966231427 | 20230105 | 829 | 20230105 | 1616 | 1920042 | 467 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4203 | 37.355 | -121.889 | Yes | Clear;32-90 F | Secondary | Broken | 23-0007346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797606 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 28873 | 20230105 | 1123 | 20230105 | 1129 | 1921944 | 6 | Distribution Circuit | Animal | Squirrel | 40 | 240 | 37.3189 | -121.9535 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797588 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS 2104 | 83182104 | FUSE | 4233 | 20230105 | 1233 | 20230107 | 209 | 1922234 | 2256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 11280 | 36.9617 | -121.5384 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798390 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 316300230777 | 20230105 | 1456 | 20230106 | 1526 | 1922862 | 1470 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 4410 | 37.3379 | -121.7733 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0007607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1797814 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL 2106 | 83242106 | TRANSFORMER | 316878620766 | 20230105 | 1515 | 20230105 | 1816 | 1922890 | 181 | Transformer only | Vegetation | Tree - grew into line | 4 | 724 | 37.0654 | -121.5705 | Yes | Heavy Rain-Clear;32-90 F | Conductor- Overhead | Normal | 23-0007617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797824 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13063 | 20230105 | 1813 | 20230105 | 1927 | 1923500 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 3256 | 37.3681 | -121.8253 | Yes | Clear;32-90 F |  |  | 23-0007874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798037 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 26671 | 20230105 | 1813 | 20230106 | 1941 | 1923499 | 1528 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 16808 | 37.4454 | -121.8434 | Yes | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0008043 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798174 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3747 | 20230105 | 1836 | 20230106 | 1039 | 1924624 | 963 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 28540 | 37.087 | -121.655 | Yes | Clear;32-90 F |  |  | 23-0008201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798273 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 8863 | 20230105 | 1919 | 20230105 | 2125 | 1922198 | 126 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 7 | 882 | 37.3786 | -121.8301 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798038 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1106 | 82261106 | SWITCH | 64652SW | 20230105 | 1930 | 20230105 | 2134 | 1923746 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 298 | 36952 | 37.3243 | -121.8994 | Yes | Clear;32-90 F |  |  | 23-0007963 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798095 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | JUMPER | OJ 5 POLES SS OF CGC#3513 | 20230106 | 7 | 20230106 | 1430 | s1798190 | 863 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1726 | 0 | 0 | No | Clear;32-90 F | Jumper | Broken | 23-0008067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1798190 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 316188434160 | 20230106 | 17 | 20230106 | 2110 | 1925263 | 1253 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2506 | 37.4313 | -121.8142 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0008475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798409 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1114 | 82261114 | TRANSFORMER | T14688 | 20230106 | 745 | 20230106 | 1316 | 1924374 | 331 | Transformer only | Unknown Cause | Patrol - found nothing | 14 | 4634 | 37.3312 | -121.8835 | No | Clear;32-90 F |  |  | 23-0008344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1798349 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 72723 | 20230106 | 1135 | 20230106 | 1216 | 1924220 | 41 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 19 | 779 | 37.0303 | -121.5774 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0008248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1798297 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4063 | 20230106 | 1240 | 20230106 | 1331 | 1924821 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 153 | 37.0565 | -121.5931 | No | Clear;32-90 F |  |  | 23-0008299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798324 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315668129608 | 20230106 | 1523 | 20230106 | 1707 | 1925223 | 104 | Transformer only | Vegetation | Tree - grew into line | 9 | 936 | 37.3041 | -121.9903 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798398 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | JUMPER | 316146527435 | 20230107 | 1004 | 20230107 | 2128 | s1797548 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8910 | 37.2459 | -121.8249 | Yes | Clear;32-90 F | Pole-Wood | Normal | 23-0007283 | OH | Sus | 45615403 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1797548 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 20230107 | 1047 | 20230107 | 1301 | 1926407 | 134 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 9246 | 37.3568 | -121.5253 | Yes | Clear;32-90 F |  |  | 23-0008731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798614 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315811830770 | 20230107 | 1504 | 20230107 | 1611 | 1926853 | 67 | Transformer only | Vegetation | Tree - fell into line | 13 | 871 | 37.3368 | -121.9415 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0008863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | Yes | 1798722 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20230107 | 1531 | 20230108 | 1810 | 1926500 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 3342 | 254816 | 37.2332 | -121.9012 | Yes | Clear;32-90 F | Secondary | Normal | 23-0008879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1798733 | 0 | Non-EPSS | N | 2023 | PHAST INST///TIME
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 238583 | 20230107 | 1542 | 20230108 | 1223 | 1927005 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 26061 | 37.3317 | -121.9265 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0009011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798839 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 408/2 | 20230107 | 1607 | 20230107 | 1726 | 1927108 | 79 | Distribution Circuit | Vegetation | Tree - branch fell on line | 640 | 50560 | 37.3281 | -121.9026 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798763 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | RECLOSER | XR010 | 20230107 | 1801 | 20230107 | 1957 | 1927432 | 116 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 417 | 48372 | 37.3857 | -121.813 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1798810 | 0 | EPSS Ckt | N | 2023 | B/C
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 14949 | 20230107 | 1917 | 20230107 | 1946 | 1927496 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 1073 | 37.2612 | -121.906 | Yes | Clear;32-90 F | Secondary | Together | 23-0009038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798865 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12537 | 20230107 | 2212 | 20230108 | 1130 | 1928232 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 33217 | 37.3269 | -121.8307 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0009396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799229 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 13647 | 20230107 | 2322 | 20230108 | 500 | 1929140 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 13520 | 37.4049 | -121.8779 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009813 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799654 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | RECLOSER | XR406 | 20230107 | 2333 | 20230107 | 2345 | 1929382 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 350 | 4200 | 37.3657 | -121.903 | Yes | Clear;32-90F |  |  | 23-0009395 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799228 | 0 | Non-EPSS | N | 2023 | A & B PHASE OC
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 8311 | 20230107 | 2348 | 20230108 | 1059 | 1929755 | 671 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 18117 | 37.3552 | -121.792 | Yes | Strong Winds;32-90 F |  |  | 23-0010030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799875 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 405/2 | 20230107 | 2352 | 20230108 | 201 | 1929911 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 592 | 76368 | 37.3281 | -121.9025 | Yes | Clear;32-90F |  |  | 23-0009455 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1799288 | 0 | Non-EPSS | N | 2023 | GRD OC RLY- TIME
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316112031856 | 20230107 | 2356 | 20230108 | 1950 | 1929982 | 1194 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4776 | 37.3672 | -121.8389 | Yes | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800035 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | 315981930234 | 20230108 | 9 | 20230108 | 1314 | 1930655 | 785 | Transformer only | Vegetation | Tree - palm frond fell into line | 15 | 11775 | 37.3221 | -121.883 | Yes | Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800012 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316111527378 | 20230108 | 26 | 20230108 | 849 | 1931048 | 503 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 4024 | 37.2441 | -121.8369 | Yes | Clear;32-90F |  |  | 23-0009909 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1799759 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | RECLOSER | XR124 | 20230108 | 133 | 20230108 | 302 | 1931776 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 876 | 77964 | 37.2862 | -121.9143 | Yes | Clear;32-90F |  |  | 23-0009680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799513 | 0 | Non-EPSS | N | 2023 | A & B PHASE TIME OC
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20230108 | 415 | 20230108 | 819 | 1932170 | 244 | Distribution Circuit | 3rd Party | Other | 125 | 30500 | 37.1083 | -121.7324 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1799645 | 0 | EPSS Ckt | N | 2023 | A AND C PH OC- TIME
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | T1265 | 20230108 | 722 | 20230109 | 1525 | s1800928 | 1923 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1923 | 37.2881 | -121.912 | Yes | Heavy Rain-Clear;32-90 F | Transformer (UG) | Broken | 23-0011118 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800928 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315871129982 | 20230108 | 1841 | 20230109 | 1411 | 1934363 | 1170 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 12870 | 37.3149 | -121.9208 | Yes | Strong Winds;32-90 F | Secondary | Broken | 23-0010421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800267 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316129827612 | 20230108 | 1845 | 20230108 | 1909 | 1934387 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 48 | 37.2507 | -121.8307 | Yes | Strong Winds;32-90 F | Jumper | Burned Open | 23-0010415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800262 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316031426081 | 20230108 | 2011 | 20230109 | 254 | 1934648 | 403 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 2418 | 37.2083 | -121.8634 | Yes | Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800316 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316031626123 | 20230108 | 2019 | 20230109 | 308 | s1800608 | 409 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 2863 | 37.2095 | -121.8634 | Yes | Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1800608 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 2101/2 | 20230109 | 528 | 20230110 | 209 | 1935802 | 801 | Distribution Circuit | Equipment Failure/Involved | Underground | 3278 | 54218 | 37.2332 | -121.9014 | Yes | Heavy Rain-Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0011122 | UG | Sus | 35419598 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800931 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 40889 | 20230109 | 542 | 20230109 | 830 | 1935869 | 168 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 161 | 27048 | 37.256 | -121.9011 | Yes | Strong Winds;32-90 F | Fuse | Failed/Faulted | 23-0010878 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1800728 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 62810 | 20230109 | 1120 | 20230110 | 157 | 1937821 | 877 | Distribution Circuit | Equipment Failure/Involved | Underground | 162 | 25469 | 37.3413 | -121.8064 | Yes | Heavy Rain-Clear;32-90 F | Elbow | Failed/Faulted | 23-0011148 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1800954 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT 2109 | 83392109 | TRANSFORMER | T9034 | 20230109 | 1604 | 20230111 | 2145 | 1938755 | 3221 | Transformer only | Environmental/External | Water | 18 | 57978 | 37.3274 | -121.7807 | Yes | Clear;32-90 F | Connector or Splice (UG) | Deteriorated | 23-0012458 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802169 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | T14415 | 20230109 | 1614 | 20230111 | 1644 | 1938781 | 2910 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 33409 | 37.1354 | -121.6436 | Yes | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0011568 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801330 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OCB | 2110/2 | 20230109 | 1658 | 20230111 | 2236 | 1938967 | 3218 | Distribution Circuit | Equipment Failure/Involved | Underground | 3126 | 320477 | 37.1267 | -121.6596 | Yes | Clear;32-90F | Switch (UG) | Failed/Faulted | 23-0011451 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801209 | 0 | EPSS Ckt | N | 2023 | C/GRD/51
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | JUMPER | OJ CORNER OF REDWOOD AVE AND N ABBOTT AVE | 20230109 | 1807 | 20230109 | 2233 | 1939196 | 266 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 5054 | 37.4403 | -121.9152 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801272 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316167531354 | 20230109 | 2219 | 20230110 | 1805 | 1939582 | 1186 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 17790 | 37.3536 | -121.8195 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0011680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801443 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20230110 | 210 | 20230110 | 608 | 1940207 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3342 | 793583 | 37.2332 | -121.9012 | Yes | Clear;32-90F |  |  | 23-0011751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801512 | 0 | Non-EPSS | N | 2023 | PH TIME TARGET
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 42109 | 20230110 | 212 | 20230111 | 1309 | 1940209 | 2097 | Distribution Circuit | Vegetation | Tree - branch fell on line | 293 | 614421 | 37.3 | -121.9827 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801990 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 72087 | 20230110 | 214 | 20230110 | 1642 | 1945379 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 34720 | 37.3158 | -121.9749 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802229 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | RECLOSER | 95808 | 20230110 | 214 | 20230115 | 338 | 1940772 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 715649 | 37.304 | -121.8803 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0011808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801569 | 0 | Non-EPSS | N | 2023 | B- C PHASE & GRD
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | OCB | 1112/2 | 20230110 | 215 | 20230112 | 1720 | 1941002 | 3785 | Distribution Circuit | Vegetation | Tree - fell into line | 2702 | 3912369 | 37.3282 | -121.9025 | Yes | Clear;32-90 F | Pole - Tower- steel | Broken- wire on ground | 23-0011809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801570 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | OCB | 1111/2/NORM | 20230110 | 216 | 20230110 | 402 | 1940506 | 106 | Distribution Circuit | Environmental/External | Lightning | 4260 | 443188 | 37.2601 | -121.8897 | Yes | Clear;32-90 F | Connector or Splice (OH) | Normal | 23-0011794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801555 | 0 | Non-EPSS | N | 2023 | A & B PHASE- INST
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 90424 | 20230110 | 216 | 20230113 | 1345 | 1940292 | 5009 | Distribution Circuit | Equipment Failure/Involved | Overhead | 188 | 183031 | 37.3093 | -121.9495 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802034 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1115 | 82261115 | OCB | 1115/2 | 20230110 | 216 | 20230110 | 712 | 1940428 | 296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1041 | 306372 | 37.341 | -121.9017 | Yes | Clear;32-90 F |  |  | 23-0011782 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801542 | 0 | Non-EPSS | N | 2023 | UNKNOWN
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 40889 | 20230110 | 217 | 20230110 | 1148 | 1940340 | 571 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 91931 | 37.256 | -121.9011 | Yes | Clear;32-90 F |  |  | 23-0012323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802071 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | RECLOSER | XR020 | 20230110 | 218 | 20230111 | 1203 | 1940594 | 2025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2829 | 1741525 | 37.3412 | -121.8815 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801552 | 0 | Non-EPSS | N | 2023 | A PHASE OC & GRD
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | RECLOSER | XR362 | 20230110 | 219 | 20230110 | 1721 | 1945960 | 902 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 562 | 506924 | 37.4234 | -121.9657 | Yes | Clear;32-90 F |  |  | 23-0012853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802435 | 0 | Non-EPSS | N | 2023 | A
SAN JOSE | SAN JOSE | SAN JOSE A-0410 | 82250410 | FUSE | 12827 | 20230110 | 219 | 20230110 | 1727 | 1945929 | 908 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 38098 | 37.315 | -121.8985 | Yes | Clear;32-90 F |  |  | 23-0012802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802390 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | OCB | 1116/2 | 20230110 | 219 | 20230110 | 1124 | 1940424 | 545 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1090 | 594050 | 37.341 | -121.9017 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801541 | 0 | Non-EPSS | N | 2023 | A- B - C PHASE OC
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 19563 | 20230110 | 219 | 20230110 | 1340 | 1940397 | 681 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 55842 | 37.2987 | -121.9766 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0012468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802175 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | RECLOSER | XR458 | 20230110 | 219 | 20230110 | 1524 | 1940500 | 785 | Distribution Circuit | Vegetation | Tree - branch fell on line | 748 | 587180 | 37.3056 | -121.894 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801523 | 0 | Non-EPSS | N | 2023 | A/B
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 28013 | 20230110 | 220 | 20230110 | 1304 | 1940436 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 181 | 116564 | 37.3084 | -121.9546 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0012412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802136 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 70587 | 20230110 | 221 | 20230110 | 1322 | 1940734 | 661 | Distribution Circuit | Vegetation | Tree - grew into line | 30 | 17638 | 37.285 | -121.9018 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0012225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801989 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OCB | 2111/2 | 20230110 | 221 | 20230110 | 508 | 1940503 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5466 | 549882 | 37.2332 | -121.9014 | Yes | Clear;32-90 F |  |  | 23-0011783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1801543 | 0 | EPSS Ckt | N | 2023 | A & C PHASE- GRD INST
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 17053 | 20230110 | 223 | 20230110 | 1116 | 1940591 | 533 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 61828 | 37.2283 | -121.8997 | Yes | Clear;32-90 F |  |  | 23-0012238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802000 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 70217 | 20230110 | 224 | 20230110 | 1637 | 1940612 | 853 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 29002 | 37.2954 | -121.9133 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802380 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | RECLOSER | XR360 | 20230110 | 224 | 20230113 | 1555 | 1940810 | 5131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 300 | 247758 | 37.3768 | -121.8983 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801568 | 0 | Non-EPSS | N | 2023 | B & C GRD
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 26815 | 20230110 | 225 | 20230110 | 2105 | 1940644 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 303520 | 37.2809 | -121.9025 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802511 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 8321 | 20230110 | 225 | 20230110 | 1721 | 1945900 | 896 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 8064 | 37.4262 | -121.9763 | Yes | Clear;32-90 F |  |  | 23-0012784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802377 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0403 | 82250403 | OCB | 403/2 | 20230110 | 225 | 20230110 | 1717 | 1940636 | 892 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 823 | 734116 | 37.3281 | -121.9025 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801554 | 0 | Non-EPSS | N | 2023 | A PHASE INST OC////B PHASE INS
SAN JOSE | SAN JOSE | SAN JOSE A-0408 | 82250408 | OCB | 408/2 | 20230110 | 226 | 20230110 | 1416 | 1940663 | 710 | Distribution Circuit | Vegetation | Tree - branch fell on line | 640 | 454400 | 37.3281 | -121.9026 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801553 | 0 | Non-EPSS | N | 2023 | SET A C PHASE TIME OC////GRD T
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 17627 | 20230110 | 227 | 20230113 | 112 | 1940687 | 4245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 915486 | 37.3584 | -121.8898 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1803215 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 41673 | 20230110 | 228 | 20230111 | 1155 | 1947346 | 2007 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 21387 | 37.2856 | -121.8439 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0013442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802961 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20230110 | 228 | 20230111 | 49 | 1940882 | 1341 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 282951 | 37.4483 | -121.8461 | Yes | Clear;32-90 F |  |  | 23-0011795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1801556 | 0 | EPSS Ckt | N | 2023 | A/B/C/51
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | FUSE | 75461 | 20230110 | 228 | 20230111 | 1745 | 1940729 | 2357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 175 | 412475 | 37.3386 | -121.88 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013904 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803266 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315770329978 | 20230110 | 229 | 20230114 | 1421 | 1940752 | 6472 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 71192 | 37.3143 | -121.9552 | Yes | Clear;32-90F | Secondary | Broken | 23-0016111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1804905 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 26889 | 20230110 | 229 | 20230110 | 1243 | 1940792 | 614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 80269 | 37.3358 | -121.9371 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802128 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 28281 | 20230110 | 229 | 20230112 | 1920 | 1944985 | 3891 | Distribution Circuit | Vegetation | Tree - fell into line | 2294 | 712674 | 37.3377 | -121.8182 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012376 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1802108 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRIP-SAVER | 13377 | 20230110 | 230 | 20230111 | 1952 | 1940818 | 2482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 235790 | 37.4347 | -121.882 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0013008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802566 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | INTERRUPTER | 3344 | 20230110 | 235 | 20230110 | 1517 | 1940926 | 762 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1316 | 777112 | 37.2292 | -121.832 | Yes | Clear;32-90 F | Interrupter | Failed/Faulted | 23-0011952 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801731 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 18269 | 20230110 | 237 | 20230110 | 1447 | 1940925 | 730 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 20440 | 37.3657 | -121.8198 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802285 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 26073 | 20230110 | 241 | 20230113 | 350 | 1940979 | 4389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 13167 | 36.9932 | -121.5381 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802596 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20230110 | 244 | 20230112 | 1702 | 1941021 | 3738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1555 | 1270207 | 37.0163 | -121.5446 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011802 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801563 | 0 | EPSS Ckt | N | 2023 | A/G
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 28143 | 20230110 | 250 | 20230110 | 1205 | 1941084 | 555 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 16095 | 37.2424 | -121.8331 | Yes | Clear;32-90 F |  |  | 23-0012363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802098 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316117029000 | 20230110 | 300 | 20230110 | 2158 | 1941099 | 1138 | Transformer only | Vegetation | Tree - palm frond fell into line | 6 | 6828 | 37.2886 | -121.8365 | Yes | Clear;32-90F | Secondary | Normal | 23-0013084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802639 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 15061 | 20230110 | 324 | 20230128 | 1342 | 1941173 | 26538 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 26538 | 37.0927 | -121.7461 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802551 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS SUB | 8318 | OCB | 2100/2 | 20230110 | 339 | 20230111 | 438 | 1941514 | 1480 | Distribution Circuit | 3rd Party | Vehicle | 7703 | 2996308 | 37.0072 | -121.5571 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1801856 | 0 | Non-EPSS | N | 2023 | NONE
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | JUMPER | HS JUMPER @ 42803 | 20230110 | 429 | 20230110 | 942 | 1944025 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 277 | 86701 | 37.3212 | -121.903 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0012087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801860 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315966331816 | 20230110 | 507 | 20230114 | 110 | 1942581 | 5523 | Transformer only | Vegetation | Tree - fell into line | 2 | 5690 | 37.3656 | -121.8892 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0015626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804466 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 41303 | 20230110 | 530 | 20230110 | 1910 | 1943150 | 820 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 269 | 217910 | 37.2435 | -121.8694 | Yes | Clear;32-90 F |  |  | 23-0012628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802294 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | TRANSFORMER | MH142 | 20230110 | 728 | 20230110 | 1715 | 1943293 | 587 | Transformer only | Unknown Cause | Patrol - found nothing | 30 | 17610 | 37.3068 | -121.8998 | Yes | Clear;32-90 F |  |  | 23-0012855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1802436 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12849 | 20230110 | 744 | 20230110 | 1949 | 1943381 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 42775 | 37.247 | -121.848 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802281 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1116 | 82921116 | JUMPER | BURNED OJ LD SIDE OF RISER | 20230110 | 819 | 20230111 | 1500 | 1948318 | 1841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 27615 | 37.2944 | -121.9642 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0013761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1803155 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | TRANSFORMER | 315881827842 | 20230110 | 836 | 20230112 | 1854 | 1943835 | 3498 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 55968 | 37.2561 | -121.9161 | Yes | Clear;32-90 F | Secondary | Burned Open | 23-0013013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802570 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | RECLOSER | XR010 | 20230110 | 839 | 20230111 | 1428 | 1943895 | 1776 | Distribution Circuit | Vegetation | Tree - branch fell on line | 417 | 443686 | 37.3857 | -121.813 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012066 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1801844 | 0 | EPSS Ckt | N | 2023 | b & c phase
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 52769 | 20230110 | 841 | 20230111 | 2357 | 1943867 | 2356 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 100077 | 37.3722 | -121.8149 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012598 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1802270 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315912828500 | 20230110 | 850 | 20230112 | 1851 | 1940259 | 3481 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 62658 | 37.2743 | -121.9059 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0012413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802137 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | OTHER | WIRE DOWN SOUTH EAST OF 6069 | 20230110 | 1250 | 20230112 | 2215 | 1945121 | 3445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 404022 | 37.3062 | -121.8893 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1802477 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 2145 | 20230110 | 1806 | 20230113 | 1627 | 1946238 | 3289 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 396525 | 37.236 | -121.8734 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0013593 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803059 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 17205 | 20230110 | 1830 | 20230112 | 1858 | 1946294 | 2908 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 270444 | 37.4347 | -121.9158 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0012923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802489 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | XR548 | 20230110 | 1912 | 20230112 | 134 | 1946016 | 1822 | Distribution Circuit | Equipment Failure/Involved | Overhead | 177 | 68592 | 37.2021 | -121.8332 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802515 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17555 | 20230110 | 1957 | 20230110 | 2123 | 1946440 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 3092 | 37.383 | -121.8103 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1802576 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 71015 | 20230110 | 2135 | 20230112 | 829 | 1949552 | 2094 | Distribution Circuit | 3rd Party | Metallic Balloon | 11 | 23034 | 37.3274 | -121.7665 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0014282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803620 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 18315 | 20230110 | 2146 | 20230111 | 1305 | 1946654 | 919 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1838 | 37.3748 | -121.7748 | Yes | Clear;32-90F |  |  | 23-0013642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803091 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | OCB | 1111/2 | 20230111 | 855 | 20230111 | 2204 | 1947235 | 789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3604 | 581429 | 37.2332 | -121.9012 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802950 | 0 | Non-EPSS | N | 2023 | A PHASE T & GRD T
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316777522626 | 20230111 | 1026 | 20230112 | 1956 | 1947521 | 2010 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2010 | 37.1162 | -121.6061 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0014131 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803478 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 1613 | 20230111 | 1106 | 20230113 | 10 | 1949081 | 2224 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4448 | 36.9592 | -121.5375 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803336 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OCB | 1107/2 | 20230111 | 1310 | 20230112 | 258 | 1948089 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 5583 | 646454 | 37.3043 | -121.8681 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0013710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803122 | 0 | Non-EPSS | N | 2023 | A-B-C
SAN JOSE | SAN JOSE | MONTAGUE-2103 | 83892103 | OCB | 2103/2 | 20230111 | 1438 | 20230111 | 1556 | 1948377 | 71 | Distribution Circuit | Equipment Failure/Involved | Substation | 255 | 19380 | 37.403 | -121.9057 | No | Clear;32-90F | Other | Malfunctioning | 23-0013805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1803196 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 9209 | 20230111 | 1459 | 20230111 | 1722 | 1948412 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 4862 | 37.3766 | -121.7973 | No | Clear;32-90F |  |  | 23-0013892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803254 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12849 | 20230111 | 1533 | 20230111 | 1920 | 1948497 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 13393 | 37.247 | -121.848 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0013800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803191 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315908427892 | 20230111 | 1754 | 20230112 | 2117 | 1947579 | 1643 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 23002 | 37.2576 | -121.9069 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0014742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803875 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | T20546 | 20230111 | 1756 | 20230113 | 1729 | 1948863 | 2853 | Distribution Circuit | Equipment Failure/Involved | Underground | 160 | 33051 | 37.2246 | -121.8545 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0014221 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803572 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 73263 | 20230111 | 1843 | 20230112 | 2123 | 1948933 | 1600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 60383 | 37.2364 | -121.9145 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0014043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803392 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 41027 | 20230111 | 2116 | 20230112 | 2116 | 1949106 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4320 | 36.9962 | -121.587 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1803371 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2107 | 82462107 | JUMPER | OJ SS OF 11929 | 20230111 | 2129 | 20230113 | 57 | 1949117 | 1648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1679 | 37.4176 | -121.959 | No | Clear;32-90F | Jumper | Burned/flashed | 23-0014233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1803584 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 41807 | 20230111 | 2249 | 20230114 | 119 | 1948104 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75750 | 37.3105 | -121.9598 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803468 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 33270 | 20230111 | 2303 | 20230111 | 2310 | 1949157 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 82 | 574 | 37.1087 | -121.6407 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0011451 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1803486 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | INTERRUPTER | 6244 | 20230112 | 131 | 20230114 | 104 | 1949229 | 2644 | Distribution Circuit | 3rd Party | Vandalism | 186 | 127042 | 37.4032 | -121.8962 | No | Clear;32-90F | Switch (UG) | Failed/Faulted | 23-0014237 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803588 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR586 | 20230112 | 956 | 20230112 | 1959 | 1949554 | 603 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1009 | 38886 | 37.0279 | -121.5275 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0014348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803664 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 75187 | 20230112 | 1540 | 20230112 | 1802 | 1940809 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1704 | 37.3285 | -121.9504 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0014691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803849 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 75187 | 20230112 | 1540 | 20230112 | 1802 | 1940809 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1704 | 37.3285 | -121.9504 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0014691 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1803849 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4165 | 20230112 | 2327 | 20230113 | 132 | 1951164 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1374 | 36.9884 | -121.4904 | No | Clear;32-90F |  |  | 23-0015034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804145 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13079 | 20230113 | 935 | 20230114 | 1514 | 1951440 | 1779 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 62265 | 37.3751 | -121.8197 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804202 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 5337 | 20230113 | 952 | 20230113 | 2350 | 1951701 | 838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 838 | 37.3027 | -121.9486 | No | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0015311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804267 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 8327 | 20230113 | 1155 | 20230113 | 1410 | 1951847 | 135 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 8390 | 37.2556 | -121.9032 | No | Clear;32-90F | Conductor- Underground | Burned/flashed | 23-0015315 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804269 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 4603 | 20230113 | 1758 | 20230113 | 1918 | 1952451 | 80 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 800 | 37.0704 | -121.5681 | No | Clear;32-90F | Secondary | Broken | 23-0015519 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804367 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | SWITCH | 3817 | 20230113 | 2319 | 20230114 | 430 | 1952656 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 16794 | 37.3772 | -121.7934 | No | Clear;32-90F | Pole-Wood | Broken | 23-0015545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1804534 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20230114 | 454 | 20230114 | 800 | 1952798 | 186 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 11904 | 37.0838 | -121.7753 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0015834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1804680 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316076130648 | 20230114 | 708 | 20230114 | 1445 | 1952928 | 457 | Transformer only | Vegetation | Tree - grew into line | 9 | 4113 | 37.3339 | -121.8507 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804899 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 45654 | 20230114 | 751 | 20230115 | 19 | 1953112 | 988 | Distribution Circuit | Equipment Failure/Involved | Underground | 717 | 215090 | 36.9931 | -121.5959 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0016154 | UG | Sus | 35419598 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804937 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 316158530830 | 20230114 | 1024 | 20230114 | 1246 | 1953939 | 142 | Transformer only | Company Initiated | Return Circuit Normal | 2 | 284 | 37.3391 | -121.8225 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0016180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1804957 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | JUMPER | OJS @ SS OF CGG # 9631 | 20230114 | 1750 | 20230114 | 2110 | 1954830 | 200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 5625 | 37.3048 | -121.9813 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805090 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315896829755 | 20230114 | 1926 | 20230115 | 1305 | 1955128 | 1059 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 19062 | 37.3086 | -121.912 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805279 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316162128570 | 20230114 | 2201 | 20230115 | 38 | 1955233 | 157 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1570 | 37.2771 | -121.8201 | Yes | Clear;32-90F | Secondary | Broken | 23-0016460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805213 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316159128577 | 20230114 | 2208 | 20230115 | 42 | 1955234 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1232 | 37.2773 | -121.8212 | Yes | Clear;32-90F | Secondary | Broken | 23-0016463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805216 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 9723 | 20230115 | 35 | 20230115 | 56 | 1955352 | 21 | Distribution Circuit | Company Initiated | Return Circuit Normal | 184 | 3864 | 37.4146 | -121.8593 | No | Clear;32-90F | Conductor- Underground | Normal | 23-0016333 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1805253 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 13017 | 20230115 | 834 | 20230115 | 949 | 1955622 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 4275 | 37.3197 | -121.8965 | No | Clear;32-90F |  |  | 23-0016594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805340 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 14923 | 20230115 | 916 | 20230116 | 1420 | 1955693 | 1744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1744 | 37.0833 | -121.7834 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0016641 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1805380 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 14151 | 20230115 | 929 | 20230115 | 1438 | 1955710 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 773 | 60055 | 37.3511 | -121.8237 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0016609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1805355 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316116131484 | 20230115 | 1041 | 20230115 | 1319 | 1955806 | 158 | Transformer only | Vegetation | Tree - fell into line | 13 | 2054 | 37.357 | -121.8373 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805367 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY 2110 | 83912110 | TRANSFORMER | T6084 | 20230115 | 1052 | 20230115 | 1141 | 1955808 | 49 | Transformer only | Equipment Failure/Involved | Underground | 22 | 1078 | 37.2863 | -121.7581 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0016628 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805368 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315949828336 | 20230115 | 1108 | 20230115 | 1719 | 1955845 | 371 | Transformer only | Vegetation | Tree - fell into line | 12 | 4452 | 37.27 | -121.893 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0016675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805408 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 28561 | 20230115 | 1227 | 20230115 | 1857 | 1956327 | 390 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1170 | 37.0005 | -121.5282 | No | Clear;32-90 F |  |  | 23-0016779 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805476 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 47515 | 20230115 | 1330 | 20230116 | 1908 | 1955959 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 62230 | 37.3182 | -121.9293 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0016699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805422 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | C84 | 20230115 | 1402 | 20230115 | 1426 | 1955955 | 24 | Transformer only | Equipment Failure/Involved | Underground | 20 | 480 | 37.217 | -121.8738 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0016698 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805421 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315925528026 | 20230115 | 1734 | 20230115 | 1758 | 1956252 | 24 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 456 | 37.2614 | -121.9011 | No | Clear;32-90 F | Secondary | Broken- wire on object | 23-0016760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805461 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 4527 | 20230115 | 2120 | 20230116 | 1648 | 1956404 | 1168 | Distribution Circuit | 3rd Party | Vehicle | 47 | 9938 | 37.0034 | -121.5609 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0016848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805546 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 43411 | 20230115 | 2129 | 20230116 | 102 | 1956408 | 213 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3408 | 37.249 | -121.6843 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016855 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805553 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | RECLOSER | XR538 | 20230116 | 323 | 20230116 | 1343 | 1956673 | 590 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2967 | 171345 | 37.3012 | -121.9677 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805592 | 0 | Non-EPSS | N | 2023 | BC
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 18751 | 20230116 | 418 | 20230116 | 846 | 1956770 | 268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 127 | 34036 | 37.2797 | -121.8908 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0017041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805740 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE 2105 | 82952105 | FUSE | 25151 | 20230116 | 507 | 20230116 | 1124 | 1957444 | 377 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2 | 753 | 37.2181 | -121.7422 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0017152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805841 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | TRANSFORMER | 316013534042 | 20230116 | 632 | 20230116 | 1514 | 1958369 | 522 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 7830 | 37.4269 | -121.8741 | Yes | Clear;32-90F | Secondary | Broken | 23-0017266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805941 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | RECLOSER | XR280 | 20230116 | 707 | 20230116 | 1920 | 1957149 | 733 | Distribution Circuit | Equipment Failure/Involved | Overhead | 621 | 72033 | 37.3589 | -121.8936 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0017046 | OH | Sus | 35419597 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805745 | 0 | Non-EPSS | N | 2023 | NONE
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315905229815 | 20230116 | 755 | 20230116 | 1208 | 1957265 | 253 | Transformer only | Vegetation | Tree - grew into line | 12 | 3036 | 37.3101 | -121.9091 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0017129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805817 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315902430626 | 20230116 | 838 | 20230116 | 1116 | 1957346 | 158 | Transformer only | Equipment Failure/Involved | Overhead | 52 | 8216 | 37.3328 | -121.9107 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0017144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805833 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 25691 | 20230116 | 940 | 20230116 | 1411 | 1957440 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 20867 | 37.328 | -121.9304 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0017062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805760 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 3279 | 20230116 | 941 | 20230116 | 1101 | 1957522 | 80 | Distribution Circuit | 3rd Party | Other | 12 | 960 | 37.3347 | -121.852 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0017124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805812 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | C3353 | 20230116 | 1139 | 20230116 | 1220 | 1957886 | 41 | Transformer only | Equipment Failure/Involved | Underground | 56 | 2296 | 37.3454 | -121.8239 | Yes | Clear;32-90F | Secondary | Broken | 23-0017155 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805844 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 8329 | 20230116 | 1259 | 20230116 | 1316 | 1958106 | 17 | Distribution Circuit | Equipment Failure/Involved | Underground | 79 | 628 | 37.2558 | -121.9037 | Yes | Clear;32-90F | Conductor- Underground | Broken | 23-0015315 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1805896 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20230116 | 1458 | 20230116 | 1653 | 1958388 | 115 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 6 | 690 | 37.2181 | -121.7422 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0017318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1805995 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316055330105 | 20230116 | 1912 | 20230117 | 203 | 1958430 | 411 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 7809 | 37.3189 | -121.8577 | Yes | Clear;32-90F | Connector or Splice (OH) | Burned/flashed | 23-0017372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806045 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | 316750422438 | 20230116 | 1932 | 20230116 | 2147 | 1958824 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 270 | 37.1109 | -121.6154 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0017385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806055 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 40182 | 20230116 | 1957 | 20230117 | 252 | 1958857 | 415 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 18174 | 37.1359 | -121.6739 | Yes | Clear;32-90F | Transformer (UG) | Deteriorated | 23-0017293 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806058 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 31430 | 20230117 | 119 | 20230117 | 1409 | 1959018 | 770 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 27720 | 37.144 | -121.6272 | No | Clear;32-90F | Elbow | Burned/flashed | 23-0017453 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806123 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 1685 | 20230117 | 540 | 20230117 | 1546 | 1959085 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1212 | 37.1208 | -121.6868 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | Yes | No | 1806124 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26057 | 20230117 | 748 | 20230117 | 1006 | 1959169 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 9246 | 37.0874 | -121.6269 | No | Clear;32-90F |  |  | 23-0017537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1806165 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316124330240 | 20230117 | 1012 | 20230117 | 1318 | 1959385 | 186 | Transformer only | Unknown Cause | Patrol - found nothing | 23 | 4278 | 37.3228 | -121.8339 | No | Clear;32-90F |  |  | 23-0017706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806224 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26719 | 20230117 | 1657 | 20230117 | 1905 | 1960151 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 256 | 37.1064 | -121.6005 | No | Clear;32-90F |  |  | 23-0017886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806296 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | OTHER | WIRE DOWN @ 3 TO 4TH POLE OF 13035 | 20230117 | 1918 | 20230118 | 558 | 1960352 | 567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 251 | 69761 | 37.3141 | -121.8833 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017903 | OH | Sus | 45643795 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1806315 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2110 | 83892110 | INTERRUPTER | 31982 | 20230117 | 1928 | 20230117 | 2055 | 1960311 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 122 | 2746 | 37.401 | -121.8953 | No | Clear;32-90F |  |  | 23-0014237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806314 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | C2299 | 20230118 | 928 | 20230118 | 2225 | 1960671 | 777 | Transformer only | Equipment Failure/Involved | Underground | 13 | 10101 | 37.2107 | -121.8524 | No | Clear;32-90F | Transformer (UG) | Contaminated | 23-0018641 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806698 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | TRANSFORMER | 316008929124 | 20230118 | 1443 | 20230119 | 13 | 1961133 | 570 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1140 | 37.2915 | -121.873 | No | Clear;32-90F |  |  | 23-0018636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806694 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316620620895 | 20230118 | 1914 | 20230119 | 504 | 1961458 | 590 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1180 | 37.068 | -121.6593 | No | Clear;32-90F |  |  | 23-0018631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806688 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316624020952 | 20230118 | 2031 | 20230118 | 2234 | 1961490 | 123 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 123 | 37.0696 | -121.6581 | No | Clear;32-90F |  |  | 23-0018632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1806689 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316828019097 | 20230118 | 2213 | 20230119 | 723 | 1961661 | 550 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2750 | 37.0194 | -121.5874 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0018643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806700 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316624020952 | 20230119 | 102 | 20230119 | 1341 | 1961739 | 759 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 759 | 37.0696 | -121.6581 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806715 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | T8704 | 20230119 | 1954 | 20230120 | 333 | 1962785 | 459 | Transformer only | Equipment Failure/Involved | Underground | 38 | 17442 | 37.3431 | -121.8234 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0019189 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806961 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 17313 | 20230120 | 15 | 20230120 | 1553 | 1962852 | 938 | Distribution Circuit | Equipment Failure/Involved | Underground | 159 | 41589 | 37.2881 | -121.8202 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0019188 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1806960 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 14253 | 20230120 | 1037 | 20230120 | 1540 | 1963043 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1818 | 37.4783 | -121.8537 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1806995 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1113 | 83371113 | TRANSFORMER | 315655429821 | 20230120 | 1215 | 20230120 | 1930 | 1963602 | 435 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5655 | 37.31 | -121.9946 | No | Clear;32-90F | Secondary | Broken | 23-0019614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807090 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315781029284 | 20230120 | 2219 | 20230120 | 2307 | 1963676 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 240 | 37.2952 | -121.9516 | No | Clear;32-90F | Conductor- Overhead | Arcing | 23-0019660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807134 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315909829724 | 20230121 | 932 | 20230121 | 1825 | 1964290 | 533 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1066 | 37.3079 | -121.9075 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807238 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315973028844 | 20230121 | 1500 | 20230121 | 1636 | 1964150 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 384 | 37.284 | -121.8854 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0019750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807218 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20230123 | 57 | 20230123 | 1145 | 1965168 | 648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 776 | 173284 | 37.133 | -121.6122 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019982 | OH | Sus | 45647075 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807415 | 0 | EPSS Ckt | N | 2023 | B PH- GRD
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | T9466 | 20230123 | 242 | 20230124 | 301 | 1965244 | 1459 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 37934 | 37.2656 | -121.8677 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0020116 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807554 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41543 | 20230123 | 656 | 20230123 | 1708 | 1965346 | 612 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 42840 | 37.3313 | -121.8409 | No | Clear;32-90F | Anchor or Guy | Broken | 23-0020180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1807575 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | SWITCH | 63344SW | 20230123 | 1313 | 20230123 | 1346 | 1965641 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 99 | 37.3626 | -121.8689 | No | Clear;32-90F |  |  | 23-0020284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807610 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | T2022 | 20230123 | 1619 | 20230124 | 322 | 1965582 | 663 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1989 | 37.3408 | -121.8875 | No | Clear;32-90F | Switch (UG) | Broken | 23-0020429 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807637 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 1505 | 20230123 | 1642 | 20230124 | 252 | 1966186 | 24 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 2232 | 37.2659 | -121.8663 | No | Clear;32-90F | Transformer (UG) | Deteriorated | 23-0020111 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807641 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | RECLOSER | XR362 | 20230123 | 1956 | 20230123 | 2205 | 1966312 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 571 | 73659 | 37.4234 | -121.9657 | No | Clear;32-90F |  |  | 23-0020463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1807660 | 0 | Non-EPSS | N | 2023 | A-B-C- GRD
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316149631651 | 20230123 | 2118 | 20230124 | 27 | 1966342 | 189 | Transformer only | Unknown Cause | Patrol - found nothing | 20 | 3780 | 37.3617 | -121.8257 | No | Clear;32-90 F |  |  | 23-0020491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1807689 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316196131980 | 20230124 | 107 | 20230124 | 500 | 1966383 | 233 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 699 | 37.3709 | -121.81 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0020495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807693 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20230124 | 129 | 20230124 | 326 | 1966390 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 776 | 86912 | 37.133 | -121.6122 | No | Clear;32-90 F |  |  | 23-0020496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807694 | 0 | EPSS Ckt | N | 2023 | GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 13471 | 20230124 | 435 | 20230125 | 317 | 1966418 | 1362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 7894 | 37.118 | -121.5838 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0020649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807832 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2101 | 83892101 | OTHER | J5881 TWD T23067 | 20230124 | 934 | 20230124 | 1704 | 1966751 | 450 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 450 | 37.4139 | -121.9207 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0020450 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1807821 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | OJ H/S OF 20007 | 20230124 | 1412 | 20230125 | 144 | 1967130 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 925 | 18248 | 37.0347 | -121.5686 | No | Clear;32-90 F | Jumper | Burned Open | 23-0020881 | OH | Sus | 31635368 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807912 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 14185 | 20230125 | 349 | 20230125 | 2339 | 1967508 | 1190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 8330 | 37.1107 | -121.5935 | No | Clear;32-90F | Pothead(Riser Termination) | Broken | 23-0021042 | OH | Sus | 31635373 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1807992 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 16045 | 20230125 | 708 | 20230125 | 1110 | 1967545 | 242 | Distribution Circuit | Animal | Bird found | 4 | 968 | 37.1741 | -121.7604 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808123 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2105 | 83892105 | SWITCH | 25476 | 20230125 | 1630 | 20230125 | 1636 | 1968228 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 37.4059 | -121.9184 | No | Clear;32-90F | Bus | Failed/Faulted | 23-0021402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808178 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 6512 | 20230125 | 1633 | 20230126 | 401 | 1968238 | 688 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 85387 | 37.3108 | -121.8139 | No | Clear;32-90F | Elbow | Burned/flashed | 23-0021410 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808193 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | JUMPER | 12033 | 20230125 | 1655 | 20230126 | 130 | 1968260 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2398 | 37.265 | -121.8192 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0021431 | OH | Sus | 45650355 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1808187 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | JUMPER | WIRE DOWN | 20230126 | 209 | 20230126 | 1304 | 1968441 | 651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 621 | 16253 | 37.364 | -121.8855 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0021523 | OH | Sus | 31635575 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808261 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 100000134791 | 20230126 | 1220 | 20230126 | 1404 | 1968915 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 936 | 37.3538 | -121.83 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0021800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808432 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 17637 | 20230126 | 1436 | 20230127 | 605 | 1969050 | 929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 32515 | 37.4267 | -121.8717 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0022009 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808480 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2107 | 82952107 | TRANSFORMER | 40098 | 20230126 | 1512 | 20230127 | 446 | 1969074 | 814 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 977 | 37.2395 | -121.7932 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0021996 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808476 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | SWITCH | 40762 | 20230126 | 1821 | 20230127 | 50 | 1969223 | 389 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 778 | 37.2318 | -121.7803 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0021942 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808486 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 3049 | 20230127 | 1401 | 20230130 | 250 | 1969993 | 3649 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 3649 | 37.2836 | -121.8434 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0022441 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808702 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | INTERRUPTER | 64392 | 20230127 | 1819 | 20230127 | 2303 | 1970174 | 284 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 15604 | 37.3897 | -121.8946 | No | Clear;32-90F | Interrupter | Failed/Faulted | 23-0022562 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808741 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 71319 | 20230127 | 2241 | 20230127 | 2257 | 1970158 | 16 | Distribution Circuit | Animal | Squirrel | 1 | 16 | 37.3013 | -121.8577 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0022573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808751 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | SWITCH | 43068 | 20230127 | 2335 | 20230128 | 143 | -1970174 | 64 | Distribution Circuit | Company Initiated | Personnel- company | 258 | 2726 | 37.3896 | -121.8946 | No | Clear;32-90F | Interrupter | Failed/Faulted | 23-0022562 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808754 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | TRANSFORMER | 315973729764 | 20230128 | 1233 | 20230128 | 1739 | 1970509 | 306 | Transformer only | 3rd Party | Metallic Balloon | 5 | 1530 | 37.3093 | -121.8856 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0022640 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808832 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR522 | 20230128 | 1445 | 20230129 | 2114 | 1970590 | 1793 | Distribution Circuit | 3rd Party | Vehicle | 3619 | 242247 | 37.2767 | -121.8342 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022648 | OH | Sus | 35423882 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1808839 | 0 | Non-EPSS | N | 2023 | B PH- GRD
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 8539 | 20230128 | 1612 | 20230129 | 1609 | 1970617 | 1437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 112086 | 37.3087 | -121.9587 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0022654 | OH | Sus | 31635821 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1808844 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 40163 | 20230128 | 1750 | 20230129 | 1931 | 1970695 | 1541 | Distribution Circuit | Animal | Bird found | 5 | 7705 | 37.0209 | -121.5689 | No | Clear;32-90F | Cutout- fuse holder | Burned/flashed | 23-0022671 | OH | Sus | 45653377 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1808860 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20230129 | 759 | 20230129 | 1712 | 1970834 | 553 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 506 | 132592 | 37.3558 | -121.8299 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022710 | OH | Sus | 45653622 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808916 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1102 | 82261102 | TRANSFORMER | T3923 | 20230130 | 917 | 20230201 | 354 | 1971634 | 2538 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 5236 | 37.3376 | -121.889 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0023223 | UG | Sus | 35424192 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809294 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 25169 | 20230130 | 1051 | 20230130 | 1316 | 1971831 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 290 | 37.1361 | -121.7001 | No | Clear;32-90F |  |  | 23-0022987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1809202 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | OTHER | WIRE DOWN S/W/O 28171 | 20230130 | 1400 | 20230131 | 147 | 1972073 | 707 | Distribution Circuit | 3rd Party | Vehicle | 1840 | 222660 | 37.3364 | -121.9369 | No | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0023107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1809241 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1109 | 83871109 | FUSE | 25291 | 20230130 | 1515 | 20230131 | 345 | 1972124 | 750 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3750 | 37.3473 | -121.9287 | No | Clear;32-90F | Jumper | Burned/flashed | 23-0023195 | OH | Sus | 45655010 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1809271 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE 1103 | 82951103 | SWITCH | 23311 | 20230130 | 2103 | 20230131 | 353 | 1972282 | 403 | Distribution Circuit | Vegetation | Tree - grew into line | 156 | 50168 | 37.2511 | -121.825 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809274 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 40407 | 20230131 | 703 | 20230131 | 1337 | 1972388 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 187 | 73678 | 37.0136 | -121.6512 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0023293 | OH | Sus | 45655426 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1809343 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | FUSE | 43209 | 20230131 | 1755 | 20230131 | 1815 | 1972986 | 20 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 30 | 600 | 37.3499 | -121.8852 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809529 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2101 | 83892101 | SWITCH | 32632SW | 20230131 | 2121 | 20230201 | 204 | 1973259 | 283 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1151 | 37.4126 | -121.9127 | No | Clear;32-90F | Transformer (UG) | Leaking | 23-0023621 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1809561 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS 1105 | 82831105 | TRANSFORMER | T465383 | 20230201 | 848 | 20230201 | 1320 | 1973572 | 272 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 272 | 37.4624 | -121.8807 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0023893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1809759 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316053030767 | 20230201 | 945 | 20230201 | 1107 | 1973775 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 1558 | 37.3371 | -121.8586 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0023901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809762 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OTHER | DBSC PULLED OFF SW 34250 TWD C1943 | 20230201 | 1502 | 20230202 | 4 | 1974176 | 542 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 194 | 49924 | 37.245 | -121.8638 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0024094 | UG | Sus | 35424663 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1809813 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | SWITCH | 9694 | 20230202 | 940 | 20230202 | 1238 | 1974701 | 178 | Distribution Circuit | Company Initiated | Return Circuit Normal | 194 | 16540 | 37.246 | -121.865 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0024094 | UG | Sus | 35424663 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1809996 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | TRANSFORMER | C2771 | 20230202 | 1033 | 20230202 | 1543 | 1974821 | 310 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 310 | 37.3629 | -121.9038 | No | Clear;32-90 F |  |  | 23-0024435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810049 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28347 | 20230202 | 1121 | 20230203 | 145 | 1974905 | 864 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 864 | 37.1321 | -121.7012 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0024438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810050 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | SWITCH | 42814 | 20230203 | 1305 | 20230203 | 1322 | 1976052 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 258 | 4386 | 37.3907 | -121.8958 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0022562 | UG | Sus | 35424106 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810366 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 19493 | 20230204 | 1410 | 20230205 | 1701 | 1976686 | 1611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 14799 | 37.2997 | -121.9801 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0025246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810547 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | RECLOSER | XR020 | 20230204 | 1758 | 20230205 | 822 | 1976809 | 864 | Distribution Circuit | Equipment Failure/Involved | Overhead | 527 | 269400 | 37.3412 | -121.8815 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025249 | OH | Sus | 45658900 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810550 | 0 | Non-EPSS | N | 2023 | A GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230204 | 1810 | 20230205 | 250 | 1976829 | 520 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 15080 | 37.1602 | -121.666 | No | Clear;32-90 F |  |  | 23-0025325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810628 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | OCB | 1111/2 | 20230204 | 2014 | 20230205 | 1514 | 1976956 | 1140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2104 | 151404 | 37.3662 | -121.8437 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025272 | OH | Sus | 31636330 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810575 | 0 | EPSS Ckt | N | 2023 | B C GRD
SAN JOSE | SAN JOSE | SAN JOSE B SUB | 8226 | OCB | 1300/2 | 20230205 | 611 | 20230205 | 802 | 1977235 | 111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5037 | 559107 | 37.341 | -121.902 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0025338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1810641 | 0 | Non-EPSS | N | 2023 | TIME PHASE OC B&C
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 7403 | 20230205 | 1126 | 20230206 | 600 | 1977422 | 1114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 227 | 218062 | 37.3216 | -121.9171 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025399 | OH | Sus | 31636156 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810689 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317138017810 | 20230205 | 1157 | 20230205 | 1357 | 1977449 | 120 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 120 | 36.9849 | -121.4794 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0025414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810703 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 889 | 20230205 | 1532 | 20230208 | 1526 | 1977988 | 4314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 30548 | 36.9472 | -121.5098 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0025590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810887 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 72925 | 20230205 | 1534 | 20230206 | 225 | 1977555 | 651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 82026 | 37.3077 | -121.8887 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0025442 | OH | Sus | 31636195 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810728 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | OTHER | CENTER PHASE DOWN | 20230205 | 1731 | 20230206 | 612 | 1977629 | 761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 321 | 191732 | 37.3595 | -121.8627 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025456 | OH | Sus | 45658932 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1810741 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20230205 | 2131 | 20230205 | 2258 | 1977750 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 776 | 67512 | 37.133 | -121.6122 | No | Partly Cloudy;32-90 F |  |  | 23-0025502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810787 | 0 | EPSS Ckt | N | 2023 | GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 4765 | 20230206 | 207 | 20230206 | 2125 | 1977781 | 1158 | Distribution Circuit | Equipment Failure/Involved | Underground | 776 | 3090 | 37.0824 | -121.5747 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0025519 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1810803 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315922929161 | 20230206 | 912 | 20230206 | 1032 | 1978055 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 480 | 37.2925 | -121.9027 | No | Clear;32-90F | Secondary | Deteriorated | 23-0025604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810925 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 27041 | 20230207 | 1459 | 20230208 | 240 | 1979382 | 701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2103 | 37.1646 | -121.6934 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0026342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811349 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316903819695 | 20230207 | 2056 | 20230208 | 1308 | 1979392 | 972 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 972 | 37.0361 | -121.5617 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0026440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1811375 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | JUMPER | JUMPERS | 20230208 | 1052 | 20230208 | 1253 | 1980006 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 3872 | 37.2918 | -121.9031 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0026623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811615 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2111 | 82832111 | TRANSFORMER | C4945 | 20230208 | 2027 | 20230208 | 2217 | 1980382 | 110 | Transformer only | Equipment Failure/Involved | Underground | 4 | 440 | 37.4309 | -121.9068 | No | Clear;32-90F | Secondary | Deteriorated | 23-0026871 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811683 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15741 | 20230209 | 235 | 20230209 | 729 | 1980431 | 294 | Distribution Circuit | 3rd Party | Metallic Balloon | 8 | 2352 | 37.1992 | -121.8221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0026927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1811726 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 2615 | 20230209 | 1400 | 20230210 | 418 | 1981098 | 858 | Distribution Circuit | Equipment Failure/Involved | Underground | 254 | 31945 | 37.345 | -121.8153 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0026791 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1811954 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 3897 | 20230209 | 1608 | 20230209 | 1708 | 1981193 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 380 | 36.9728 | -121.521 | No | Clear;32-90 F |  |  | 23-0027287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1811981 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 40283 | 20230210 | 1318 | 20230210 | 1723 | 1981872 | 245 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 40 | 9800 | 37.3138 | -121.8222 | No | Clear;32-90 F | Fuse | Normal | 23-0027620 | OH | Sus | 45667356 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1812250 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | RECLOSER | XR418 | 20230212 | 1023 | 20230213 | 305 | 1982866 | 1002 | Distribution Circuit | Equipment Failure/Involved | Underground | 668 | 181576 | 37.3154 | -121.985 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0027918 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812508 | 0 | Non-EPSS | N | 2023 | B PH GRD
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12479 | 20230212 | 1249 | 20230212 | 1405 | 1982951 | 76 | Distribution Circuit | 3rd Party | Metallic Balloon | 48 | 3648 | 37.3344 | -121.835 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0027933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812528 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15569 | 20230212 | 1651 | 20230212 | 1703 | 1983049 | 12 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 12 | 37.3422 | -121.722 | No | Clear;32-90 F |  |  | 23-0027949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812547 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 42411 | 20230212 | 1726 | 20230213 | 1611 | 1983055 | 1365 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 6825 | 37.2757 | -121.7476 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0027988 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812584 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | OCB | 2102/2 | 20230212 | 1837 | 20230213 | 1232 | 1983085 | 1075 | Distribution Circuit | Equipment Failure/Involved | Underground | 993 | 203431 | 37.403 | -121.9058 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 23-0027953 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1812551 | 0 | Non-EPSS | N | 2023 | A PHASE-GRD- T OC
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 40009 | 20230213 | 657 | 20230213 | 937 | 1983232 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 3680 | 37.3463 | -121.8291 | No | Clear;32-90F |  |  | 23-0028074 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812720 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRIP-SAVER | 28421 | 20230213 | 1509 | 20230214 | 1301 | 1983870 | 1312 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 2624 | 36.9304 | -121.5251 | No | Clear;32-90F |  |  | 23-0028256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1812834 | 0 | EPSS Ckt | N | 2023 | OC (10T VALUE)
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 71015 | 20230214 | 1233 | 20230214 | 1950 | 1985399 | 437 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4807 | 37.3274 | -121.7665 | No | Clear;32-90F |  |  | 23-0028934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813279 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 1449 | 20230214 | 1807 | 20230215 | 330 | 1985391 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 169 | 18661 | 37.0418 | -121.5418 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0028937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813281 | 0 | EPSS Ckt | N | 2023 | PHASE OC A & B TRIPPED
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317000420220 | 20230214 | 2041 | 20230215 | 510 | 1985495 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2545 | 37.0507 | -121.5288 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0028966 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813307 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | SWITCH | 25098 | 20230214 | 2157 | 20230215 | 858 | 1985560 | 661 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 5698 | 37.3713 | -121.8945 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0028675 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813309 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 6249 | 20230215 | 931 | 20230215 | 1017 | 1985976 | 46 | Distribution Circuit | 3rd Party | Metallic Balloon | 169 | 7774 | 37.0086 | -121.5625 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0029129 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813487 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 3041 | 20230215 | 1102 | 20230215 | 1201 | 1986067 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 982 | 37.0434 | -121.5868 | No | Clear;32-90 F |  |  | 23-0029188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1813505 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316180827379 | 20230215 | 2031 | 20230216 | 41 | 1986085 | 250 | Transformer only | Vegetation | Tree - grew into line | 8 | 2000 | 37.2444 | -121.8131 | No | Clear;32-90 F | Secondary | Contaminated | 23-0029457 | OH | Sus | 31636921 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813587 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | T5321 | 20230215 | 2150 | 20230215 | 2306 | 1986509 | 76 | Transformer only | Equipment Failure/Involved | Underground | 21 | 1596 | 37.3848 | -121.8298 | No | Clear;32-90F | Secondary | Broken | 23-0029491 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1813608 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 13987 | 20230217 | 824 | 20230217 | 946 | 1987414 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3690 | 37.2752 | -121.8978 | No | Clear;32-90 F |  |  | 23-0030053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1813955 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | OCB | 1105/2 | 20230218 | 219 | 20230218 | 1841 | 1988032 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 2086 | 290628 | 37.2915 | -121.9358 | No | Clear;32-90 F | Secondary | Bent or Twisted | 23-0030402 | OH | Sus | 31636878 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814122 | 0 | Non-EPSS | N | 2023 | PH TIME - TIME INST
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | SWITCH | 32570 | 20230218 | 712 | 20230218 | 855 | 1988074 | 103 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 515 | 37.3826 | -121.9007 | No | Clear;32-90F | Switch (UG) | Normal | 23-0023502 | UG | Sus | 47022706 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814133 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 34134 | 20230218 | 1655 | 20230218 | 1759 | 1988323 | 64 | Distribution Circuit | Animal | Squirrel | 39 | 961 | 37.1442 | -121.6269 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0030485 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814219 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2111 | 82832111 | FUSE | 75087 | 20230219 | 1804 | 20230219 | 1934 | 1988998 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 5814 | 37.4249 | -121.9075 | Yes | Clear;32-90F |  |  | 23-0030577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814328 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | MTR#1011012271 | 20230220 | 950 | 20230220 | 1213 | 1989296 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 286 | 37.223 | -121.8371 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0030624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814429 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 33832 | 20230220 | 1103 | 20230220 | 1320 | 1989385 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 21509 | 37.2334 | -121.8307 | No | Clear;32-90F |  |  | 23-0030671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814467 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | SWITCH | 9948 | 20230220 | 1325 | 20230220 | 1339 | -1989385 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 157 | 2198 | 37.2366 | -121.8376 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0030671 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814473 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | TRANSFORMER | 316054927693 | 20230221 | 919 | 20230221 | 947 | 1989958 | 28 | Transformer only | Vegetation | Tree - grew into line | 4 | 112 | 37.2526 | -121.8566 | Yes | Clear;32-90F | Secondary | Normal | 23-0030853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814670 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 41951 | 20230221 | 951 | 20230221 | 1405 | 1989981 | 254 | Distribution Circuit | Vegetation | Tree - grew into line | 454 | 115316 | 37.3422 | -121.8731 | Yes |  | Conductor- Overhead | Normal | 23-0030800 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1814684 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 4655 | 20230221 | 1027 | 20230222 | 118 | 1990091 | 891 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 891 | 37.1562 | -121.6712 | Yes | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0031072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814798 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | FUSE | 75461 | 20230221 | 1154 | 20230221 | 1919 | 1990235 | 445 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 58 | 25932 | 37.3386 | -121.88 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0031040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814773 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15749 | 20230221 | 1319 | 20230221 | 1458 | 1990609 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 227 | 22473 | 37.3675 | -121.8048 | Yes | Clear;32-90 F |  |  | 23-0031160 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814855 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 12767 | 20230221 | 1332 | 20230222 | 1650 | 1993105 | 1638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 910 | 131459 | 37.3148 | -121.8194 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0031466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815101 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316080331461 | 20230221 | 1345 | 20230222 | 2345 | 1990912 | 2040 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 24480 | 37.3562 | -121.8496 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0032818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816163 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 71353 | 20230221 | 1348 | 20230221 | 1534 | 1990956 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 9010 | 37.305 | -121.9924 | Yes | Clear;32-90 F |  |  | 23-0031262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814925 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | RECLOSER | XR066 | 20230221 | 1400 | 20230221 | 1600 | 1991203 | 120 | Distribution Circuit | Vegetation | Tree - branch fell on line | 995 | 119400 | 37.311 | -121.9076 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031156 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1814852 | 0 | Non-EPSS | N | 2023 | A & B PHASE
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315957328249 | 20230221 | 1406 | 20230222 | 2047 | 1991336 | 1841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 23352 | 37.2676 | -121.8904 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0031504 | OH | Sus | 35427391 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815133 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | OCB | 2108/2 | 20230221 | 1434 | 20230221 | 1733 | 1991860 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1536 | 274944 | 37.2448 | -121.7953 | Yes | Clear;32-90 F |  |  | 23-0031294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1814952 | 0 | Non-EPSS | N | 2023 | B AND G
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315956728278 | 20230221 | 1437 | 20230222 | 1831 | 1991746 | 1674 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 28458 | 37.2684 | -121.8906 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032351 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815852 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 28111 | 20230221 | 1453 | 20230222 | 2041 | 1991980 | 1788 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 89400 | 37.0676 | -121.5559 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0031949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815547 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20230221 | 1500 | 20230221 | 1837 | 1992128 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 776 | 168392 | 37.133 | -121.6122 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0031335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1814991 | 0 | EPSS Ckt | N | 2023 | C PHASE & GRD
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 30034 | 20230221 | 1501 | 20230221 | 1908 | 1992086 | 247 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1454 | 359138 | 37.2992 | -121.8232 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0031621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815243 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 25449 | 20230221 | 1504 | 20230223 | 25 | 1992113 | 2001 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 16008 | 37.1549 | -121.6888 | Yes | Clear;32-90 F |  |  | 23-0032824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816169 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 28143 | 20230221 | 1507 | 20230221 | 2034 | 1992145 | 327 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 9483 | 37.2424 | -121.8331 | Yes | Clear;32-90 F |  |  | 23-0031852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815450 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 469810 | 20230221 | 1511 | 20230223 | 1931 | 1992219 | 3140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 53380 | 37.2003 | -121.7222 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814977 | 0 | EPSS Ckt | N | 2023 | A PHASE & GRD
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 6841 | 20230221 | 1511 | 20230221 | 1818 | 1992197 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 191 | 35717 | 37.327 | -121.9302 | Yes | Clear;32-90 F |  |  | 23-0031645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815264 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 27997 | 20230221 | 1512 | 20230222 | 1648 | 1992307 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23040 | 37.2114 | -121.8612 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0031652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815270 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 7403 | 20230221 | 1517 | 20230222 | 951 | 1992305 | 1114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 151 | 168670 | 37.3216 | -121.9171 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0031494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815123 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | JUMPER | OJ SOURCE OF CGC 316188628078 | 20230221 | 1518 | 20230223 | 205 | 1992324 | 2087 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 52175 | 37.2632 | -121.8115 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0031551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815177 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230221 | 1519 | 20230223 | 2245 | 1992370 | 3326 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 96454 | 37.1602 | -121.666 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0031684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815295 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 72477 | 20230221 | 1529 | 20230223 | 1650 | 1992462 | 2961 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 242802 | 37.3115 | -121.9457 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815164 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1451 | 20230221 | 1533 | 20230222 | 1914 | 1992494 | 1661 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 45141 | 37.0061 | -121.5108 | Yes |  |  |  | 23-0031747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815349 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15749 | 20230221 | 1534 | 20230225 | 442 | 1992531 | 5108 | Distribution Circuit | Equipment Failure/Involved | Underground | 227 | 366517 | 37.3675 | -121.8048 | Yes | Clear;32-90 F | Conductor- Underground | Broken | 23-0032482 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815925 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40723 | 20230221 | 1535 | 20230222 | 2142 | 1998702 | 1807 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1807 | 37.0643 | -121.6922 | Yes | Clear;32-90 F |  |  | 23-0032777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816146 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 11065 | 20230221 | 1537 | 20230221 | 1840 | 1992554 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 255 | 46665 | 37.2944 | -121.8345 | Yes | Clear;32-90 F |  |  | 23-0031628 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815250 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3747 | 20230221 | 1537 | 20230223 | 1618 | 1992574 | 2921 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 306705 | 37.087 | -121.655 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815870 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | JUMPER | OJ 2 E/OF M61 | 20230221 | 1546 | 20230223 | 1512 | 1992709 | 2846 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1754 | 2188422 | 37.1008 | -121.6213 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0031958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815556 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 18753 | 20230221 | 1547 | 20230222 | 1751 | 1992718 | 1564 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 81016 | 37.28 | -121.8905 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815122 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 28321 | 20230221 | 1550 | 20230222 | 1603 | 1992756 | 1453 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 72650 | 37.1498 | -121.5953 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0032585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816004 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 13789 | 20230221 | 1600 | 20230222 | 1436 | 1992865 | 1356 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 171 | 231876 | 37.4313 | -121.8854 | Yes | Clear;32-90 F |  |  | 23-0032466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815915 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315758529327 | 20230221 | 1601 | 20230223 | 1655 | 1993091 | 2934 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 20538 | 37.2966 | -121.959 | Yes | Partly Cloudy-Strong Winds;32-90 F | Secondary | Broken | 23-0031772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815371 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | RECLOSER | XR066 | 20230221 | 1603 | 20230221 | 1645 | 1992946 | 42 | Distribution Circuit | Vegetation | Tree - branch fell on line | 995 | 41790 | 37.311 | -121.9076 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815071 | 0 | Non-EPSS | N | 2023 | A-B & C PHASE
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 17725 | 20230221 | 1605 | 20230222 | 1119 | 1992932 | 1154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 17310 | 37.2229 | -121.8759 | Yes | Clear;32-90 F |  |  | 23-0032246 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815798 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2101 | 83892101 | FUSE | 43387 | 20230221 | 1608 | 20230222 | 1157 | 1992969 | 1189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 130790 | 37.4046 | -121.9057 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0031819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815416 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 72087 | 20230221 | 1611 | 20230221 | 1923 | 1993015 | 192 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 7680 | 37.3158 | -121.9749 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0031755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815357 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 72191 | 20230221 | 1616 | 20230222 | 1033 | 1996636 | 1097 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 36201 | 37.3656 | -121.8955 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Underground | Contaminated | 23-0032202 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815772 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 41965 | 20230221 | 1618 | 20230222 | 1738 | 1993086 | 1520 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 30400 | 37.3373 | -121.91 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0031631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815253 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 28307 | 20230221 | 1619 | 20230222 | 1219 | 1993088 | 1200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 32400 | 37.2977 | -121.8814 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815831 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OCB | 2111/2 | 20230221 | 1622 | 20230221 | 2051 | 1993143 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5467 | 976143 | 37.2332 | -121.9014 | Yes | Clear;32-90 F |  |  | 23-0031475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815108 | 0 | EPSS Ckt | N | 2023 | A AND B INST
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 71017 | 20230221 | 1624 | 20230223 | 40 | 1993142 | 1936 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 94864 | 37.2473 | -121.8384 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816115 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 71131 | 20230221 | 1639 | 20230222 | 2353 | 1993315 | 1874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 384170 | 37.3428 | -121.8456 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0031780 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815379 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | OCB | 1101/2 | 20230221 | 1641 | 20230221 | 2152 | 1993379 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1372 | 426692 | 37.2448 | -121.7956 | Yes | Clear;32-90 F |  |  | 23-0031528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815154 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 71353 | 20230221 | 1641 | 20230222 | 13 | 1993327 | 452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 38420 | 37.305 | -121.9924 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0031988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815585 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 21233 | 20230221 | 1642 | 20230221 | 2140 | 1995951 | 298 | Distribution Circuit | Vegetation | Tree - bark fell into line | 35 | 10430 | 37.3807 | -121.8265 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815469 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 17099 | 20230221 | 1647 | 20230222 | 1120 | 1993387 | 1113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 178911 | 37.3382 | -121.859 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0032245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815797 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 72585 | 20230221 | 1648 | 20230222 | 1308 | 1993399 | 1220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 37820 | 37.3001 | -121.8708 | Yes | Clear;32-90 F |  |  | 23-0032356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815854 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OCB | 1107/2 | 20230221 | 1650 | 20230222 | 2030 | 1993441 | 1660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1919 | 990400 | 37.3043 | -121.8681 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815157 | 0 | Non-EPSS | N | 2023 | B & C PHASE
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315987828210 | 20230221 | 1653 | 20230222 | 1501 | 1993453 | 1328 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 5312 | 37.2666 | -121.8799 | Yes | Clear;32-90 F |  |  | 23-0032516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815952 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26095 | 20230221 | 1658 | 20230222 | 1301 | 1993529 | 1203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 13233 | 37.0115 | -121.5165 | Yes | Clear;32-90 F |  |  | 23-0032352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815853 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316190631820 | 20230221 | 1659 | 20230224 | 1324 | 1993627 | 4105 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 12315 | 37.3664 | -121.8118 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032695 | OH | Sus | 35427391 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816078 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | TRANSFORMER | 316555424365 | 20230221 | 1703 | 20230222 | 1659 | 1993605 | 1436 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1436 | 37.1631 | -121.683 | Yes | Clear;32-90 F |  |  | 23-0032620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816027 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 8505 | 20230221 | 1709 | 20230221 | 2257 | 1993677 | 348 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 224 | 75577 | 37.2662 | -121.8082 | Yes | Clear;32-90 F |  |  | 23-0031872 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815471 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 434649 | 20230221 | 1710 | 20230222 | 2140 | 1993691 | 1710 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 155 | 265050 | 37.341 | -121.8351 | Yes | Clear;32-90 F |  |  | 23-0032776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816145 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2111 | 82832111 | SWITCH | X2010 | 20230221 | 1713 | 20230224 | 836 | 1992509 | 3724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 290 | 24086 | 37.4316 | -121.9022 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0031563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815187 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT 2107 | 83392107 | FUSE | 2539 | 20230221 | 1716 | 20230223 | 1823 | 1993742 | 2947 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 20629 | 37.3088 | -121.7854 | Yes | Clear;32-90 F | Secondary | Broken | 23-0031831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815429 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42707 | 20230221 | 1728 | 20230224 | 724 | 1993900 | 3716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 148640 | 37.2758 | -121.9144 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1815377 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | OCB | 2108/2 | 20230221 | 1742 | 20230222 | 1551 | 1994234 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 1734 | 265655 | 37.2448 | -121.7953 | Yes | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0031636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815256 | 0 | Non-EPSS | N | 2023 | B AND GRD
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 12033 | 20230221 | 1742 | 20230222 | 1507 | 1997656 | 1285 | Distribution Circuit | Vegetation | Tree - grew into line | 5 | 6425 | 37.265 | -121.8192 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0032371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815862 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 17277 | 20230221 | 1756 | 20230222 | 1103 | 1994482 | 1027 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 49931 | 37.013 | -121.578 | Yes | Clear;32-90 F |  |  | 23-0032235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815792 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | T25464 | 20230221 | 1807 | 20230222 | 1659 | 1994725 | 1372 | Transformer only | Equipment Failure/Involved | Overhead | 76 | 104272 | 37.3046 | -121.8808 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0032617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816025 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1107 | 83801107 | JUMPER | LINE DOWN | 20230221 | 1840 | 20230222 | 1355 | 1995047 | 1155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 101 | 116655 | 37.3862 | -121.9058 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815565 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 100000114463 | 20230221 | 1846 | 20230222 | 1739 | 1993092 | 1373 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 9611 | 37.3024 | -121.8923 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0032644 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816041 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 13473 | 20230221 | 1847 | 20230222 | 1436 | 1995112 | 1189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 29725 | 37.1186 | -121.5842 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0032473 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815920 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | JUMPER | OJ LD SIDE 3259 | 20230221 | 1848 | 20230222 | 2216 | 1995119 | 1648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 70864 | 37.0959 | -121.5794 | Yes | Clear-Strong Winds;32-90 F | Jumper | Burned Open | 23-0032531 | OH | Sus | 35427391 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815961 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRIP-SAVER | 8439 | 20230221 | 1849 | 20230222 | 1602 | 1994456 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 562 | 356542 | 37.4349 | -121.913 | Yes | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0031763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815364 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS SUB | 8318 | JUMPER | CB 122 | 20230221 | 1852 | 20230223 | 354 | 1995213 | 1982 | Distribution Circuit | Equipment Failure/Involved | Underground | 10914 | 5332499 | 37.0073 | -121.557 | Yes | Partly Cloudy-Strong Winds;32-90 F | Switch (UG) | Failed/Faulted | 23-0031769 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1815369 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | JUMPER | BURNT OPEN JUMPERS SOURCE SIDE OF 25201 | 20230221 | 1930 | 20230223 | 1505 | 1995520 | 2615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 384300 | 37.1266 | -121.6623 | Yes | Partly Cloudy-Strong Winds;32-90 F | Jumper | Burned Open | 23-0032276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1815814 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | SWITCH | X1748 | 20230221 | 2103 | 20230221 | 2331 | 1993859 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2976 | 440448 | 37.2958 | -121.8359 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815482 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | FUSE | 19575 | 20230221 | 2211 | 20230221 | 2353 | 1996162 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 23460 | 37.2464 | -121.8123 | Yes | Clear;32-90 F |  |  | 23-0031941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815540 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316487125140 | 20230221 | 2223 | 20230224 | 17 | 1996176 | 2994 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3201 | 37.1842 | -121.7069 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0031936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815535 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | TRANSFORMER | 315958231873 | 20230222 | 451 | 20230223 | 1915 | 1996399 | 2304 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2304 | 37.3671 | -121.8919 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0032126 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815713 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 1687 | 20230222 | 717 | 20230223 | 2330 | 1996595 | 2413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 7239 | 37.4318 | -121.9634 | No | Clear;32-90 F | Jumper | Arcing | 23-0032262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815808 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 12767 | 20230222 | 837 | 20230222 | 1417 | 1996863 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 870 | 295800 | 37.3148 | -121.8194 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815871 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 12835 | 20230222 | 913 | 20230222 | 2000 | 1998564 | 647 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 647 | 37.1649 | -121.6384 | No | Clear;32-90 F |  |  | 23-0032723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816104 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 41673 | 20230222 | 930 | 20230223 | 1530 | 1997018 | 1800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 54270 | 37.2856 | -121.8439 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0032314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1815833 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | SWITCH | 63714SW | 20230222 | 936 | 20230222 | 1803 | 1996947 | 507 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 28392 | 37.381 | -121.8264 | No | Clear;32-90 F |  |  | 23-0032584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816003 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315932128253 | 20230222 | 1048 | 20230222 | 1346 | 1997253 | 178 | Transformer only | Vegetation | Tree - grew into line | 16 | 2848 | 37.2676 | -121.899 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0032457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815907 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316472525165 | 20230222 | 1212 | 20230222 | 2328 | 1997532 | 676 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 2704 | 37.185 | -121.712 | No | Clear;32-90 F |  |  | 23-0032822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1816167 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315876127914 | 20230222 | 1345 | 20230224 | 122 | 1993097 | 2137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 52088 | 37.2581 | -121.9181 | No | Clear;32-90 F | Secondary | Broken- wire on object | 23-0032435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1815895 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 42959 | 20230222 | 1519 | 20230223 | 1717 | 1999649 | 1558 | Distribution Circuit | Vegetation | Tree - grew into line | 88 | 137104 | 37.2874 | -121.9102 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816344 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315794429709 | 20230222 | 1644 | 20230222 | 2227 | 1998269 | 343 | Transformer only | Vegetation | Tree - fell into line | 60 | 20580 | 37.3069 | -121.9471 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0032802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816153 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE 1102 | 82951102 | FUSE | 18073 | 20230222 | 1823 | 20230223 | 1434 | 1998461 | 1211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 12110 | 37.2201 | -121.7872 | No | Clear;32-90 F |  |  | 23-0032679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816065 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316191931826 | 20230222 | 2054 | 20230224 | 1323 | 1998668 | 2429 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 14574 | 37.3666 | -121.8113 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0032823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816168 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 18223 | 20230222 | 2127 | 20230223 | 1542 | 1998696 | 1095 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 51126 | 37.3223 | -121.8732 | No | Partly Cloudy;32-90 F |  |  | 23-0033288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816373 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | 316011730243 | 20230222 | 2143 | 20230224 | 1430 | 1998704 | 2447 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 12235 | 37.3225 | -121.8727 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0033307 | OH | Sus | 35427391 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816386 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | JUMPER | OPEN JUMPERS 1 S/W/O CGC #315958432271 | 20230223 | 723 | 20230224 | 1150 | 1998917 | 1707 | Distribution Circuit | Vegetation | Tree - bark fell into line | 6 | 10242 | 37.378 | -121.8929 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033058 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816268 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316080331461 | 20230223 | 1021 | 20230225 | 1702 | 1999220 | 3281 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 39372 | 37.3562 | -121.8496 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0033122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1816295 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 41791 | 20230223 | 1317 | 20230223 | 1402 | 1999549 | 45 | Distribution Circuit | Vegetation | Tree - grew into line | 61 | 2745 | 37.3189 | -121.9634 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816315 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 6469 | 20230223 | 1325 | 20230223 | 1845 | 1999560 | 320 | Distribution Circuit | Equipment Failure/Involved | Underground | 135 | 43200 | 37.286 | -121.8293 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0033072 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816318 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | OCB | 1105/2 | 20230223 | 1729 | 20230223 | 1818 | 2000142 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3362 | 53165 | 37.341 | -121.9019 | Yes | Partly Cloudy;32-90 F |  |  | 23-0033360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1816413 | 0 | Non-EPSS | N | 2023 | A/B/C
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 40177 | 20230223 | 1901 | 20230225 | 1045 | 2000297 | 2384 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 3176 | 37.3305 | -121.7663 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0033422 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816455 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 13031 | 20230223 | 2131 | 20230223 | 2249 | 2000694 | 78 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 13572 | 37.3067 | -121.8925 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0033471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816501 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 43239 | 20230223 | 2158 | 20230223 | 2306 | 2000742 | 68 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 680 | 37.3066 | -121.905 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0033480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816512 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 72107 | 20230223 | 2245 | 20230224 | 9 | 2000839 | 84 | Distribution Circuit | 3rd Party | Metallic Balloon | 117 | 9828 | 37.3197 | -121.9187 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0033510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816542 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11885 | 20230224 | 47 | 20230224 | 1756 | 2001410 | 1029 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 33957 | 37.3827 | -121.8171 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0033576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816612 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OCB | 2111/2 | 20230224 | 237 | 20230224 | 406 | 2001921 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5328 | 124612 | 37.2332 | -121.9014 | Yes | Overcast-Snow;32-90 F | Circuit Breaker | Normal | 23-0033585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816621 | 0 | EPSS Ckt | N | 2023 | A-B-C-GRD INST(50) TRGTS
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316009030723 | 20230224 | 534 | 20230225 | 1858 | 2002892 | 2244 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 38148 | 37.3357 | -121.8739 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0033863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816869 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 20230224 | 649 | 20230226 | 1813 | 2003572 | 3564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 245916 | 37.3568 | -121.5253 | Yes | Clear;32-90 F | Insulator | Broken | 23-0033732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816763 | 0 | EPSS Ckt | N | 2023 | INST
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | JUMPER | OJS CORNER WOODLAWN & FIRESIDE | 20230224 | 1011 | 20230224 | 1621 | 2004946 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 10730 | 37.3041 | -121.9477 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0033967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1816944 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | FUSE | 6401 | 20230224 | 1024 | 20230225 | 1545 | s1817087 | 1761 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1761 | 37.4038 | -121.8995 | Yes | Clear;32-90 F | Transformer (UG) | Leaking | 23-0034178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817087 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 92776 | 20230224 | 1104 | 20230226 | 1640 | 2008822 | 3216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 35376 | 37.3709 | -121.6728 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818251 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315678229944 | 20230224 | 1412 | 20230224 | 1849 | 1993121 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2216 | 37.3135 | -121.9869 | Yes | Clear;32-90 F | Secondary | Broken | 23-0034225 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817122 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 26599 | 20230224 | 1618 | 20230224 | 1819 | 2006219 | 121 | Distribution Circuit | Vegetation | Tree - grew into line | 26 | 3146 | 37.3429 | -121.7898 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817233 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 73387 | 20230224 | 1719 | 20230224 | 1820 | 2006435 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 305 | 37.1646 | -121.6384 | Yes | Clear;32-90 F |  |  | 23-0034434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817288 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316159128577 | 20230224 | 1935 | 20230225 | 28 | 2006845 | 293 | Transformer only | Vegetation | Tree - grew into line | 8 | 2344 | 37.2773 | -121.8212 | Yes | Clear;32-90 F | Secondary | Contaminated | 23-0034528 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817378 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 9730 | 20230224 | 2122 | 20230225 | 2100 | 2007223 | 1418 | Distribution Circuit | Equipment Failure/Involved | Underground | 141 | 55518 | 37.2371 | -121.8201 | Yes | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0034806 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1817666 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 943083 | 20230225 | 956 | 20230226 | 1125 | 2007834 | 1529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 265 | 6719 | 37.3018 | -121.9011 | Yes | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0035122 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1817985 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | JUMPER | OJ 2/S OF CGC 7784 | 20230225 | 1023 | 20230225 | 1242 | 2008224 | 139 | Distribution Circuit | Vegetation | Tree - grew into line | 102 | 14178 | 37.2542 | -121.913 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0035135 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1817998 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20230225 | 1325 | 20230225 | 1433 | 2008539 | 42 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4258 | 220948 | 37.4156 | -121.8881 | Yes | Partly Cloudy;32-90 F |  |  | 23-0035267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818105 | 0 | EPSS Ckt | N | 2023 | A & C PH OC
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | SWITCH | 25626 | 20230225 | 1438 | 20230225 | 1916 | 2009007 | 278 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1 | 278 | 37.3769 | -121.9141 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0035322 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818245 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20230225 | 1634 | 20230225 | 1802 | 2008953 | 88 | Distribution Circuit | Vegetation | Tree - grew into line | 4258 | 150117 | 37.4156 | -121.8881 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0035384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818221 | 0 | EPSS Ckt | N | 2023 | A & C PH OC
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | TRANSFORMER | T10486 | 20230225 | 1914 | 20230226 | 708 | 2008790 | 714 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 1674 | 37.3637 | -121.8794 | Yes | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0035461 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818309 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315932128253 | 20230226 | 905 | 20230226 | 1128 | 2009756 | 143 | Transformer only | Vegetation | Tree - grew into line | 16 | 2288 | 37.2676 | -121.899 | Yes | Clear;32-90 F | Secondary | Normal | 23-0035622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1818469 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 12881 | 20230226 | 2002 | 20230228 | 56 | 2010854 | 1734 | Distribution Circuit | Equipment Failure/Involved | Underground | 892 | 193264 | 37.3499 | -121.8527 | Yes | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 23-0036005 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1818814 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 40232 | 20230226 | 2051 | 20230227 | 1150 | 2010913 | 899 | Distribution Circuit | Equipment Failure/Involved | Underground | 84 | 51787 | 37.3132 | -121.84 | Yes | Overcast-Rain;32-90 F | Transformer (UG) | Broken | 23-0036056 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818865 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15919 | 20230227 | 636 | 20230227 | 800 | 2011191 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1510 | 37.1947 | -121.8067 | Yes | Clear;32-90 F |  |  | 23-0036087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1818878 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315802330715 | 20230227 | 1044 | 20230227 | 2200 | 2013925 | 676 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 8112 | 37.3353 | -121.9446 | Yes | Clear;32-90F | Secondary | Deteriorated | 23-0036992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819531 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 42147 | 20230227 | 1050 | 20230227 | 1255 | 2011864 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 250 | 37.2879 | -121.8251 | Yes | Clear;32-90F |  |  | 23-0036402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819052 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1081 | 20230227 | 1206 | 20230227 | 1318 | 2012155 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 2736 | 36.9982 | -121.5243 | Yes | Clear;32-90F |  |  | 23-0036413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819057 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 200771 | 20230227 | 1234 | 20230227 | 1425 | 2012229 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 4440 | 37.3736 | -121.8216 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0036312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819043 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | C2453 | 20230227 | 1330 | 20230228 | 618 | 2012460 | 1008 | Transformer only | Equipment Failure/Involved | Underground | 90 | 90720 | 37.3157 | -121.8402 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0036628 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819199 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | T12530 | 20230227 | 1351 | 20230228 | 547 | 2012906 | 956 | Transformer only | Equipment Failure/Involved | Underground | 10 | 9560 | 37.3143 | -121.8404 | Yes | Overcast-Rain;32-90 F | Transformer (UG) | Leaking | 23-0036597 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1819174 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR366 | 20230227 | 1723 | 20230303 | 1755 | 2013289 | 5792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 392 | 783652 | 37.3326 | -121.7785 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819309 | 0 | EPSS Ckt | N | 2023 | B & C PH
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR366 | 20230227 | 1723 | 20230303 | 1755 | 2013289 | 5792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 392 | 783652 | 37.3326 | -121.7785 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1819309 | 0 | EPSS Ckt | N | 2023 | B & C PH
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | SWITCH | 40232SW | 20230227 | 1959 | 20230228 | 538 | 2012907 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 74 | 892 | 37.3132 | -121.84 | Yes | Overcast-Rain;32-90 F | Transformer (UG) | Leaking | 23-0036597 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819460 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 14763 | 20230228 | 20 | 20230228 | 202 | 2014057 | 102 | Distribution Circuit | Animal | Bird found | 156 | 15754 | 37.3901 | -121.8141 | Yes | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0037040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1819574 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 11323 | 20230228 | 948 | 20230228 | 1824 | 2014710 | 516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 516 | 37.3071 | -121.9208 | Yes | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0037195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819658 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 13025 | 20230228 | 1612 | 20230301 | 310 | 2016149 | 658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 37506 | 37.3202 | -121.8873 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0037838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1820167 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | OTHER | WIRE DOWN CGC #0364 | 20230228 | 2247 | 20230301 | 742 | 2017287 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 96245 | 37.3253 | -121.9269 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1820194 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OCB | 2107/2 | 20230301 | 703 | 20230301 | 741 | 2017682 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3890 | 147820 | 37.0071 | -121.5569 | No | Overcast;32-90 F | Switch (OH) | Arcing | 23-0037938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820264 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 6759 | 20230301 | 1700 | 20230301 | 2152 | 2018876 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8284 | 37.0047 | -121.5555 | No | Clear;32-90 F | Switch (OH) | Arcing | 23-0038332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820607 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315774729355 | 20230301 | 2155 | 20230301 | 2209 | 2019170 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 67 | 938 | 37.2974 | -121.9536 | No | Clear;32-90F | Secondary | Burned/flashed | 23-0038539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820722 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | T9760 | 20230301 | 2300 | 20230301 | 2352 | 2019294 | 52 | Transformer only | Equipment Failure/Involved | Underground | 9 | 468 | 37.209 | -121.8409 | No | Clear;32-90F | Secondary | Deteriorated | 23-0038544 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1820727 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 42145 | 20230302 | 1806 | 20230303 | 300 | 2020383 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 711 | 37.2616 | -121.8039 | No | Clear;32-90F | Pothead(Riser Termination) | Burned/flashed | 23-0039029 | OH | Sus | 35427391 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821023 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315888727463 | 20230303 | 1917 | 20230304 | 1307 | 2021730 | 1070 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 14980 | 37.2458 | -121.9135 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0039698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821452 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 2525 | 20230304 | 626 | 20230304 | 838 | 2022079 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1141 | 37.06 | -121.5927 | No | Clear;32-90F |  |  | 23-0039879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821645 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 25449 | 20230304 | 1051 | 20230304 | 1439 | 2022278 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1824 | 37.1549 | -121.6888 | No | Clear;32-90F |  |  | 23-0040005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1821760 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | TRANSFORMER | 316645518900 | 20230304 | 1219 | 20230305 | 57 | 2022404 | 758 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3032 | 37.0131 | -121.6497 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821806 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 13053 | 20230305 | 240 | 20230305 | 418 | 2023146 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 325 | 31899 | 37.2455 | -121.8926 | No | Clear;32-90 F |  |  | 23-0040208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821957 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315999730495 | 20230305 | 1043 | 20230305 | 1637 | 2023631 | 354 | Transformer only | Vegetation | Tree - fell into line | 29 | 10266 | 37.3294 | -121.877 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0040424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1822155 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 21267 | 20230305 | 1148 | 20230305 | 1327 | 2023681 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 339 | 33561 | 37.2622 | -121.8798 | No | Clear;32-90 F | Fuse | Burned Open | 23-0040356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822081 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316167730022 | 20230305 | 2036 | 20230306 | 442 | 2024133 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 221 | 30875 | 37.317 | -121.8189 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0040535 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822269 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 2171 | 20230306 | 123 | 20230306 | 544 | 2024200 | 261 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 35496 | 37.2268 | -121.8947 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0040544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822280 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315904628328 | 20230307 | 1639 | 20230307 | 1830 | 2025862 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1887 | 37.2696 | -121.9085 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0041329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822668 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OCB | 1107/2 | 20230307 | 1846 | 20230308 | 1149 | 2025962 | 1023 | Distribution Circuit | 3rd Party | Vehicle | 1918 | 144728 | 37.3043 | -121.8681 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0041380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822707 | 0 | Non-EPSS | N | 2023 | NEU/GRD
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | MTR#1006781892 | 20230308 | 259 | 20230308 | 629 | 2026177 | 210 | Transformer only | 3rd Party | Fire- house or bldg. | 20 | 4200 | 37.3085 | -121.8137 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0041457 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1822787 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 27075 | 20230308 | 842 | 20230309 | 322 | 2026367 | 1120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 35749 | 37.0148 | -121.5858 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0041653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822906 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 3037 | 20230308 | 931 | 20230308 | 1216 | 2026462 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1485 | 37.1769 | -121.8205 | No | Clear;32-90F |  |  | 23-0041666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822915 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20230308 | 1107 | 20230308 | 1416 | 2026597 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 16632 | 37.2267 | -121.8632 | No | Clear;32-90 F |  |  | 23-0041734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822930 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | SWITCH | 8025 | 20230308 | 1307 | 20230309 | 253 | 2026789 | 826 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2606 | 37.3227 | -121.8123 | No | Clear;32-90 F | Jumper | Burned Open | 23-0041745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1822946 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 316003230620 | 20230308 | 1434 | 20230309 | 325 | 2026798 | 771 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 23130 | 37.3328 | -121.8759 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0041853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1822991 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRIP-SAVER | 8439 | 20230309 | 1503 | 20230309 | 1655 | 2027867 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 20960 | 37.4349 | -121.913 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0042299 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823168 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316191532175 | 20230309 | 1507 | 20230309 | 2045 | 2027877 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2366 | 37.3762 | -121.8116 | Yes | Clear;32-90F | Secondary | Deteriorated | 23-0042539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1823358 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315924928092 | 20230309 | 1723 | 20230309 | 1805 | 2028234 | 42 | Transformer only | Vegetation | Tree - grew into line | 15 | 630 | 37.2632 | -121.9014 | Yes | Clear;32-90F | Secondary | Arcing | 23-0042408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823246 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 405/2 | 20230309 | 1723 | 20230309 | 1835 | 2028237 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 595 | 42840 | 37.3281 | -121.9025 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0042380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823220 | 0 | Non-EPSS | N | 2023 | C PH OC
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15741 | 20230309 | 2207 | 20230310 | 56 | 2029533 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1352 | 37.1992 | -121.8221 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0042645 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823455 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15919 | 20230310 | 644 | 20230310 | 905 | 2030200 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 7614 | 37.1947 | -121.8067 | No | Clear;32-90F |  |  | 23-0042781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823581 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | INTERRUPTER | 6534 | 20230310 | 716 | 20230310 | 824 | 2030311 | 68 | Distribution Circuit | Animal | Bird found | 670 | 45560 | 37.3206 | -121.7958 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0042811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823596 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20230310 | 1141 | 20230310 | 1904 | 2030728 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 506 | 40265 | 37.3558 | -121.8299 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823698 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 12981 | 20230310 | 1146 | 20230311 | 1046 | 2030849 | 1380 | Distribution Circuit | Equipment Failure/Involved | Underground | 114 | 56016 | 37.4035 | -121.8488 | No | Overcast-Fog;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0043083 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823727 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20230310 | 1405 | 20230310 | 1714 | 2031122 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 23476 | 37.2174 | -121.8338 | No | Overcast-Drizzle;32-90 F |  |  | 23-0043214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823807 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | SWITCH | 24297 | 20230310 | 1417 | 20230310 | 1445 | 2031177 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1037 | 17303 | 37.2671 | -121.9191 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Deteriorated | 23-0042385 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823759 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 17537 | 20230310 | 1428 | 20230310 | 2202 | 2031179 | 454 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 14074 | 37.3438 | -121.8205 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0043262 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823849 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315710829778 | 20230310 | 1543 | 20230310 | 2015 | 2031312 | 272 | Transformer only | Vegetation | Tree - branch fell on line | 16 | 4352 | 37.3088 | -121.9755 | No | Clear;32-90F | Secondary | Normal | 23-0043186 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1823783 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OCB | 2111/2 | 20230311 | 221 | 20230311 | 1706 | 2031818 | 836 | Distribution Circuit | 3rd Party | Vehicle | 5467 | 499933 | 37.2332 | -121.9014 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0043324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823910 | 0 | EPSS Ckt | N | 2023 | A & B (50)
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20230311 | 733 | 20230311 | 1707 | 2031972 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 36736 | 37.0838 | -121.7753 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Together | 23-0043355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1823935 | 0 | EPSS Ckt | N | 2023 | B & C
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 4253 | 20230311 | 2004 | 20230312 | 1930 | 2032880 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7030 | 37.0457 | -121.7231 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824220 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20230312 | 134 | 20230312 | 600 | 2032990 | 266 | Distribution Circuit | 3rd Party | Vehicle | 373 | 99218 | 37.2174 | -121.8338 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0043631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824173 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316053830124 | 20230312 | 347 | 20230312 | 526 | 2033039 | 99 | Transformer only | 3rd Party | Fire- house or bldg. | 7 | 693 | 37.3192 | -121.858 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0043627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824169 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26169 | 20230312 | 455 | 20230312 | 1600 | 2033051 | 665 | Distribution Circuit | Animal | Bird found | 3 | 1993 | 37.0516 | -121.5524 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824244 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 1891 | 20230312 | 1431 | 20230312 | 2118 | 2033385 | 407 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 3414 | 37.2202 | -121.843 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Underground | Burned/flashed | 23-0043756 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824272 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316795423060 | 20230312 | 1926 | 20230312 | 2120 | 2033655 | 114 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 570 | 37.1282 | -121.6002 | No | Clear;32-90 F |  |  | 23-0043809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1824323 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | SWITCH | 28024 | 20230313 | 915 | 20230314 | 39 | 2034175 | 924 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 41343 | 37.3199 | -121.8416 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0044116 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824541 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316058730128 | 20230313 | 1331 | 20230314 | 1111 | 2034552 | 1300 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1300 | 37.3194 | -121.8566 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0044341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824616 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315929727097 | 20230313 | 1508 | 20230313 | 2206 | 2034745 | 418 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3762 | 37.2358 | -121.8993 | No | Clear;32-90F | Transformer (OH) | Contaminated | 23-0044264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824580 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315929727097 | 20230313 | 2230 | 20230314 | 247 | 2035110 | 257 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 2313 | 37.2358 | -121.8993 | No | Clear;32-90 F | Transformer | Malfunctioning | 23-0044458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824724 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | C1906 | 20230313 | 2351 | 20230314 | 1739 | 2035108 | 1068 | Transformer only | Vegetation | Tree - fell into line | 25 | 26700 | 37.2959 | -121.8179 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0044457 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1824723 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | JUMPER | 1 POLE SS OF 828 BARELEY AVE | 20230314 | 104 | 20230314 | 256 | 2035138 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 3808 | 37.2992 | -121.8844 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0044460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1824726 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 103451 | 20230314 | 712 | 20230314 | 1017 | 2035227 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2035 | 37.3846 | -121.8006 | Yes | Clear;32-90F |  |  | 23-0044663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1824816 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315878827454 | 20230314 | 1020 | 20230316 | 1459 | 2046003 | 3159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 26802 | 37.2455 | -121.9169 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0046276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826120 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | 316044726549 | 20230314 | 1046 | 20230317 | 1526 | 2036064 | 4600 | Transformer only | Vegetation | Tree - fell into line | 17 | 78200 | 37.2212 | -121.8593 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0047545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826880 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 13099 | 20230314 | 1052 | 20230314 | 1315 | 2036165 | 143 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 200 | 28600 | 37.3541 | -121.8777 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045088 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825150 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 15085 | 20230314 | 1104 | 20230315 | 1543 | 2036337 | 1719 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 84231 | 37.2264 | -121.8957 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0046458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826231 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316144732103 | 20230314 | 1128 | 20230315 | 638 | 2037191 | 1150 | Transformer only | Vegetation | Tree - fell into line | 15 | 17250 | 37.374 | -121.8277 | Yes | Clear;32-90F | Secondary | Broken | 23-0046036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825953 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 14989 | 20230314 | 1132 | 20230317 | 1550 | 2042529 | 4578 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 215166 | 37.2363 | -121.922 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825381 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 103451 | 20230314 | 1137 | 20230314 | 1903 | 2037633 | 446 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 4906 | 37.3846 | -121.8006 | Yes | Clear;32-90F |  |  | 23-0045766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825696 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | OTHER | WIRE DOWN 1 P/S/OF CGC #6630 | 20230314 | 1140 | 20230315 | 1633 | 2040588 | 1733 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1948 | 2719790 | 37.223 | -121.8732 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | Yes | 1825218 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11939 | 20230314 | 1150 | 20230315 | 505 | 2037659 | 1035 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 109710 | 37.2222 | -121.8624 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825985 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | FUSE | 27099 | 20230314 | 1155 | 20230315 | 530 | 2037785 | 1055 | Distribution Circuit | Vegetation | Tree - branch fell on line | 520 | 548600 | 37.2472 | -121.9028 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0046069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825991 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20230314 | 1201 | 20230315 | 2056 | 2040433 | 1975 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3265 | 2181906 | 37.1066 | -121.6618 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045236 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825264 | 0 | EPSS Ckt | N | 2023 | A- B - C PHASE TARGET
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20230314 | 1208 | 20230315 | 2035 | 2038233 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 145302 | 37.1869 | -121.8177 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044964 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1825048 | 0 | EPSS Ckt | N | 2023 | A & C TARGET
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 72087 | 20230314 | 1213 | 20230314 | 1625 | 2038694 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 10080 | 37.3158 | -121.9749 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825498 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 42183 | 20230314 | 1214 | 20230315 | 1904 | 2043688 | 1850 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 138750 | 37.2364 | -121.9006 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0045641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825584 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | TRANSFORMER | 315906427341 | 20230314 | 1221 | 20230316 | 1223 | 2038532 | 2882 | Transformer only | Vegetation | Tree - branch fell on line | 25 | 72050 | 37.2421 | -121.9075 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer | Broken- wire on ground | 23-0046638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826344 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20230314 | 1224 | 20230315 | 1907 | 2038695 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3266 | 6012286 | 37.2332 | -121.9012 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825093 | 0 | Non-EPSS | N | 2023 | A & B PHASE TARGET
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 28429 | 20230314 | 1234 | 20230316 | 2143 | 2038991 | 3429 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 75438 | 37.414 | -121.7799 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826687 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | OCB | 2111/2 | 20230314 | 1238 | 20230314 | 1642 | 2036619 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5467 | 1330416 | 37.2332 | -121.9014 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0045059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825127 | 0 | EPSS Ckt | N | 2023 | A- B- C TARGET
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230314 | 1241 | 20230316 | 245 | 2039196 | 2284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 66236 | 37.1602 | -121.666 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826451 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20230314 | 1242 | 20230315 | 1638 | 2040728 | 1676 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 208174 | 37.2174 | -121.8338 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826268 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230314 | 1243 | 20230315 | 1317 | 2039319 | 1474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 114972 | 37.2239 | -121.8583 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826138 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316092827356 | 20230314 | 1244 | 20230316 | 1731 | 2044527 | 3167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 48436 | 37.2434 | -121.8433 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0045821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825743 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316094927402 | 20230314 | 1244 | 20230316 | 1731 | 2044528 | 3167 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 22169 | 37.2447 | -121.8426 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0046672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826359 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | FUSE | 13677 | 20230314 | 1244 | 20230315 | 8 | 2039299 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 160056 | 37.2471 | -121.9104 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0045735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825671 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 26917 | 20230314 | 1245 | 20230315 | 2055 | 2043123 | 1930 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 326170 | 37.0998 | -121.6727 | Yes | Clear;32-90 F |  |  | 23-0045518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1825481 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 3069 | 20230314 | 1249 | 20230315 | 1456 | 2039567 | 1567 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 57979 | 37.1606 | -121.6814 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0046434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826217 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 15103 | 20230314 | 1249 | 20230317 | 1318 | 2039606 | 4349 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17396 | 37.1383 | -121.6687 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0046742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826395 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 70217 | 20230314 | 1254 | 20230314 | 1616 | 2039546 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 6868 | 37.2954 | -121.9133 | Yes | Clear;32-90F |  |  | 23-0045407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825391 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 3159 | 20230314 | 1255 | 20230315 | 1936 | 2040257 | 1841 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 44184 | 37.0135 | -121.6347 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0046654 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826353 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 2501 | 20230314 | 1257 | 20230315 | 1715 | 2046370 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 54336 | 37.1502 | -121.7491 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1826202 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 4243 | 20230314 | 1259 | 20230315 | 2054 | 2039724 | 1915 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 22980 | 37.0612 | -121.5964 | Yes | Clear;32-90 F |  |  | 23-0046692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826373 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 75523 | 20230314 | 1304 | 20230316 | 1536 | 2046743 | 3032 | Distribution Circuit | Vegetation | Tree - branch fell on line | 468 | 290959 | 37.2447 | -121.8469 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0046540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826279 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 13539 | 20230314 | 1306 | 20230315 | 2000 | 2043927 | 1854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3708 | 37.0786 | -121.6725 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825625 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315911628923 | 20230314 | 1307 | 20230314 | 1502 | 2040626 | 115 | Transformer only | Vegetation | Tree - grew into line | 8 | 920 | 37.2859 | -121.9065 | Yes | Clear;32-90F | Secondary | Normal | 23-0045176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825223 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OCB | 2110/2 | 20230314 | 1308 | 20230314 | 2246 | 2040185 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 2982 | 1344712 | 37.1267 | -121.6596 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045393 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825378 | 0 | EPSS Ckt | N | 2023 | SET A RLY & MAINT ALARM
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26057 | 20230314 | 1310 | 20230315 | 1841 | 2044146 | 1771 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 118657 | 37.0874 | -121.6269 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0045740 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825676 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OTHER | HI SIDE OF 4539 TWD CGC #2728 | 20230314 | 1310 | 20230316 | 1215 | 2044417 | 2825 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 59075 | 37.1187 | -121.6463 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 23-0045792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825717 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10677 | 20230314 | 1310 | 20230315 | 2153 | 2044777 | 1963 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 35334 | 37.107 | -121.6067 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0045886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825809 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OTHER | WIRE DOWN 13475 HARDING AVE | 20230314 | 1310 | 20230316 | 1241 | 2044814 | 2851 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 118768 | 37.0838 | -121.6173 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045896 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1825819 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | INTERRUPTER | 61036 | 20230314 | 1319 | 20230315 | 1411 | 2046276 | 1492 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 250 | 373000 | 37.113 | -121.6424 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0046376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826183 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20230314 | 1330 | 20230315 | 1419 | 2040705 | 1489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 297 | 134907 | 37.1334 | -121.6754 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1825238 | 0 | EPSS Ckt | N | 2023 | A- B & C
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 19375 | 20230314 | 1335 | 20230315 | 1357 | 2043673 | 1462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 32228 | 37.1695 | -121.7571 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0045637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825580 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 20147 | 20230314 | 1335 | 20230315 | 1514 | 2043727 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 578664 | 37.1148 | -121.6883 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0045652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825594 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6917 | 20230314 | 1339 | 20230314 | 2130 | 2040826 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 163 | 76773 | 37.2668 | -121.8834 | Yes | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0045869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825792 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR320 | 20230314 | 1340 | 20230314 | 2345 | 2041194 | 605 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2037 | 1232385 | 37.0019 | -121.5672 | Yes | Clear;32-90 F |  |  | 23-0045835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825757 | 0 | EPSS Ckt | N | 2023 | C GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 72853 | 20230314 | 1344 | 20230315 | 236 | 2045103 | 772 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 89552 | 37.1218 | -121.6621 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0046042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825960 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 25349 | 20230314 | 1347 | 20230316 | 1648 | 2040993 | 3061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 39793 | 37.0637 | -121.5707 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0046803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826440 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 37264 | 20230314 | 1402 | 20230316 | 113 | 2043104 | 2111 | Distribution Circuit | Vegetation | Tree - fell into line | 1288 | 536388 | 37.0132 | -121.5513 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825716 | 0 | EPSS Ckt | N | 2023 | A & B
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316889918632 | 20230314 | 1402 | 20230316 | 1825 | 2041865 | 3143 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 9429 | 37.0068 | -121.566 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Fuse | Failed/Faulted | 23-0047216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826681 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 1049 | 20230314 | 1404 | 20230315 | 2100 | 2042409 | 1856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1856 | 37.037 | -121.59 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0046696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826375 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41773 | 20230314 | 1405 | 20230315 | 2342 | 2041685 | 2017 | Distribution Circuit | Equipment Failure/Involved | Overhead | 380 | 115882 | 37.2952 | -121.9486 | Yes | Partly Cloudy-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0045680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825621 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14017 | 20230314 | 1407 | 20230316 | 1937 | 2041792 | 3210 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 60990 | 37.1942 | -121.798 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0046583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826305 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | OTHER | WIRE DOWN IRO 7591 MILLER | 20230314 | 1407 | 20230315 | 2222 | 2044689 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 55155 | 37.0064 | -121.5824 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1825784 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | 975388 | 20230314 | 1410 | 20230315 | 22 | 2041933 | 612 | Distribution Circuit | Vegetation | Tree - branch fell on line | 140 | 85680 | 37.1264 | -121.6626 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0045355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825344 | 0 | EPSS Ckt | N | 2023 | C INST & TIME
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 71117 | 20230314 | 1419 | 20230315 | 2350 | 2042001 | 2011 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 246786 | 37.011 | -121.5651 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0046784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826432 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 26113 | 20230314 | 1421 | 20230315 | 1617 | 2046162 | 1556 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 93 | 144708 | 37.0023 | -121.564 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0046502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826254 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20230314 | 1422 | 20230314 | 2123 | 2042096 | 421 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 776 | 275932 | 37.133 | -121.6122 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0045374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825360 | 0 | EPSS Ckt | N | 2023 | C GRD
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 4261 | 20230314 | 1430 | 20230314 | 2310 | 2042168 | 520 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 465 | 241800 | 37.0318 | -121.5812 | Yes | Clear;32-90 F |  |  | 23-0045980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825906 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20230314 | 1434 | 20230315 | 1204 | 2042261 | 1290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1009 | 1300518 | 37.0163 | -121.5446 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0045350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825341 | 0 | EPSS Ckt | N | 2023 | A & B
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316839119062 | 20230314 | 1453 | 20230316 | 1734 | 2042485 | 3041 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 15205 | 37.0185 | -121.5836 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0047194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826665 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | OCB | 1101/2 | 20230314 | 1457 | 20230314 | 1858 | 2042547 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 142913 | 37.3043 | -121.8683 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0045401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1825385 | 0 | Non-EPSS | N | 2023 | A & B
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | OCB | 1116/2 | 20230314 | 1507 | 20230316 | 2103 | 2037264 | 3236 | Distribution Circuit | Vegetation | Tree - fell into line | 2405 | 1923953 | 37.2332 | -121.9011 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825450 | 0 | EPSS Ckt | N | 2023 | A & C TIME
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | OTHER | WIRE DOWN @ 521 RICHMOND AVE | 20230314 | 1507 | 20230315 | 1428 | 2042622 | 1401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 41271 | 37.3191 | -121.9233 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | Yes | 1825606 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316885718883 | 20230314 | 1518 | 20230316 | 1905 | 2042709 | 3107 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 15535 | 37.0136 | -121.5675 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0047185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826661 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 70297 | 20230314 | 1537 | 20230314 | 1803 | 2042865 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 15768 | 37.353 | -121.8119 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045464 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825437 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | OCB | 1111/2 | 20230314 | 1649 | 20230315 | 2110 | 2039559 | 1701 | Distribution Circuit | Vegetation | Tree - fell into line | 3572 | 2381923 | 37.2332 | -121.9012 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825569 | 0 | Non-EPSS | N | 2023 | GRD TIME
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315899528529 | 20230314 | 1649 | 20230316 | 1538 | 2045063 | 2809 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 30899 | 37.275 | -121.9104 | Yes | Clear;32-90 F | Secondary | Broken | 23-0045623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825952 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315913128580 | 20230314 | 1649 | 20230316 | 1517 | 2045070 | 2788 | Transformer only | Vegetation | Tree - fell into line | 15 | 41820 | 37.2764 | -121.9058 | Yes | Clear;32-90 F | Secondary | On Ground | 23-0045623 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825956 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 17429 | 20230314 | 1718 | 20230314 | 2032 | 2043721 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 29488 | 37.2481 | -121.8766 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0045874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825798 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 4695 | 20230314 | 1755 | 20230316 | 1519 | 2041012 | 2724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 19068 | 37.1128 | -121.6612 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0045703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1825641 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 28343 | 20230314 | 2003 | 20230316 | 615 | 2044607 | 2052 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 43092 | 37.028 | -121.5525 | Yes | Clear;32-90 F |  |  | 23-0046842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826464 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 27981 | 20230314 | 2018 | 20230317 | 1754 | 2044644 | 4176 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 66816 | 37.2264 | -121.9024 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0047639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826924 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316164025250 | 20230314 | 2117 | 20230316 | 644 | 2044812 | 2007 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 8028 | 37.1872 | -121.819 | Yes | Overcast;32-90 F | Secondary | Broken | 23-0046703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826378 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 657273 | 20230314 | 2241 | 20230316 | 1453 | 2044933 | 2412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 24120 | 37.1292 | -121.6261 | Yes | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0045986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1825912 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 3145 | 20230314 | 2305 | 20230315 | 1240 | 2045321 | 815 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3260 | 37.0899 | -121.6227 | Yes | Clear;32-90 F |  |  | 23-0046317 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826144 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 4675 | 20230315 | 249 | 20230316 | 1725 | 2045136 | 2316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 6948 | 37.0792 | -121.6556 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826351 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 28517 | 20230315 | 305 | 20230317 | 1325 | 2045142 | 3500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 158158 | 37.2765 | -121.9153 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0046518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826263 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 27153 | 20230315 | 422 | 20230315 | 1651 | 2045207 | 749 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 56175 | 37.2389 | -121.9062 | No | Clear;32-90 F |  |  | 23-0046537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826276 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | JUMPER | OJ 1 W/OF 23383 | 20230315 | 859 | 20230315 | 1127 | 2045883 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1184 | 175232 | 37.0089 | -121.5796 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0046218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1826096 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | OTHER | WIRE DOWN 1 SP W/OF 75342 | 20230315 | 1001 | 20230316 | 1450 | 2045783 | 1729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 779 | 189497 | 37.351 | -121.8153 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | Yes | 1826094 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | FUSE | 590493 | 20230315 | 1116 | 20230315 | 1533 | 2045963 | 257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 7967 | 37.2992 | -121.9409 | No | Overcast;32-90 F | Secondary | Broken | 23-0046252 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826110 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41771 | 20230315 | 1120 | 20230315 | 2341 | 2045970 | 741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 15561 | 37.2952 | -121.9476 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0046255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826111 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 44470 | 20230315 | 1341 | 20230315 | 2357 | 2047094 | 616 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3282 | 37.3883 | -121.9007 | No | Partly Cloudy;32-90 F |  |  | 23-0046789 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826434 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | TRANSFORMER | 316030927144 | 20230315 | 1433 | 20230315 | 2024 | 2046400 | 351 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 351 | 37.2374 | -121.8644 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0046684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826366 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316033226255 | 20230315 | 1514 | 20230316 | 1535 | 2046527 | 1461 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 7305 | 37.2131 | -121.8628 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0046686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826368 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20230315 | 1646 | 20230316 | 1543 | 2046825 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 143826 | 37.1083 | -121.7324 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0046550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826284 | 0 | EPSS Ckt | N | 2023 | A & INST
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316878918670 | 20230315 | 1656 | 20230316 | 404 | 2046795 | 668 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 4008 | 37.0078 | -121.5698 | No | Clear;32-90 F | Transformer | Broken | 23-0046761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826413 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | TRANSFORMER | 315925527322 | 20230315 | 1948 | 20230316 | 1852 | 2047068 | 1384 | Transformer only | Vegetation | Tree - fell into line | 12 | 16608 | 37.242 | -121.9008 | No | Clear;32-90 F | Transformer | Contaminated | 23-0047159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826643 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 26531 | 20230315 | 2032 | 20230315 | 2325 | 2047267 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 33562 | 37.2725 | -121.8988 | No | Clear;32-90 F | Secondary | Broken | 23-0046687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826369 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 10831 | 20230315 | 2336 | 20230316 | 625 | 2047471 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9816 | 37.0142 | -121.574 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826441 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315873329904 | 20230316 | 448 | 20230316 | 630 | 2047633 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1020 | 37.3126 | -121.92 | No | Clear;32-90 F | Secondary | Broken | 23-0046843 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826465 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316640020130 | 20230316 | 619 | 20230317 | 1038 | 2049513 | 1699 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5097 | 37.0472 | -121.6525 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0047482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826845 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | JUMPER | OJ LD OF CGC 316588521585 | 20230316 | 629 | 20230317 | 1830 | 2047665 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4322 | 37.0873 | -121.6699 | No | Clear;32-90 F | Secondary | Normal | 23-0047489 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826848 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20230316 | 701 | 20230317 | 1625 | 2047723 | 1201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 67718 | 37.053 | -121.5276 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0047037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826578 | 0 | EPSS Ckt | N | 2023 | B & C TARGET
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315792629272 | 20230316 | 706 | 20230316 | 1807 | 2047704 | 661 | Transformer only | Company Initiated | Personnel- company | 1 | 661 | 37.295 | -121.9474 | No | Clear;32-90 F | Transformer (OH) |  | 23-0047211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826676 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 12529 | 20230316 | 738 | 20230316 | 1203 | 2047743 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 15635 | 37.1055 | -121.6059 | No | Clear;32-90 F |  |  | 23-0046988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1826546 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316838718974 | 20230316 | 818 | 20230317 | 1356 | 2048824 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 24892 | 37.016 | -121.5836 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826771 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 14403 | 20230316 | 822 | 20230317 | 2230 | 2047811 | 2288 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 2288 | 36.965 | -121.5321 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047598 | OH | Sus | 35431716 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1826906 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | JUMPER | JUMPERS 1 SPAN SS OF CGC 316759019790 | 20230316 | 1052 | 20230316 | 2030 | 2048184 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1734 | 37.038 | -121.6106 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0046952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826524 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316851518569 | 20230316 | 1118 | 20230317 | 1454 | 2047715 | 1656 | Distribution Circuit | Vegetation | Tree - branch fell on line | 213 | 70528 | 37.005 | -121.5796 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047138 | OH | Sus | 35431716 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826627 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 3149 | 20230316 | 1127 | 20230316 | 1915 | 2048259 | 468 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 11700 | 37.0056 | -121.5195 | No | Partly Cloudy;32-90 F |  |  | 23-0047229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826693 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317043919175 | 20230316 | 1244 | 20230316 | 1818 | 2046143 | 334 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1002 | 37.0222 | -121.5133 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0047023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826569 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315936528378 | 20230316 | 1344 | 20230316 | 1624 | 2048411 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2400 | 37.2711 | -121.8976 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0047052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826585 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | 316030526647 | 20230316 | 1419 | 20230316 | 1435 | 2039011 | 16 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 256 | 37.2241 | -121.8646 | No | Clear;32-90 F |  |  | 23-0047078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1826602 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315873327449 | 20230316 | 1700 | 20230316 | 1833 | 2048985 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 651 | 37.2454 | -121.9189 | No | Clear;32-90 F | Secondary | Normal | 23-0047184 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826660 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 41403 | 20230317 | 925 | 20230317 | 1716 | 2048012 | 471 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 471 | 37.1707 | -121.7575 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0047447 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826835 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11939 | 20230317 | 946 | 20230317 | 1210 | 2049748 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 15264 | 37.2222 | -121.8624 | No | Clear;32-90 F |  |  | 23-0047558 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1826887 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315949028735 | 20230317 | 1013 | 20230317 | 1235 | 2049846 | 142 | Transformer only | Vegetation | Tree - grew into line | 8 | 1136 | 37.2809 | -121.8935 | No | Clear;32-90 F | Secondary | Normal | 23-0047506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826858 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | OTHER | J5700 TWD T6124 | 20230317 | 1421 | 20230317 | 2232 | 2050192 | 491 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 1984 | 37.2284 | -121.8862 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Broken | 23-0047368 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826919 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28747 | 20230317 | 1721 | 20230317 | 1928 | 2050564 | 127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 2667 | 37.277 | -121.8109 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0047723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826967 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | SWITCH | 10131 | 20230317 | 1723 | 20230317 | 1741 | 2050595 | 18 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 828 | 37.192 | -121.8007 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0047732 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826975 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 18751 | 20230317 | 1819 | 20230317 | 1941 | 2050653 | 82 | Distribution Circuit | Vegetation | Tree - grew into line | 127 | 10414 | 37.2797 | -121.8908 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0047738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1826981 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1116 | 82921116 | JUMPER | WIRE DOWN @ 1159 BISMARCK | 20230317 | 2112 | 20230318 | 1431 | 2050794 | 1039 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7820 | 591455 | 37.2954 | -121.9699 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1826998 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315970627591 | 20230318 | 920 | 20230318 | 1037 | 2050964 | 77 | Transformer only | Vegetation | Tree - fell into line | 9 | 693 | 37.2496 | -121.8855 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0048261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827486 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | TRANSFORMER | 316930417520 | 20230318 | 952 | 20230318 | 1458 | 2051049 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 396 | 36.9764 | -121.5518 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0048278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827502 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 2505 | 20230318 | 1039 | 20230318 | 2341 | 2051054 | 782 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 8990 | 37.1176 | -121.66 | No | Clear;32-90 F | Other | Deteriorated | 23-0048244 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827503 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 786125 | 20230318 | 1640 | 20230318 | 1838 | 2051422 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 5900 | 37.3106 | -121.9758 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0048344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827548 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15525 | 20230318 | 1936 | 20230318 | 2315 | 2051503 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 13273 | 37.3353 | -121.7714 | No | Overcast;32-90 F |  |  | 23-0048408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827614 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 103451 | 20230319 | 406 | 20230319 | 1003 | 2051780 | 357 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3927 | 37.3846 | -121.8006 | No | Clear;32-90 F |  |  | 23-0048466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827677 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 889 | 20230319 | 855 | 20230320 | 1501 | 2051727 | 1806 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 11060 | 36.9472 | -121.5098 | No | Overcast-Rain;32-90 F | Insulator | Burned/flashed | 23-0048456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827666 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 70479 | 20230319 | 1131 | 20230319 | 1242 | 2051979 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.1935 | -121.8255 | No | Overcast;32-90 F |  |  | 23-0048484 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827694 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20230319 | 1457 | 20230319 | 1643 | 2052144 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 386 | 34841 | 37.1503 | -121.6194 | No | Overcast-Drizzle;32-90 F |  |  | 23-0048512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1827719 | 0 | EPSS Ckt | N | 2023 | A & G
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 711900 | 20230319 | 1533 | 20230321 | 1450 | 2052182 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 95093 | 37.3561 | -121.8052 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1827728 | 0 | EPSS Ckt | N | 2023 | A B C G
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316207531309 | 20230319 | 1659 | 20230320 | 58 | 2052522 | 479 | Transformer only | 3rd Party | Metallic Balloon | 10 | 4790 | 37.3525 | -121.8058 | No | Overcast;32-90 F | Secondary | Contaminated | 23-0048595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827802 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 15137 | 20230320 | 717 | 20230320 | 937 | 2052658 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1820 | 37.4135 | -121.843 | No | Overcast;32-90 F |  |  | 23-0048675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827837 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 11681 | 20230320 | 851 | 20230320 | 1124 | 2052700 | 153 | Distribution Circuit | Animal | Squirrel | 201 | 30753 | 37.2635 | -121.8123 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0048775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827900 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 7531 | 20230320 | 1105 | 20230320 | 1322 | 2052931 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 274 | 37.0935 | -121.7199 | No | Clear;32-90 F |  |  | 23-0048891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827924 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | C2407 | 20230320 | 1245 | 20230320 | 1259 | 2053041 | 14 | Transformer only | Equipment Failure/Involved | Underground | 23 | 322 | 37.441 | -121.8749 | No | Clear;32-90 F | Secondary | Broken | 23-0048865 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827919 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316519724733 | 20230320 | 1730 | 20230321 | 137 | 2053363 | 487 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 487 | 37.1731 | -121.6955 | No | Partly Cloudy;32-90 F |  |  | 23-0049061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828017 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 72451 | 20230320 | 1901 | 20230320 | 2221 | 2053424 | 200 | Distribution Circuit | 3rd Party | Vehicle | 90 | 18000 | 37.2905 | -121.9029 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0049019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1827977 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2103 | 14722103 | SWITCH | 42686 | 20230320 | 1922 | 20230321 | 351 | 2053432 | 509 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 509 | 37.4497 | -121.918 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0048879 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1827968 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316516824625 | 20230320 | 2114 | 20230321 | 135 | 2053481 | 261 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 261 | 37.1701 | -121.6965 | No | Overcast;32-90 F |  |  | 23-0049060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1828016 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 28321 | 20230321 | 913 | 20230321 | 1049 | 2053814 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 4800 | 37.1498 | -121.5953 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0049174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828103 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20230321 | 1300 | 20230321 | 1451 | 2054856 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3341 | 268475 | 37.2332 | -121.9012 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828276 | 0 | Non-EPSS | N | 2023 | C & PH OC TIMED
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | RECLOSER | XR536 | 20230321 | 1303 | 20230321 | 1541 | 2054957 | 158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4324 | 682877 | 37.3032 | -121.9836 | Yes | Overcast-Heavy Rain;32-90 F | Other | Arcing | 23-0049466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | No | No | 1828235 | 0 | Non-EPSS | N | 2023 | ABC
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20230321 | 1304 | 20230321 | 1812 | 2055750 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 768 | 236544 | 37.1334 | -121.6754 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049561 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828315 | 0 | EPSS Ckt | N | 2023 | A & GRD
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | JUMPER | 2 PHASES DOWN | 20230321 | 1306 | 20230321 | 2015 | 2054994 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 39468 | 37.277 | -121.91 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1828338 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 28321 | 20230321 | 1308 | 20230321 | 1911 | 2055088 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 18150 | 37.1498 | -121.5953 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0050055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828733 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | RECLOSER | XR240 | 20230321 | 1309 | 20230321 | 1436 | 2055086 | 87 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2121 | 184527 | 37.2512 | -121.8304 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828248 | 0 | Non-EPSS | N | 2023 | B & C
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | RECLOSER | XR150 | 20230321 | 1313 | 20230321 | 1457 | 2055145 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 877 | 91208 | 37.2977 | -121.8704 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828256 | 0 | Non-EPSS | N | 2023 | C & GRD
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15741 | 20230321 | 1315 | 20230321 | 1807 | 2055127 | 292 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2336 | 37.1992 | -121.8221 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0049899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828591 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 96741 | 20230321 | 1315 | 20230322 | 1213 | 2055267 | 1378 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 4134 | 37.3208 | -121.8762 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829131 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230321 | 1318 | 20230321 | 1956 | 2055178 | 398 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 11542 | 37.1602 | -121.666 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828784 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 41815 | 20230321 | 1322 | 20230321 | 1754 | 2055417 | 270 | Distribution Circuit | 3rd Party | Other | 16 | 4320 | 37.3059 | -121.9544 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828674 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 108971 | 20230321 | 1332 | 20230321 | 1652 | 2055510 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 8600 | 37.3206 | -121.9525 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828530 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 28847 | 20230321 | 1335 | 20230321 | 1657 | 2055400 | 202 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 9090 | 37.2978 | -121.9429 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049849 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828550 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 103451 | 20230321 | 1346 | 20230321 | 1926 | 2056243 | 340 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3740 | 37.3846 | -121.8006 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0050079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828754 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41727 | 20230321 | 1358 | 20230321 | 1529 | 2056097 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3003 | 37.298 | -121.9184 | Yes | Overcast-Rain;32-90 F |  |  | 23-0049736 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828453 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | TRANSFORMER | 315947334957 | 20230321 | 1411 | 20230322 | 1521 | 2055117 | 1510 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 27180 | 37.4517 | -121.8974 | Yes | Overcast;32-90 F | Secondary | Broken- wire on ground | 23-0049620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828360 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR176 | 20230321 | 1446 | 20230321 | 2304 | 2056703 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 1081 | 199651 | 37.0929 | -121.6472 | Yes | Overcast;32-90 F | Conductor- Overhead | On Ground | 23-0049683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828410 | 0 | EPSS Ckt | N | 2023 | B & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3157 | 20230321 | 1446 | 20230322 | 1741 | 2059434 | 1615 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 32300 | 37.0608 | -121.665 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0049941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828629 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316064030860 | 20230321 | 1509 | 20230322 | 605 | 2056941 | 896 | Transformer only | Environmental/External | Water | 25 | 22400 | 37.3398 | -121.8551 | Yes | Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 23-0050157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828819 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 315991234505 | 20230321 | 1525 | 20230323 | 211 | 2055886 | 2086 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 29204 | 37.4395 | -121.8821 | Yes | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 23-0049810 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828514 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75149 | 20230321 | 1559 | 20230322 | 1559 | 2060532 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 63360 | 37.2946 | -121.9536 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0050120 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1828788 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING 2101 | 14722101 | TRANSFORMER | 315936435160 | 20230321 | 1642 | 20230321 | 2116 | 2056121 | 274 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 3287 | 37.4573 | -121.9012 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0049875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828570 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 72451 | 20230321 | 1645 | 20230322 | 116 | 2058382 | 511 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 90 | 45990 | 37.2905 | -121.9029 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0049859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828557 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20230321 | 1703 | 20230321 | 1852 | 2059156 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 212 | 23108 | 37.4483 | -121.8461 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0049939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Multi-Fault | 0 | No | No | No | 1828627 | 0 | EPSS Ckt | N | 2023 | A C & SGF
SAN JOSE | SAN JOSE | SWIFT 2102 | 83392102 | FUSE | 34220 | 20230321 | 1708 | 20230322 | 1300 | 2062556 | 1192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 7152 | 37.2996 | -121.758 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0050609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829129 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315928235300 | 20230321 | 1715 | 20230321 | 1735 | 2057866 | 20 | Transformer only | Vegetation | Tree - grew into line | 20 | 400 | 37.4611 | -121.9041 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0049958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828643 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR044 | 20230321 | 1855 | 20230321 | 1901 | 2060104 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 326 | 1956 | 37.4385 | -121.8718 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0050037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1828720 | 0 | EPSS Ckt | N | 2023 | UNKNOWN
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 28429 | 20230321 | 1922 | 20230322 | 2342 | 2060315 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 37400 | 37.414 | -121.7799 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1829053 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | RECLOSER | XR538 | 20230321 | 1930 | 20230321 | 2046 | 2057619 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6193 | 450456 | 37.3012 | -121.9677 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0050091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828763 | 0 | Non-EPSS | N | 2023 | A & GRD
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | SWITCH | 3163 | 20230321 | 2012 | 20230322 | 437 | 2060584 | 505 | Distribution Circuit | 3rd Party | Vehicle | 1925 | 215694 | 37.2988 | -121.8928 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0049631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828796 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | JUMPER | 1 JUMPER 1 SPAN SOURCE SIDE 40365 | 20230321 | 2055 | 20230321 | 2246 | 2061173 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1684 | 42288 | 37.2775 | -121.9157 | Yes | Overcast-Rain;32-90 F | Jumper | Burned Open | 23-0050210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1828869 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 4251 | 20230321 | 2115 | 20230322 | 1559 | 2060936 | 1124 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 14612 | 37.212 | -121.9093 | Yes | Overcast-Rain-Strong Winds;32-90 F | Anchor or Guy | Broken | 23-0050875 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829291 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316170931204 | 20230321 | 2119 | 20230322 | 1236 | 2060950 | 917 | Transformer only | Vegetation | Tree - branch fell on line | 10 | 9170 | 37.3495 | -121.8183 | Yes | Rain-Overcast;32-90 F | Secondary | On Ground | 23-0050238 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828898 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 10104 | 20230322 | 38 | 20230322 | 224 | 2061422 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1605 | 38657 | 37.2351 | -121.8037 | No | Clear;32-90 F |  |  | 23-0050283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1828944 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20230322 | 402 | 20230322 | 411 | 2061559 | 9 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 2484 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828976 | 0 | EPSS Ckt | N | 2023 | SENSITIVE GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20230322 | 402 | 20230322 | 2130 | -2061559 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 61680 | 37.1083 | -121.7324 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1828979 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315736929659 | 20230322 | 905 | 20230322 | 1031 | 2062048 | 86 | Transformer only | Vegetation | Tree - grew into line | 17 | 1462 | 37.3056 | -121.9665 | No | Overcast-Fog-Rain;32-90 F | Secondary | Arcing | 23-0050407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829025 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 70479 | 20230322 | 1116 | 20230322 | 1147 | 2062407 | 31 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 62 | 37.1935 | -121.8255 | No | Overcast-Drizzle;32-90 F |  |  | 23-0050591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829120 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10541 | 20230322 | 1131 | 20230323 | 221 | 2062443 | 890 | Distribution Circuit | 3rd Party | Vehicle | 50 | 12532 | 37.1035 | -121.6165 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0050729 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829206 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | T8499 | 20230322 | 1256 | 20230322 | 1412 | 2062770 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 760 | 37.2966 | -121.8137 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0050752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829221 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 33264 | 20230322 | 1256 | 20230323 | 457 | 2062740 | 961 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 150 | 63639 | 37.3076 | -121.802 | No | Clear;32-90 F | Conductor- Underground | Contaminated | 23-0050789 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829243 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20230322 | 1644 | 20230322 | 1732 | 2063361 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 4224 | 37.2267 | -121.8632 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0050932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829333 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315900429049 | 20230322 | 1832 | 20230322 | 2051 | 2063624 | 139 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 3 | 417 | 37.2893 | -121.9104 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Normal | 23-0050972 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829364 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 14933 | 20230322 | 2020 | 20230323 | 1737 | 2063796 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1277 | 37.0846 | -121.7734 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0051026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829407 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315659530047 | 20230322 | 2030 | 20230322 | 2218 | 2063784 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1404 | 37.3162 | -121.9933 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Normal | 23-0051024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829405 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 8311 | 20230323 | 1215 | 20230323 | 1422 | 2064616 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 2921 | 37.3552 | -121.792 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0051360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829629 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 71697 | 20230323 | 1840 | 20230324 | 501 | 2065206 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 35397 | 37.4045 | -121.8495 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0051588 | OH | Sus | 45707617 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1829753 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 15137 | 20230324 | 700 | 20230324 | 1256 | 2065615 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2660 | 37.4135 | -121.843 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0051716 | OH | Sus | 45708582 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829838 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 7531 | 20230324 | 1208 | 20230324 | 1445 | 2066029 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 314 | 37.0935 | -121.7199 | No | Clear;32-90 F |  |  | 23-0051928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1829934 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 3053 | 20230325 | 9 | 20230325 | 1159 | 2066666 | 710 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2130 | 36.9487 | -121.5156 | No | Overcast;32-90 F | Transformer (OH) | Arcing | 23-0052415 | OH | Sus | 31640291 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830376 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 70407 | 20230325 | 100 | 20230325 | 1050 | 2066694 | 590 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 84370 | 37.156 | -121.6116 | No | Overcast;32-90 F |  |  | 23-0052472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830434 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 18073 | 20230325 | 647 | 20230325 | 1623 | 2066766 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 5760 | 37.2201 | -121.7872 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052436 | OH | Sus | 31640350 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1830396 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20230325 | 1426 | 20230325 | 1640 | 2067093 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 12618 | 37.2267 | -121.8632 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0052516 | OH | Sus | 35433931 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830468 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | OTHER | J5404 TWD T10129 | 20230325 | 2051 | 20230327 | 216 | 2067689 | 1765 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 18870 | 37.3143 | -121.7947 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0052669 | UG | Sus | 35434008 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830611 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2107 | 82462107 | FUSE | 35386 | 20230325 | 2208 | 20230326 | 2035 | 2067410 | 1347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 10776 | 37.4169 | -121.9553 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 23-0052619 | OH | Sus | 35434003 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830561 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4351 | 20230326 | 549 | 20230326 | 1156 | 2067651 | 367 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2936 | 37.0687 | -121.5974 | No | Clear;32-90 F |  |  | 23-0052664 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830606 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | T24358 | 20230326 | 1316 | 20230326 | 1549 | 2067648 | 153 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 153 | 37.1638 | -121.7044 | No | Clear;32-90 F |  |  | 23-0052694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830630 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T10129 | 20230327 | 401 | 20230327 | 1007 | 2068097 | 366 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 2196 | 37.3143 | -121.7946 | No | Clear;32-90 F |  |  | 23-0052870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1830777 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | 534019 | 20230327 | 658 | 20230327 | 1035 | 2068531 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 868 | 36.9865 | -121.579 | No | Clear;32-90 F |  |  | 23-0052877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830782 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | OCB | 1102/2/NORM | 20230327 | 702 | 20230327 | 1330 | 2068160 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3839 | 140282 | 37.2601 | -121.89 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1830700 | 0 | Non-EPSS | N | 2023 | SET A: B PH- TOC- SET B: B-C-I
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316838818726 | 20230327 | 920 | 20230327 | 1117 | 2068414 | 117 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1521 | 37.0093 | -121.5835 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0052840 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1830760 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 5285 | 20230327 | 1023 | 20230327 | 1130 | 2068549 | 67 | Distribution Circuit | Animal | Bird found | 55 | 3685 | 37.1092 | -121.5955 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0052915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1830800 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13955 | 20230328 | 404 | 20230328 | 435 | 2069502 | 31 | Distribution Circuit | Animal | Bird found | 507 | 15717 | 37.3265 | -121.8473 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0053219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1830973 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 40833 | 20230328 | 933 | 20230328 | 1748 | 2069957 | 495 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 990 | 37.3281 | -121.8467 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0053347 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831055 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 405/2 | 20230328 | 1016 | 20230328 | 1247 | 2070137 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 595 | 89777 | 37.3281 | -121.9025 | No | Overcast;32-90 F |  |  | 23-0053444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831107 | 0 | Non-EPSS | N | 2023 | TIME GRD OC RLY (51N)
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 26733 | 20230328 | 2057 | 20230329 | 1425 | 2072059 | 1048 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 16751 | 37.3433 | -121.7959 | No | Overcast;32-90 F | Conductor- Underground | Deteriorated | 23-0053963 | UG | Sus | 45710756 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831444 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 26917 | 20230329 | 339 | 20230329 | 653 | 2072249 | 194 | Distribution Circuit | Animal | Bird found | 169 | 32786 | 37.0998 | -121.6727 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0053987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831469 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 39934 | 20230329 | 1403 | 20230330 | 1159 | 2073206 | 1141 | Distribution Circuit | Environmental/External | Lightning | 123 | 114129 | 37.2841 | -121.8156 | No | Overcast;32-90 F | Pothead/Riser Termination | Burned/flashed | 23-0054535 | OH | Sus | 31640710 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831683 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20230329 | 1417 | 20230329 | 1846 | 2073283 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 7801 | 37.1602 | -121.666 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0054617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831721 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 42776 | 20230329 | 1423 | 20230330 | 627 | 2073276 | 964 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 21372 | 37.0215 | -121.5918 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0054640 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831743 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | RECLOSER | 773372 | 20230329 | 1546 | 20230329 | 1742 | 2073442 | 116 | Distribution Circuit | 3rd Party | Metallic Balloon | 653 | 75748 | 37.3847 | -121.8366 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 23-0054551 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831692 | 0 | Non-EPSS | N | 2023 | A & B
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 30995 | 20230330 | 15 | 20230330 | 1325 | 2073714 | 790 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 22120 | 37.2871 | -121.9226 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0054714 | OH | Sus | 31640713 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1831803 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40088 | 20230330 | 831 | 20230331 | 615 | 2073994 | 1115 | Distribution Circuit | Equipment Failure/Involved | Underground | 283 | 85900 | 37.1046 | -121.6432 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0054885 | UG | Sus | 45711888 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831915 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 15127 | 20230330 | 1126 | 20230330 | 1356 | 2074341 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 300 | 37.3824 | -121.8874 | No | Partly Cloudy;32-90 F |  |  | 23-0055021 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1831973 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 11807 | 20230330 | 1240 | 20230331 | 1215 | 2074450 | 1010 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 20484 | 37.296 | -121.8834 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0055232 | OH | Sus | 31641104 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832030 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | SWITCH | 10786 | 20230330 | 1244 | 20230330 | 2139 | 2074697 | 535 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 19670 | 37.2799 | -121.8158 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0055114 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832012 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | OCB | 1116/2 | 20230330 | 1857 | 20230330 | 1907 | 2074702 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3424 | 34240 | 37.2332 | -121.9011 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0055227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832032 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 72639 | 20230330 | 2222 | 20230330 | 2351 | 2074860 | 89 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4 | 356 | 37.2364 | -121.9141 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0055274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832066 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20230331 | 118 | 20230331 | 135 | 2075001 | 17 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 398 | 6766 | 37.1446 | -121.6698 | No | Overcast;32-90 F |  |  | 23-0055300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1832096 | 0 | EPSS Ckt | N | 2023 | TIME OC RLY TARGET
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | T6293 | 20230331 | 737 | 20230331 | 1328 | 2075120 | 351 | Transformer only | Equipment Failure/Involved | Underground | 15 | 5265 | 37.2234 | -121.8823 | No | Clear;32-90 F | Secondary | Normal | 23-0055580 | UG | Sus | 45712896 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1832226 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 558681 | 20230331 | 1620 | 20230331 | 1739 | 2075673 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 188 | 14852 | 37.2976 | -121.982 | No | Partly Cloudy;32-90 F |  |  | 23-0055663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1832260 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20230331 | 1920 | 20230401 | 1030 | 2075793 | 910 | Distribution Circuit | Animal | Bird found | 400 | 105853 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0055677 | OH | Sus | 45713211 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1832274 | 0 | EPSS Ckt | N | 2023 | A-B PH
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 711900 | 20230331 | 2027 | 20230401 | 1945 | 2076300 | 1398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 605 | 139308 | 37.3561 | -121.8052 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0055688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1832285 | 0 | EPSS Ckt | N | 2023 | C PH & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 40411 | 20230401 | 1540 | 20230401 | 1726 | 2076828 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 106 | 37.1057 | -121.6318 | No | Clear;32-90 F |  |  | 23-0055887 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832482 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 42225 | 20230401 | 1928 | 20230401 | 2057 | 2076983 | 89 | Distribution Circuit | 3rd Party | Metallic Balloon | 34 | 3026 | 37.2909 | -121.8492 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0055899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832495 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2112 | 82952112 | OCB | 2112/2 | 20230402 | 1049 | 20230402 | 1205 | 2077397 | 22 | Distribution Circuit | Animal | Squirrel | 853 | 18766 | 37.2448 | -121.7952 | No | Clear;32-90 F | Recloser | Burned/flashed | 23-0056019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1832614 | 0 | Non-EPSS | N | 2023 | phase & grd
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 12653 | 20230402 | 1122 | 20230402 | 1235 | 2077427 | 73 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 1387 | 37.4323 | -121.8719 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0056034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832627 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20230402 | 1526 | 20230403 | 1205 | 2077542 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8673 | 37.0839 | -121.7682 | No | Clear;32-90 F | Fuse | Normal | 23-0056052 | OH | Sus | 45713948 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1832644 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1117 | 82261117 | OCB | 1117/2 | 20230403 | 124 | 20230404 | 423 | 2077759 | 1619 | Distribution Circuit | 3rd Party | Vandalism | 720 | 148274 | 37.3411 | -121.9017 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0056124 | OH | Sus | 35435963 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832690 | 0 | Non-EPSS | N | 2023 | B & C
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 92999 | 20230403 | 332 | 20230403 | 815 | 2077794 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 660 | 37.3368 | -121.8171 | No | Partly Cloudy;32-90 F |  |  | 23-0056175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1832729 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 1049 | 20230403 | 1232 | 20230403 | 1440 | 2078327 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 128 | 37.037 | -121.59 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0056374 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832868 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | JUMPER | OJ'S @ BROADLEAF LN TWD EOL | 20230403 | 1700 | 20230403 | 2031 | 2078872 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 5697 | 37.3339 | -121.9402 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0056499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1832928 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 12975 | 20230403 | 1748 | 20230403 | 2122 | 2079137 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 603 | 129042 | 37.2859 | -121.8428 | No | Clear;32-90 F |  |  | 23-0056601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1832991 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T2087 | 20230404 | 1339 | 20230404 | 1547 | 2079572 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 128 | 37.3318 | -121.7662 | No | Clear;32-90 F |  |  | 23-0057078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1833252 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 71015 | 20230404 | 1510 | 20230404 | 1525 | 2080125 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 150 | 37.3274 | -121.7665 | No | Clear;32-90 F |  |  | 23-0057137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833269 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20230405 | 643 | 20230405 | 857 | 2080392 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 28274 | 37.1869 | -121.8177 | No | Partly Cloudy;32-90 F |  |  | 23-0057271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1833344 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 12017 | 20230405 | 2103 | 20230406 | 1527 | 2081192 | 1104 | Distribution Circuit | Equipment Failure/Involved | Underground | 374 | 99526 | 37.2127 | -121.8362 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0057717 | UG | Sus | 45716451 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833578 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 18291 | 20230406 | 844 | 20230406 | 1246 | 2081415 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2662 | 37.3707 | -121.8013 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0057806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1833662 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1117 | 82261117 | INTERRUPTER | 65520 | 20230406 | 856 | 20230406 | 902 | 2081485 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 6 | 37.3413 | -121.9183 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0057829 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833700 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316376921882 | 20230406 | 1157 | 20230406 | 2138 | 2081779 | 581 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1162 | 37.0939 | -121.7437 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0057983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833814 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315959531686 | 20230406 | 1607 | 20230407 | 115 | 2081967 | 548 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1096 | 37.362 | -121.8915 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058150 | OH | Sus | 35436704 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1833854 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316120529748 | 20230407 | 1509 | 20230408 | 1023 | 2082753 | 1154 | Transformer only | Unknown Cause | Patrol - found nothing | 20 | 23080 | 37.3094 | -121.835 | No | Overcast;32-90 F |  |  | 23-0058638 | OH | Sus | 45719302 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1834105 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | INTERRUPTER | 721686 | 20230407 | 1709 | 20230408 | 1754 | 2082852 | 1485 | Distribution Circuit | 3rd Party | Vandalism | 72 | 32748 | 37.4256 | -121.9738 | No | Overcast;32-90 F | Pothead(Riser Termination) | Broken | 23-0058694 | OH | Sus | 45719251 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834130 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2109 | 83892109 | SWITCH | 27708 | 20230407 | 2141 | 20230407 | 2147 | 2082939 | 6 | Distribution Circuit | 3rd Party | Vandalism | 5 | 30 | 37.3987 | -121.8914 | No | Overcast;32-90 F | Secondary | Normal | 23-0058703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834141 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 25345 | 20230408 | 958 | 20230408 | 1235 | 2083234 | 157 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 471 | 37.061 | -121.5802 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834233 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | OCB | 1106/12 | 20230408 | 2152 | 20230409 | 1815 | 2083473 | 1188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4766 | 365160 | 37.3611 | -121.8646 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1834271 | 0 | Non-EPSS | N | 2023 | C & GRD
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 11135 | 20230409 | 718 | 20230410 | 309 | 2083565 | 1191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2382 | 37.3784 | -121.8364 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0058862 | OH | Sus | 31641740 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1834311 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 11133 | 20230410 | 1112 | 20230410 | 1335 | 2084159 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3052 | 37.3791 | -121.8378 | No | Clear;32-90 F |  |  | 23-0059155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834588 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315944935208 | 20230410 | 2257 | 20230411 | 225 | 2084940 | 208 | Transformer only | Vegetation | Tree - grew into line | 6 | 1248 | 37.4586 | -121.8999 | No | Overcast-Fog;32-90 F | Secondary | Burned/flashed | 23-0059352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834680 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15919 | 20230411 | 601 | 20230411 | 1045 | 2085359 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 5107 | 37.1947 | -121.8067 | No | Overcast-Fog;32-90 F |  |  | 23-0059517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1834856 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | OPEN JUMPERS 3 P/E/O CGC 315930727316 | 20230411 | 1202 | 20230411 | 1356 | 2085622 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1824 | 37.2421 | -121.8985 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0051606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1834907 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2114 | 82832114 | OCB | 2114/2 | 20230412 | 105 | 20230412 | 540 | 2086094 | 106 | Distribution Circuit | Equipment Failure/Involved | Underground | 1994 | 40794 | 37.4156 | -121.8882 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0059848 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1835008 | 0 | Non-EPSS | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | MILPITAS-2111 | 82832111 | OCB | 2111/2 | 20230412 | 445 | 20230412 | 453 | s1836419 | 8 | Distribution Circuit | Equipment Failure/Involved | Underground | 1086 | 8688 | 37.4156 | -121.8881 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0059848 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Multi-Fault | 0 | No | No | No | 1836419 | 0 | Non-EPSS | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315990028642 | 20230412 | 700 | 20230412 | 1314 | 2086186 | 374 | Transformer only | 3rd Party | Vehicle | 8 | 2992 | 37.2785 | -121.8794 | No | Clear;32-90 F | Service conductor | Broken | 23-0059906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1835035 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 28507 | 20230413 | 2306 | 20230414 | 110 | 2088178 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 136 | 16872 | 37.3588 | -121.862 | No | Clear;32-90 F |  |  | 23-0060938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835693 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | INTERRUPTER | 76982 | 20230414 | 617 | 20230414 | 839 | 2088240 | 142 | Distribution Circuit | Animal | Bird found | 146 | 20732 | 37.1609 | -121.6446 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0061005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1835720 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | JUMPER | 4457 #2 LD SIDE JUMPER | 20230414 | 1129 | 20230414 | 2205 | 2088901 | 636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1908 | 36.9282 | -121.5467 | No | Clear;32-90 F | Jumper | Burned Open | 23-0061258 | OH | Sus | 45730761 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1835919 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4885 | 20230414 | 1811 | 20230415 | 1550 | 2088935 | 1299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 11691 | 37.0201 | -121.5423 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835928 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 28455 | 20230415 | 811 | 20230415 | 900 | 2089097 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 1421 | 37.428 | -121.9121 | No | Partly Cloudy;32-90 F |  |  | 23-0061322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1835999 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 12007 | 20230415 | 1244 | 20230416 | 1820 | 2089254 | 1776 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 27858 | 37.3455 | -121.834 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0061366 | OH | Sus | 35438113 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836050 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 63746 | 20230416 | 1154 | 20230418 | 324 | 2089663 | 2264 | Distribution Circuit | Equipment Failure/Involved | Underground | 173 | 43772 | 37.24 | -121.8505 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0061463 | UG | Sus | 45731869 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836164 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28665 | 20230416 | 1314 | 20230416 | 1734 | 2089698 | 260 | Distribution Circuit | 3rd Party | Metallic Balloon | 41 | 10660 | 37.3071 | -121.9882 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0061491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836179 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 8431 | 20230417 | 745 | 20230417 | 903 | 2090004 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 183 | 14274 | 37.4347 | -121.914 | No | Clear;32-90 F |  |  | 23-0061559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836294 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230417 | 832 | 20230417 | 951 | 2090092 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 6162 | 37.2239 | -121.8583 | No | Overcast;32-90 F |  |  | 23-0061584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836368 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 1983 | 20230417 | 840 | 20230417 | 1400 | 2090113 | 320 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 320 | 36.981 | -121.5278 | No | Clear;32-90 F |  |  | 23-0061716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1836448 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0407 | 82250407 | TRANSFORMER | 315904330387 | 20230417 | 1640 | 20230419 | 1728 | 2090396 | 2928 | Transformer only | Equipment Failure/Involved | Overhead | 31 | 90768 | 37.326 | -121.9097 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 23-0061805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836487 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-2118 | 83802118 | SWITCH | 43776 | 20230417 | 1718 | 20230417 | 1730 | 2090781 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 24 | 37.4036 | -121.936 | No | Partly Cloudy;32-90 F | Capacitor | Broken | 23-0061814 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1836493 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | RECLOSER | 388696 | 20230418 | 919 | 20230418 | 1035 | 2091294 | 76 | Distribution Circuit | Animal | Squirrel | 2704 | 108205 | 37.311 | -121.9076 | No | Partly Cloudy;32-90 F | Recloser | Failed/Faulted | 23-0061938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836680 | 0 | Non-EPSS | N | 2023 | A- B PHASE & GRD
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRIP-SAVER | 28421 | 20230418 | 1410 | 20230418 | 1445 | 2091502 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 70 | 36.9304 | -121.5251 | No | Partly Cloudy;32-90 F |  |  | 23-0062151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1836768 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316611021045 | 20230418 | 1632 | 20230418 | 1859 | 2091750 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 294 | 37.0723 | -121.6624 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0062229 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1836792 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 70351 | 20230419 | 706 | 20230419 | 1131 | 2091987 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 25440 | 37.3235 | -121.8449 | No | Clear;32-90 F |  |  | 23-0062461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837037 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | RIVER OAKS-2102 | 82342102 | FUSE | 43230 | 20230419 | 935 | 20230419 | 1140 | 2092439 | 125 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 375 | 37.4102 | -121.9464 | No | Partly Cloudy;32-90 F | Customer Equipment | Broken | 23-0062464 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837038 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316628019420 | 20230420 | 1453 | 20230421 | 215 | 2093274 | 682 | Transformer only | Vegetation | Tree - fell into line | 1 | 682 | 37.0276 | -121.656 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0063126 | OH | Sus | 45737381 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | Yes | 1837288 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRANSFORMER | 316966015575 | 20230421 | 1511 | 20230421 | 1909 | 2094083 | 238 | Transformer only | Environmental/External | Flood/Erosion | 1 | 238 | 36.9232 | -121.539 | No | Clear;32-90 F | Metering Equipment |  | 23-0063647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837617 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 40745 | 20230421 | 1626 | 20230421 | 1758 | 2094180 | 92 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 16008 | 37.2588 | -121.8053 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0063629 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837608 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315968131044 | 20230421 | 1933 | 20230422 | 928 | 2094295 | 835 | Transformer only | Equipment Failure/Involved | Overhead | 40 | 33400 | 37.3443 | -121.8881 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0063648 | OH | Sus | 31642791 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1837618 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316360323836 | 20230422 | 1545 | 20230423 | 1400 | 2094679 | 1335 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1335 | 37.1486 | -121.7487 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0063779 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837795 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315873730690 | 20230423 | 541 | 20230423 | 832 | 2094903 | 279 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 4743 | 37.3345 | -121.9203 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837840 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0407 | 82250407 | TRANSFORMER | 315904330387 | 20230423 | 1148 | 20230423 | 1744 | 2095029 | 356 | Transformer only | Equipment Failure/Involved | Overhead | 31 | 11036 | 37.326 | -121.9097 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837872 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | TRANSFORMER | 315922231637 | 20230423 | 1222 | 20230424 | 354 | 2095046 | 932 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2536 | 37.3606 | -121.9043 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1837882 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 70217 | 20230423 | 1445 | 20230423 | 1652 | 2095085 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 1240 | 37.2954 | -121.9133 | No | Partly Cloudy;32-90 F |  |  | 23-0063866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1837891 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | JUMPER | OJ 6 SP S/W/ OF FUCO 1983 | 20230424 | 1157 | 20230425 | 1139 | s1838196 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1422 | 36.9764 | -121.5302 | No | Clear;32-90 F | Jumper | Broken | 23-0064247 | OH | Sus | 45739901 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1838196 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 98637 | 20230424 | 1418 | 20230424 | 1721 | 2095861 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 183 | 37.3158 | -121.8665 | No | Clear;32-90 F |  |  | 23-0064233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1838190 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | TRANSFORMER | C475 | 20230425 | 3 | 20230425 | 136 | 2096118 | 93 | Transformer only | Equipment Failure/Involved | Underground | 16 | 1488 | 37.2547 | -121.8321 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0064297 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838229 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T20744 | 20230425 | 407 | 20230426 | 129 | 2096176 | 1282 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 10256 | 37.2946 | -121.7743 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0064475 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838413 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | OCB | 1107/2 | 20230425 | 437 | 20230425 | 826 | 2096178 | 229 | Distribution Circuit | Equipment Failure/Involved | Underground | 5607 | 249937 | 37.341 | -121.9019 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0064303 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838237 | 0 | Non-EPSS | N | 2023 | GRD INST & B INST
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | OCB | 1107/2 | 20230425 | 437 | 20230425 | 923 | -2096178 | 286 | Distribution Circuit | Equipment Failure/Involved | Underground | 327 | 93522 | 37.341 | -121.9019 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0064303 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1838376 | 0 | Non-EPSS | N | 2023 | A PH TIME - B PH INST - GRD IN
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 42487 | 20230425 | 831 | 20230425 | 949 | 2096322 | 78 | Distribution Circuit | Animal | Squirrel | 4 | 338 | 37.3425 | -121.7767 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0064399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838385 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2112 | 82952112 | FUSE | 42742 | 20230425 | 1129 | 20230425 | 1402 | 2096609 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3366 | 37.257 | -121.7899 | No | Clear;32-90 F |  |  | 23-0064532 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838441 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 9786 | 20230425 | 1637 | 20230425 | 1836 | 2096945 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 17731 | 37.2458 | -121.8285 | No | Clear;32-90 F |  |  | 23-0064699 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838501 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR176 | 20230426 | 940 | 20230427 | 140 | 2097410 | 960 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1101 | 234960 | 37.0929 | -121.6472 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0065024 | OH | Sus | 31643382 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1838756 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | INTERRUPTER | 4318 | 20230426 | 2047 | 20230427 | 2230 | 2097902 | 1543 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 159554 | 37.2218 | -121.8788 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0065262 | UG | Sus | 45741968 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838837 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 33832 | 20230427 | 809 | 20230427 | 923 | 2098123 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 11618 | 37.2334 | -121.8307 | No | Clear;32-90 F |  |  | 23-0065381 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1838929 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316770522410 | 20230427 | 1204 | 20230427 | 1830 | 2098244 | 386 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 772 | 37.1102 | -121.6085 | No | Clear;32-90 F | Transformer | Broken | 23-0065529 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839037 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 92999 | 20230427 | 1356 | 20230427 | 1717 | 2098694 | 201 | Distribution Circuit | Animal | Bird found | 7 | 1407 | 37.3368 | -121.8171 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839079 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 28913 | 20230427 | 1406 | 20230427 | 1559 | 2098554 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1582 | 37.3094 | -121.8867 | No | Overcast;32-90 F |  |  | 23-0065694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839069 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | T28332 | 20230427 | 1810 | 20230428 | 31 | 2098790 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5334 | 37.129 | -121.6526 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0065815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839159 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | T97535 | 20230427 | 1810 | 20230428 | 34 | 2098789 | 384 | Transformer only | Equipment Failure/Involved | Underground | 13 | 4992 | 37.1293 | -121.652 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0065817 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839160 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | TRANSFORMER | 316230830006 | 20230427 | 1811 | 20230427 | 1924 | 2098913 | 73 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 730 | 37.3167 | -121.7972 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0065791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1839147 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | OCB | 2108/2 | 20230427 | 1832 | 20230427 | 1958 | 2098792 | 86 | Distribution Circuit | Equipment Failure/Involved | Underground | 1252 | 71977 | 37.403 | -121.9056 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 23-0065734 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839095 | 0 | Non-EPSS | N | 2023 | 51- 51N
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 12767 | 20230427 | 1836 | 20230427 | 2221 | 2098798 | 225 | Distribution Circuit | Animal | Bird found | 910 | 77792 | 37.3148 | -121.8194 | No | Clear;32-90 F | Fuse | Normal | 23-0065773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839129 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315971428837 | 20230427 | 2245 | 20230428 | 224 | 2098905 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 2409 | 37.2838 | -121.8859 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0065788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839143 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 14225 | 20230428 | 1036 | 20230428 | 2351 | 2099285 | 795 | Distribution Circuit | Animal | Bird found | 17 | 13515 | 37.3813 | -121.8247 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0066052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839328 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | C2541 | 20230428 | 1206 | 20230428 | 1433 | 2099365 | 147 | Transformer only | Unknown Cause | Patrol - found nothing | 65 | 9555 | 37.3209 | -121.9763 | No | Overcast;32-90 F |  |  | 23-0066108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1839349 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 38848 | 20230429 | 1503 | 20230429 | 1800 | 2100149 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 8837 | 37.4299 | -121.9123 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0066304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839534 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 77753 | 20230429 | 1727 | 20230429 | 1825 | 2100208 | 58 | Distribution Circuit | Animal | Bird found | 3 | 174 | 37.363 | -121.8706 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0066326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839546 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | B PHASE BURNT OPEN JUMPER | 20230429 | 1837 | 20230430 | 11 | 2100220 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4008 | 37.2761 | -121.8979 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0066338 | OH | Sus | 45745034 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839554 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | TRANSFORMER | 315903227465 | 20230430 | 200 | 20230430 | 408 | 2100347 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1792 | 37.2459 | -121.9086 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0066365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1839584 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15571 | 20230430 | 610 | 20230430 | 750 | 2100388 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 600 | 37.3429 | -121.7227 | No | Clear;32-90 F |  |  | 23-0066386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1839605 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR586 | 20230430 | 751 | 20230430 | 2133 | 2100403 | 822 | Distribution Circuit | Animal | Bird found | 463 | 255206 | 37.0279 | -121.5275 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0066384 | OH | Sus | 45745404 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1839603 | 0 | EPSS Ckt | N | 2023 | C PHASE- GRD & 51 TIME OC
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315896034475 | 20230501 | 113 | 20230501 | 1036 | 2101011 | 563 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3378 | 37.4383 | -121.9148 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839725 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | 316700823752 | 20230501 | 614 | 20230501 | 1315 | 2101358 | 421 | Transformer only | Animal | Bird found | 1 | 421 | 37.1469 | -121.6329 | No | Overcast;32-90 F | Transformer (OH) |  | 23-0066704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1839911 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 14165 | 20230502 | 456 | 20230502 | 1059 | 2102129 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 45910 | 37.3366 | -121.8468 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0066895 | OH | Sus | 31643769 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840025 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2107 | 83892107 | SWITCH | 24970 | 20230502 | 1442 | 20230502 | 1453 | 2102992 | 11 | Distribution Circuit | 3rd Party | Vandalism | 8 | 88 | 37.4014 | -121.9149 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0067250 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840242 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | SWITCH | X1118 | 20230502 | 1625 | 20230502 | 1635 | 2103019 | 10 | Distribution Circuit | Vegetation | Tree - fell into line | 356 | 3560 | 37.3886 | -121.9002 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0067335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840259 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 25179 | 20230503 | 1539 | 20230503 | 1804 | 2104000 | 145 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1305 | 37.0278 | -121.6565 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0067802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1840568 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1103 | 83801103 | FUSE | 11841 | 20230503 | 1928 | 20230504 | 424 | 2104136 | 536 | Distribution Circuit | Animal | Squirrel | 9 | 4824 | 37.3759 | -121.9053 | No | Partly Cloudy-Rain;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0067863 | OH | Sus | 31644028 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840595 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 27965 | 20230504 | 1221 | 20230505 | 216 | 2104768 | 514 | Distribution Circuit | Equipment Failure/Involved | Underground | 196 | 163660 | 37.3248 | -121.7923 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0068241 | UG | Sus | 31644067 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840865 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20230504 | 1351 | 20230504 | 1525 | 2104842 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 506 | 47564 | 37.3558 | -121.8299 | No | Clear;32-90 F |  |  | 23-0068377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840901 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 17725 | 20230504 | 1521 | 20230504 | 1728 | 2104909 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1905 | 37.2229 | -121.8759 | No | Clear;32-90 F |  |  | 23-0068438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840924 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15571 | 20230505 | 615 | 20230505 | 752 | 2105194 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 582 | 37.3429 | -121.7227 | No | Clear;32-90 F |  |  | 23-0068596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1841029 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13931 | 20230505 | 712 | 20230505 | 949 | 2105212 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 8478 | 37.331 | -121.8514 | No | Partly Cloudy;32-90 F |  |  | 23-0068660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841122 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | TRANSFORMER | 316011430040 | 20230505 | 1053 | 20230506 | 41 | 2105470 | 828 | Transformer only | Unknown Cause | Patrol - not conducted | 14 | 11592 | 37.3187 | -121.8753 | No | Overcast;32-90 F |  |  | 23-0068766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1841168 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 1103 | 20230505 | 1157 | 20230505 | 1507 | 2105563 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 134 | 25460 | 37.3136 | -121.9168 | No | Overcast;32-90 F |  |  | 23-0068812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841181 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315962729038 | 20230505 | 1538 | 20230506 | 314 | 2105725 | 696 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 11832 | 37.2893 | -121.889 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0068978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841212 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 27047 | 20230505 | 1657 | 20230507 | 1035 | 2106101 | 2498 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2498 | 37.1145 | -121.6441 | No | Overcast;32-90 F | Connector or Splice (UG) | Broken | 23-0069145 | UG | Sus | 45750836 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841345 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 28255 | 20230505 | 1711 | 20230507 | 320 | 2105769 | 2049 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 47127 | 37.1146 | -121.6442 | No | Overcast;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0068996 | UG | Sus | 45750836 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841222 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-2115 | 83802115 | TRANSFORMER | T22225 | 20230506 | 727 | 20230507 | 1427 | 2105985 | 1834 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 5520 | 37.3892 | -121.9241 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0069136 | UG | Sus | 35441912 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841335 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 42237 | 20230506 | 1007 | 20230507 | 1504 | 2106086 | 1737 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 12159 | 37.2504 | -121.8439 | No | Clear;32-90 F | Bushing | Burned/flashed | 23-0069152 | UG | Sus | 45750930 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1841354 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20230506 | 1051 | 20230506 | 1656 | 2106135 | 365 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 7 | 2555 | 37.0839 | -121.7682 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0069147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841348 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 3219 | 20230507 | 1220 | 20230508 | 1430 | 2106778 | 1570 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 3140 | 37.0032 | -121.562 | No | Overcast;32-90 F | Elbow | Burned/flashed | 23-0069289 | UG | Sus | 45751328 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841486 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | JUMPER | FB @ 3720 SIERRA RD | 20230508 | 2122 | 20230509 | 719 | 2108169 | 597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 4776 | 37.4072 | -121.8356 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1841801 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | RECLOSER | XR024 | 20230509 | 1915 | 20230509 | 2215 | 2108962 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 28080 | 37.395 | -121.8571 | No | Partly Cloudy;32-90 F | Jumper | Broken | 23-0070182 | OH | Sus | 45753654 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842077 | 0 | Non-EPSS | N | 2023 | A & B PHASE OC
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 40465 | 20230510 | 2013 | 20230510 | 2150 | 2109788 | 97 | Distribution Circuit | 3rd Party | Vehicle | 39 | 3783 | 37.0244 | -121.5617 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0070669 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1842378 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 2075 | 20230511 | 129 | 20230511 | 1529 | 2109874 | 840 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 30240 | 37.3344 | -121.8263 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0070717 | UG | Sus | 31644919 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842415 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315999730495 | 20230511 | 741 | 20230511 | 1034 | 2110047 | 173 | Transformer only | Unknown Cause | Patrol - found nothing | 29 | 5017 | 37.3294 | -121.877 | No | Overcast;32-90 F |  |  | 23-0070848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1842550 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | JUMPER | OPEN JUMPERS 1 SP/E/O 19415 | 20230511 | 2242 | 20230512 | 145 | 2110751 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4209 | 37.3001 | -121.8827 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0071163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1842701 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315796730661 | 20230512 | 1830 | 20230512 | 1922 | 2111491 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 468 | 37.3338 | -121.9465 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842940 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15571 | 20230513 | 555 | 20230513 | 953 | 2111610 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1428 | 37.3429 | -121.7227 | No | Clear;32-90 F |  |  | 23-0071549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843009 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4871 | 20230513 | 1445 | 20230513 | 1609 | 2111839 | 84 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 1512 | 37.0904 | -121.6134 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843039 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20230514 | 1653 | 20230514 | 1840 | 2112260 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 9416 | 37.2267 | -121.8632 | No | Clear;32-90 F |  |  | 23-0071687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1843134 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 12891 | 20230514 | 2136 | 20230515 | 830 | 2112387 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 452 | 46862 | 37.353 | -121.847 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0071721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843171 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 40269 | 20230515 | 509 | 20230515 | 1600 | 2113065 | 651 | Distribution Circuit | Animal | Squirrel | 1 | 651 | 37.2611 | -121.9209 | No | Clear;32-90 F | Fuse | Normal | 23-0072053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843393 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | INTERRUPTER | 32104 | 20230516 | 15 | 20230516 | 1756 | 2113633 | 1061 | Distribution Circuit | Equipment Failure/Involved | Underground | 750 | 564354 | 37.2921 | -121.7521 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 23-0072125 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1843448 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | OCB | 2105/2 | 20230516 | 1423 | 20230516 | 2110 | 2114269 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 572 | 18250 | 37.0071 | -121.5569 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0072233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1843655 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | TRIMBLE-2119 | 83802119 | OCB | 2119/2 | 20230516 | 1705 | 20230516 | 1923 | 2114372 | 138 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 7213 | 37.3828 | -121.9262 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0072448 | UG | Sus | 31645746 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843674 | 0 | Non-EPSS | N | 2023 | GRD
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | SWITCH | 7303 | 20230516 | 1821 | 20230517 | 254 | 2114420 | 513 | Distribution Circuit | Vegetation | Tree - bark fell into line | 449 | 17254 | 37.2869 | -121.9126 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0072268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1843684 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 11205 | 20230517 | 1026 | 20230517 | 1408 | 2114935 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 233 | 41605 | 37.245 | -121.8565 | No | Clear;32-90 F | Jumper | Broken | 23-0072680 | OH | Sus | 45766013 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1843944 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 33306 | 20230517 | 1627 | 20230518 | 512 | 2115246 | 765 | Distribution Circuit | Equipment Failure/Involved | Underground | 153 | 89013 | 37.3029 | -121.8071 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0072895 | UG | Sus | 45766540 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844029 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315900529657 | 20230517 | 2256 | 20230518 | 107 | 2115478 | 131 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1572 | 37.306 | -121.9107 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0072921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844054 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 26571 | 20230518 | 305 | 20230518 | 515 | 2115520 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1690 | 37.3175 | -121.8719 | No | Overcast;32-90 F |  |  | 23-0072942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1844070 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | JUMPER | FB'S @ 1423 SANTE FE DRIVE | 20230518 | 802 | 20230518 | 1810 | 2116373 | 608 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 19456 | 37.2538 | -121.8904 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073235 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844263 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4871 | 20230518 | 1007 | 20230519 | 310 | 2115969 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6132 | 37.0904 | -121.6134 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844184 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | OCB | 2105/2 | 20230518 | 1213 | 20230519 | 749 | 2116117 | 1176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4299 | 147334 | 37.1267 | -121.6595 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073107 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844206 | 0 | EPSS Ckt | N | 2023 | GRD/PH INST BKR TRBL & VIRT
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | TRANSFORMER | 316276829662 | 20230518 | 2015 | 20230519 | 1514 | 2116495 | 1139 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 5695 | 37.3075 | -121.7812 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0073304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844313 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315875129077 | 20230519 | 1457 | 20230519 | 1654 | 2117188 | 117 | Transformer only | Company Initiated | Construction Activity/equip- company | 8 | 936 | 37.2899 | -121.9191 | No | Partly Cloudy;32-90 F | Secondary | Together | 23-0073706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1844543 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | OCB | 1105/2 | 20230519 | 2021 | 20230520 | 2320 | 2117340 | 1575 | Distribution Circuit | 3rd Party | Vehicle | 98 | 20416 | 37.3828 | -121.9267 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0073735 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | No | 1844560 | 0 | Non-EPSS | N | 2023 | B & C PH
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 28213 | 20230521 | 736 | 20230521 | 853 | 2117914 | 77 | Distribution Circuit | Animal | Squirrel | 1 | 77 | 37.1907 | -121.7127 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0073954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844779 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 17455 | 20230521 | 1729 | 20230521 | 1826 | 2118105 | 57 | Distribution Circuit | 3rd Party | Metallic Balloon | 89 | 5073 | 37.3446 | -121.843 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0074005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1844834 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | OCB | 2101/2 | 20230522 | 915 | 20230522 | 1056 | 2118555 | 101 | Distribution Circuit | Equipment Failure/Involved | Underground | 1680 | 126204 | 37.2386 | -121.7912 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0074129 | UG | Sus | 45770470 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845015 | 0 | Non-EPSS | N | 2023 | C- GRD & INST
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | TRANSFORMER | 315898927272 | 20230522 | 927 | 20230522 | 1505 | 2118484 | 338 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 4056 | 37.2405 | -121.9099 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0074146 | OH | Sus | 45770337 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1845032 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | SWITCH | 953640 | 20230522 | 1623 | 20230523 | 137 | 2118981 | 554 | Distribution Circuit | Company Initiated | Personnel- company | 3 | 1662 | 37.239 | -121.7914 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0074129 | UG | Sus | 45770470 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845107 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316782320411 | 20230522 | 1813 | 20230522 | 2344 | 2119081 | 331 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 331 | 37.0554 | -121.6036 | No | Clear;32-90 F |  |  | 23-0074438 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1845164 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1102 | 82261102 | SWITCH | 29878 | 20230522 | 1854 | 20230522 | 1902 | 2119099 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 8 | 37.3378 | -121.8904 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0065065 | UG | Sus | 35384221 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1845126 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230523 | 1331 | 20230523 | 1424 | 2119857 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 3888 | 37.2239 | -121.8583 | No | Clear;32-90 F |  |  | 23-0074781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845394 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 2083 | 20230523 | 1421 | 20230523 | 1600 | 2119888 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 196 | 19385 | 37.4142 | -121.8671 | No | Clear;32-90 F |  |  | 23-0074820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845407 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 40847 | 20230523 | 1453 | 20230524 | 320 | 2119912 | 747 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 31 | 23157 | 37.2423 | -121.8439 | No | Clear;32-90 F | Fuse | Normal | 23-0074882 | OH | Sus | 45771845 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845443 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315958729450 | 20230523 | 1638 | 20230523 | 1815 | 2119962 | 97 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1358 | 37.3006 | -121.8906 | No | Partly Cloudy;32-90 F | Secondary | Arcing | 23-0074844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845415 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 19401 | 20230524 | 1226 | 20230524 | 1241 | 2120606 | 15 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 1275 | 37.2945 | -121.9034 | No | Clear;32-90 F | Jumper | Broken | 23-0075147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845659 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 30927 | 20230524 | 1243 | 20230524 | 1747 | 2120620 | 304 | Distribution Circuit | Vegetation | Tree - grew into line | 53 | 16112 | 37.2899 | -121.9228 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0075154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845663 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20230524 | 1622 | 20230525 | 45 | 2120762 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3521 | 37.0839 | -121.7682 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0075269 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845697 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 18073 | 20230525 | 532 | 20230525 | 929 | 2120955 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2370 | 37.2201 | -121.7872 | No | Clear;32-90 F |  |  | 23-0075413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1845799 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 41461 | 20230525 | 933 | 20230525 | 1016 | 2121156 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 4085 | 37.3121 | -121.796 | No | Partly Cloudy;32-90 F |  |  | 23-0075474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845879 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20230525 | 1131 | 20230525 | 1253 | 2121243 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 137 | 36.9852 | -121.4853 | No | Overcast;32-90 F |  |  | 23-0075566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1845922 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28145 | 20230526 | 851 | 20230526 | 943 | 2121972 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 936 | 37.0653 | -121.6615 | No | Clear;32-90 F |  |  | 23-0075940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846147 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28279 | 20230526 | 950 | 20230526 | 1035 | 2122072 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 195 | 8775 | 37.0992 | -121.6425 | No | Clear;32-90 F |  |  | 23-0075974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846160 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 3797 | 20230527 | 500 | 20230527 | 1621 | 2122536 | 681 | Distribution Circuit | 3rd Party | Vehicle | 41 | 27921 | 37.0728 | -121.588 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0076265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846285 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | SWITCH | 603392 | 20230527 | 840 | 20230527 | 1412 | 2122684 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3984 | 36.9652 | -121.5654 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0076309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1846331 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | SWITCH | 603392 | 20230527 | 840 | 20230527 | 1412 | 2122717 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 3984 | 36.9652 | -121.5654 | No | Clear;32-90 F |  |  | 23-0076309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1846339 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 42217 | 20230528 | 746 | 20230528 | 1156 | 2122979 | 250 | Distribution Circuit | Animal | Squirrel | 1 | 250 | 37.3214 | -121.8964 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0076440 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846422 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2106 | 83892106 | TRANSFORMER | C1279 | 20230528 | 826 | 20230528 | 1005 | 2122952 | 99 | Transformer only | Equipment Failure/Involved | Electrical Overload | 28 | 2772 | 37.4126 | -121.907 | No | Overcast;32-90 F | Secondary | Normal | 23-0076429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846416 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | INTERRUPTER | 4318 | 20230528 | 1509 | 20230529 | 802 | 2123101 | 1013 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 53407 | 37.2218 | -121.8788 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 23-0076466 | UG | Sus | 45793349 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846441 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315964229718 | 20230529 | 1343 | 20230529 | 1629 | 2123473 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 996 | 37.3079 | -121.8889 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0076580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846532 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315740029960 | 20230529 | 1348 | 20230530 | 32 | 2123490 | 644 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 16 | 10304 | 37.3137 | -121.9656 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0076612 | OH | Sus | 45790878 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846560 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12849 | 20230530 | 721 | 20230530 | 757 | 2123695 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 2124 | 37.247 | -121.848 | No | Clear;32-90 F |  |  | 23-0076652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846599 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 11851 | 20230530 | 1309 | 20230530 | 1835 | 2124103 | 326 | Distribution Circuit | Vegetation | Tree - grew into line | 94 | 30644 | 37.337 | -121.9368 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0076873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846785 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316121730624 | 20230530 | 1317 | 20230531 | 155 | 2124118 | 758 | Distribution Circuit | 3rd Party | Other | 60 | 25188 | 37.3334 | -121.8349 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0076922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1846798 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | T20143 | 20230530 | 2338 | 20230531 | 832 | 2124388 | 534 | Transformer only | Equipment Failure/Involved | Underground | 18 | 9612 | 37.125 | -121.6398 | No | Overcast;32-90 F | Service conductor | Burned/flashed | 23-0077049 | UG | Sus | 45805521 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846857 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 27935 | 20230531 | 809 | 20230531 | 913 | 2124544 | 64 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 3516 | 37.2246 | -121.8587 | No | Partly Cloudy;32-90 F |  |  | 23-0077155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1846952 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0403 | 82250403 | TRANSFORMER | 315895630559 | 20230531 | 941 | 20230531 | 1945 | 2124565 | 604 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 10268 | 37.3305 | -121.9129 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0077201 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1847008 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 7237 | 20230531 | 1705 | 20230601 | 410 | 2125010 | 665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 101745 | 37.3573 | -121.8644 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0077432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1847084 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 14253 | 20230531 | 1908 | 20230531 | 2002 | 2125083 | 54 | Distribution Circuit | 3rd Party | Metallic Balloon | 6 | 324 | 37.4783 | -121.8537 | No | Clear;32-90 F | Fuse | Normal | 23-0077480 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1847096 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316144527296 | 20230602 | 626 | 20230602 | 742 | 2127050 | 76 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 532 | 37.242 | -121.8255 | No | Clear;32-90 F |  |  | 23-0078098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847441 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1081 | 20230602 | 631 | 20230602 | 1349 | 2127056 | 438 | Distribution Circuit | 3rd Party | Vehicle | 38 | 16644 | 36.9982 | -121.5243 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0078086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1847433 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20230602 | 2323 | 20230603 | 1711 | 2127705 | 1068 | Distribution Circuit | 3rd Party | Vehicle | 400 | 103929 | 37.1263 | -121.7284 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0078507 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847642 | 0 | EPSS Ckt | N | 2023 | A- B & G
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40800 | 20230603 | 640 | 20230603 | 959 | 2127765 | 199 | Distribution Circuit | Animal | Squirrel | 147 | 29253 | 37.2179 | -121.8575 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0078541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847682 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 6293 | 20230603 | 641 | 20230603 | 849 | 2127766 | 128 | Distribution Circuit | Animal | Squirrel | 163 | 20864 | 37.3158 | -121.9615 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0078543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847686 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230603 | 827 | 20230603 | 1122 | 2127818 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 13650 | 37.2239 | -121.8583 | No | Clear;32-90 F |  |  | 23-0078565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847706 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 9659 | 20230603 | 1859 | 20230603 | 2001 | 2128084 | 62 | Distribution Circuit | 3rd Party | Vehicle | 74 | 4588 | 37.3044 | -121.8258 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0078631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1847745 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 28535 | 20230604 | 641 | 20230604 | 1218 | 2128300 | 337 | Distribution Circuit | Animal | Squirrel | 15 | 5055 | 37.0245 | -121.5708 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0078707 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847813 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | FUSE | 15971 | 20230604 | 649 | 20230604 | 855 | 2128301 | 126 | Distribution Circuit | Animal | Bird found | 1 | 126 | 37.4585 | -121.9128 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0078682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847788 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315972229651 | 20230604 | 949 | 20230604 | 1019 | 2128330 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 630 | 37.2897 | -121.8858 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0078692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847802 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | T1937 | 20230605 | 1430 | 20230605 | 1622 | 2129368 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 784 | 37.4319 | -121.9066 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848097 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315917134248 | 20230605 | 1430 | 20230605 | 2125 | 2129367 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2075 | 37.431 | -121.9062 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0079130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848138 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 2831 | 20230605 | 1627 | 20230606 | 1201 | 2129473 | 1174 | Distribution Circuit | Vegetation | Tree - grew into line | 35 | 41090 | 37.2685 | -121.9152 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0079072 | OH | Sus | 45824860 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848101 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 28427 | 20230605 | 1635 | 20230605 | 2252 | 2129480 | 377 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 151 | 56927 | 37.2578 | -121.9126 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848098 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315817130237 | 20230605 | 2045 | 20230606 | 230 | 2129584 | 345 | Transformer only | Vegetation | Tree - fell into line | 16 | 5520 | 37.3216 | -121.9394 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 23-0079135 | OH | Sus | 31651380 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848145 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315821030279 | 20230605 | 2048 | 20230606 | 2250 | 2130014 | 1562 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 6248 | 37.3226 | -121.9382 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0079163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848168 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315762029343 | 20230605 | 2120 | 20230606 | 640 | 2130048 | 560 | Distribution Circuit | Vegetation | Tree - bark fell into line | 28 | 9786 | 37.297 | -121.9578 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0079183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848188 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | FUSE | 34668 | 20230606 | 416 | 20230606 | 620 | s1848197 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 361 | 44764 | 37.45 | -121.9096 | No | Clear;32-90 F |  |  | 23-0079189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848197 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | OCB | 1111/2 | 20230606 | 528 | 20230606 | 846 | 2130152 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3535 | 482845 | 37.3662 | -121.8437 | No | Overcast;32-90 F |  |  | 23-0079187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848192 | 0 | EPSS Ckt | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230606 | 701 | 20230606 | 931 | 2130196 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 8297 | 37.2239 | -121.8583 | No | Overcast-Drizzle;32-90 F |  |  | 23-0079244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848250 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316154628613 | 20230606 | 926 | 20230606 | 1900 | 2130439 | 574 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 19 | 10906 | 37.2784 | -121.8228 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0079475 | OH | Sus | 45825305 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848439 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 915889 | 20230606 | 947 | 20230606 | 1545 | 2130356 | 358 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 358 | 37.3717 | -121.9009 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0079518 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848453 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | TRANSFORMER | T50535 | 20230606 | 1108 | 20230606 | 1234 | 2130565 | 86 | Transformer only | Equipment Failure/Involved | Underground | 15 | 1290 | 37.2842 | -121.8559 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0079376 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1848396 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | INTERRUPTER | 55498 | 20230606 | 1907 | 20230607 | 58 | 2131253 | 351 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 17916 | 37.2844 | -121.8548 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 23-0079380 | UG | Sus | 35454524 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848481 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315762029343 | 20230607 | 50 | 20230607 | 201 | 2131353 | 71 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 994 | 37.297 | -121.9578 | No | Partly Cloudy;32-90 F | Secondary | Together | 23-0079612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1848527 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 26809 | 20230607 | 1201 | 20230607 | 1302 | 2131943 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 198 | 12078 | 37.2953 | -121.9703 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0079881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1848782 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 128561 | 20230607 | 1219 | 20230607 | 1225 | 2131965 | 6 | Distribution Circuit | 3rd Party | Vandalism | 9 | 54 | 37.4236 | -121.9725 | No | Overcast;32-90 F | Secondary | Normal | 23-0079873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848780 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | SWITCH | 4242 | 20230607 | 1611 | 20230608 | 745 | 2132093 | 934 | Distribution Circuit | 3rd Party | Vehicle | 2687 | 79295 | 37.4067 | -121.8469 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0079811 | UG | Sus | 38454594 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848822 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315905028371 | 20230608 | 843 | 20230608 | 902 | 2132472 | 19 | Transformer only | Vegetation | Tree - grew into line | 7 | 133 | 37.2708 | -121.9085 | No | Clear;32-90 F | Secondary | Normal | 23-0080203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1848973 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | XR336 | 20230608 | 1216 | 20230608 | 1353 | 2132729 | 97 | Distribution Circuit | 3rd Party | Metallic Balloon | 366 | 32686 | 37.2316 | -121.7616 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0080346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849078 | 0 | EPSS Ckt | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 2803 | 20230609 | 10 | 20230609 | 458 | 2133188 | 288 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 4608 | 37.3634 | -121.8904 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0080515 | UG | Sus | 35456399 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1849209 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | JUMPER | OJ AT 40437 | 20230609 | 726 | 20230609 | 1823 | 2133277 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3312 | 37.0698 | -121.5714 | No | Overcast;32-90 F | Jumper | Burned Open | 23-0080722 | OH | Sus | 45834537 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1849343 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 90473 | 20230609 | 1434 | 20230610 | 448 | 2133739 | 854 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 253 | 61666 | 37.3059 | -121.9066 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0081028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1849449 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230610 | 1318 | 20230610 | 1418 | 2134281 | 60 | Distribution Circuit | Animal | Bird found | 78 | 4680 | 37.2239 | -121.8583 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0081149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849602 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | FUSE | 34220 | 20230610 | 1833 | 20230610 | 1935 | 2134422 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 496 | 37.2996 | -121.758 | No | Partly Cloudy;32-90 F |  |  | 23-0081174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849620 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 14761 | 20230611 | 208 | 20230611 | 316 | 2134521 | 68 | Distribution Circuit | 3rd Party | Metallic Balloon | 47 | 3196 | 37.2641 | -121.8922 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 23-0081240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1849685 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15749 | 20230611 | 1012 | 20230611 | 1140 | 2134593 | 88 | Distribution Circuit | 3rd Party | Metallic Balloon | 227 | 19976 | 37.3675 | -121.8048 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0081275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849716 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 40289 | 20230611 | 1022 | 20230611 | 1952 | 2134569 | 570 | Distribution Circuit | 3rd Party | Metallic Balloon | 43 | 13810 | 37.3154 | -121.8239 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849710 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2109 | 82462109 | SWITCH | X1624 | 20230611 | 2031 | 20230613 | 43 | 2134829 | 1692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 50736 | 37.4196 | -121.9515 | No | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 23-0081346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849759 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 22523 | 20230612 | 740 | 20230612 | 903 | 2134971 | 83 | Distribution Circuit | Animal | Squirrel | 26 | 2158 | 37.315 | -121.9179 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0081420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849861 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | TRANSFORMER | T10854 | 20230612 | 918 | 20230613 | 601 | 2135151 | 1243 | Transformer only | Equipment Failure/Involved | Underground | 1 | 1243 | 37.3173 | -121.8757 | No | Partly Cloudy;32-90 F | Transformer | Leaking | 23-0081482 | UG | Sus | 35457206 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1849966 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | SWITCH | 4222 | 20230612 | 952 | 20230612 | 1258 | 2135193 | 186 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 211 | 37.3144 | -121.9382 | No | Partly Cloudy;32-90 F | Elbow | Deteriorated | 23-0081456 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1849958 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1114 | 82921114 | TRANSFORMER | T5081 | 20230612 | 1629 | 20230612 | 1653 | 2135591 | 24 | Transformer only | Equipment Failure/Involved | Underground | 31 | 744 | 37.3014 | -121.9263 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0081674 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850065 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | JUMPER | JUMPERS SOURCE SIDE 12051 | 20230612 | 2050 | 20230613 | 525 | 2135687 | 515 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1030 | 37.3637 | -121.9061 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0081699 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850082 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 17717 | 20230613 | 614 | 20230613 | 820 | 2135745 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1804 | 37.1153 | -121.6356 | No | Overcast;32-90 F |  |  | 23-0081775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850150 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 6955 | 20230613 | 758 | 20230613 | 1741 | 2135810 | 583 | Distribution Circuit | Animal | Bird found | 78 | 26655 | 37.2239 | -121.8583 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0081824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850269 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 26441 | 20230613 | 945 | 20230613 | 2322 | 2136014 | 817 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 817 | 37.3172 | -121.8756 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0081825 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850272 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 28679 | 20230613 | 2251 | 20230614 | 405 | 2136483 | 314 | Distribution Circuit | Vegetation | Tree - grew into line | 26 | 8164 | 37.3019 | -121.9908 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0082094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850411 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | FUSE | 43209 | 20230614 | 1215 | 20230614 | 1236 | 2136895 | 21 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 30 | 630 | 37.3499 | -121.8852 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0082290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850615 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315893434416 | 20230614 | 1220 | 20230614 | 1850 | 2136878 | 390 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 7020 | 37.4367 | -121.9158 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0082260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850604 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 26463 | 20230614 | 1623 | 20230614 | 1656 | 2137111 | 33 | Distribution Circuit | 3rd Party | Metallic Balloon | 192 | 6336 | 37.1146 | -121.6415 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082459 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1850671 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 71435 | 20230615 | 10 | 20230615 | 323 | 2137365 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 7334 | 37.2659 | -121.9112 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0082532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850734 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 8105 | 20230615 | 957 | 20230615 | 1605 | 2137597 | 368 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 27600 | 37.3295 | -121.8429 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0082755 | UG | Sus | 45849633 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1850859 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | RECLOSER | 93368 | 20230615 | 1739 | 20230616 | 156 | 2137916 | 497 | Distribution Circuit | Vegetation | Tree - grew into line | 2226 | 34960 | 37.3466 | -121.8498 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0082897 | OH | Sus | 45849647 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850906 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 41807 | 20230615 | 1900 | 20230616 | 324 | 2137980 | 504 | Distribution Circuit | Vegetation | Tree - grew into line | 25 | 12600 | 37.3105 | -121.9598 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 23-0082924 | OH | Sus | 45849667 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850915 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 1727 | 20230615 | 2134 | 20230615 | 2335 | 2138069 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 4114 | 37.333 | -121.8529 | No | Partly Cloudy;32-90 F |  |  | 23-0082960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1850949 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | XR162 | 20230616 | 400 | 20230616 | 448 | 2138133 | 48 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1083 | 45492 | 37.2123 | -121.836 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0082994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1850966 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 8507 | 20230616 | 1448 | 20230616 | 1642 | 2138714 | 114 | Distribution Circuit | 3rd Party | Metallic Balloon | 224 | 16536 | 37.2666 | -121.8047 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0083260 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851181 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | T8890 | 20230616 | 1527 | 20230616 | 1552 | 2138748 | 25 | Transformer only | Equipment Failure/Involved | Underground | 14 | 350 | 37.0898 | -121.6316 | No | Clear;32-90 F | Secondary | Broken | 23-0083257 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1851179 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20230617 | 1657 | 20230617 | 1935 | 2139480 | 158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 19592 | 37.1083 | -121.7324 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0083411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851355 | 0 | EPSS Ckt | Y | 2023 | A & C INST
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | RECLOSER | XR032 | 20230617 | 1815 | 20230617 | 1821 | 2139501 | 6 | Distribution Circuit | 3rd Party | Metallic Balloon | 1283 | 7698 | 37.3755 | -121.8207 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0083417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851366 | 0 | EPSS Ckt | N | 2023 | A & B
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | TRANSFORMER | 315980535037 | 20230617 | 2342 | 20230618 | 30 | 2139637 | 48 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 48 | 37.4541 | -121.886 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0083469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1851412 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 3799 | 20230618 | 1613 | 20230618 | 1737 | 2139878 | 84 | Distribution Circuit | 3rd Party | Metallic Balloon | 46 | 3832 | 37.0765 | -121.5715 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0083531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851476 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 32190 | 20230618 | 1930 | 20230618 | 2220 | 2139998 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 4930 | 37.3446 | -121.8512 | No | Partly Cloudy;32-90 F |  |  | 23-0083570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851514 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1106 | 82831106 | OCB | 1106/2 | 20230619 | 301 | 20230620 | 225 | 2140143 | 1404 | Distribution Circuit | 3rd Party | Vehicle | 1812 | 54074 | 37.4156 | -121.888 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0083583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1851523 | 0 | Non-EPSS | N | 2023 | B-C-GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | T28332 | 20230619 | 827 | 20230619 | 846 | 2140290 | 19 | Transformer only | Equipment Failure/Involved | Underground | 14 | 266 | 37.129 | -121.6526 | No | Clear;32-90 F | Transformer (UG) | Normal | 23-0083605 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851564 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316139927578 | 20230619 | 1040 | 20230619 | 1455 | 2140390 | 255 | Transformer only | Vegetation | Tree - fell into line | 10 | 2550 | 37.2498 | -121.8273 | No | Clear;32-90 F | Transformer | Arcing | 23-0083629 | OH | Sus | 45851912 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851620 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20230619 | 1252 | 20230620 | 205 | 2140530 | 793 | Distribution Circuit | 3rd Party | Vehicle | 769 | 127768 | 37.1334 | -121.6754 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0083657 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1851639 | 0 | EPSS Ckt | Y | 2023 | A & C PHASE OC
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 12139 | 20230619 | 1907 | 20230619 | 2103 | 2140735 | 116 | Distribution Circuit | Animal | Bird found | 85 | 9860 | 37.2792 | -121.815 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0083723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851687 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 32020 | 20230619 | 2050 | 20230621 | 1334 | 2140766 | 149 | Distribution Circuit | Animal | Bird found | 615 | 26057 | 37.386 | -121.8886 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0083727 | OH | Sus | 35459880 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851691 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 30034 | 20230619 | 2359 | 20230620 | 143 | 2140793 | 104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1513 | 117928 | 37.2992 | -121.8232 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851717 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 12503 | 20230620 | 613 | 20230620 | 929 | 2140851 | 196 | Distribution Circuit | Animal | Squirrel | 33 | 6406 | 37.3437 | -121.9299 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0083814 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1851858 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 316375022425 | 20230620 | 959 | 20230620 | 1252 | 2141205 | 173 | Distribution Circuit | Animal | Bird found | 19 | 2279 | 37.1098 | -121.744 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0083842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851886 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE OC
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | INTERRUPTER | 30900 | 20230620 | 1407 | 20230622 | 240 | 2141498 | 2151 | Distribution Circuit | Equipment Failure/Involved | Underground | 451 | 160605 | 37.2761 | -121.8331 | No | Clear;32-90 F | Elbow | Broken | 23-0083984 | UG | Sus | 35460407 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1851948 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | RECLOSER | 517530 | 20230621 | 320 | 20230621 | 1610 | 2141896 | 770 | Distribution Circuit | 3rd Party | Other | 119 | 21789 | 36.9737 | -121.519 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0084079 | OH | Sus | 31652949 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | Yes | No | 1852013 | 0 | EPSS Ckt | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 27026 | 20230621 | 338 | 20230622 | 58 | 2141892 | 1280 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 18748 | 37.0721 | -121.5936 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0084176 | UG | Sus | 35460680 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852100 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28271 | 20230621 | 547 | 20230621 | 1012 | 2141910 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 5565 | 37.0967 | -121.6325 | No | Clear;32-90 F |  |  | 23-0084216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852156 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1109 | 83801109 | FUSE | 35148 | 20230621 | 1959 | 20230621 | 2131 | 2142671 | 92 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 1331 | 37.3834 | -121.9243 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0084457 | UG | Sus | 45855852 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852247 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | SWITCH | 35046 | 20230622 | 125 | 20230622 | 134 | 2142804 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 210 | 1890 | 37.3872 | -121.8904 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0083727 | OH | Sus | 35459880 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852282 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | SWITCH | 33476 | 20230622 | 204 | 20230622 | 229 | 2142810 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 133 | 3325 | 37.3833 | -121.8858 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0083727 | OH | Sus | 35459880 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852284 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316110931514 | 20230622 | 1417 | 20230622 | 1611 | 2143286 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1824 | 37.3578 | -121.8391 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0084818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852494 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | JUMPER | JUMPERS @ 888 DIANA AVE | 20230622 | 2035 | 20230623 | 208 | 2143590 | 333 | Distribution Circuit | Equipment Failure/Involved | Overhead | 707 | 108759 | 37.3472 | -121.8372 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0084860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1852520 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 93058 | 20230622 | 2036 | 20230623 | 312 | -2143590 | 396 | Distribution Circuit | Company Initiated | Return Circuit Normal | 69 | 27324 | 37.345 | -121.8379 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 23-0084860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1852564 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 15505 | 20230623 | 527 | 20230623 | 1138 | 2143974 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 3710 | 37.314 | -121.7557 | No | Overcast;32-90 F |  |  | 23-0085049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852713 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 60726 | 20230623 | 950 | 20230623 | 1745 | 2143989 | 475 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 77425 | 37.2595 | -121.8632 | No | Clear;32-90 F | Other | Failed/Faulted | 23-0085220 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852757 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5179 | 20230624 | 1143 | 20230624 | 1507 | 2144866 | 204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 408 | 37.0715 | -121.7134 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085345 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852892 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 28201 | 20230624 | 1329 | 20230625 | 928 | 2144931 | 1199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 34771 | 37.1409 | -121.6417 | No | Clear;32-90 F |  |  | 23-0085360 | OH | Sus | 31653304 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852904 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316173031218 | 20230624 | 1346 | 20230624 | 2305 | 2144939 | 559 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 7826 | 37.3499 | -121.8176 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852901 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 19775 | 20230625 | 750 | 20230625 | 838 | 2145190 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 4032 | 37.2597 | -121.8894 | No | Partly Cloudy;32-90 F |  |  | 23-0085409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1852959 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0408 | 82250408 | TRANSFORMER | 315972930305 | 20230625 | 1959 | 20230626 | 1357 | 2145492 | 1078 | Transformer only | Equipment Failure/Involved | Electrical Overload | 19 | 20482 | 37.3241 | -121.8861 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0085472 | OH | Sus | 35461271 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853026 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | RECLOSER | XR376 | 20230625 | 2117 | 20230626 | 500 | 2145534 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 954 | 133465 | 37.2692 | -121.809 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085452 | OH | Sus | 45858930 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853006 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4351 | 20230626 | 701 | 20230626 | 758 | 2145595 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 456 | 37.0687 | -121.5974 | No | Clear;32-90 F |  |  | 23-0085493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853045 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 5939 | 20230626 | 907 | 20230626 | 1017 | 2145760 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 5740 | 37.4337 | -121.8675 | No | Partly Cloudy;32-90 F |  |  | 23-0085539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853170 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | JUMPER | FB @ 4045 KLAMATH DR | 20230626 | 1207 | 20230626 | 1440 | 2146077 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 5967 | 37.3006 | -121.9726 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0085634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853211 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2112 | 82952112 | SWITCH | 67446 | 20230626 | 1849 | 20230626 | 2129 | 2146401 | 160 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 480 | 37.258 | -121.7843 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0085723 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853286 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | COIS AT C1697 TWD 1696 | 20230626 | 1921 | 20230627 | 556 | 2146409 | 632 | Distribution Circuit | Equipment Failure/Involved | Underground | 134 | 18280 | 37.3362 | -121.7901 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0085736 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853289 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315731829716 | 20230626 | 1939 | 20230627 | 1738 | 2146318 | 1319 | Transformer only | Vegetation | Tree - branch fell on line | 36 | 47484 | 37.3071 | -121.9682 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0085835 | OH | Sus | 45860694 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853291 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 67275 | 20230626 | 2100 | 20230626 | 2249 | 2146448 | 109 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2196 | 84045 | 37.3537 | -121.8291 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0080628 | OH | Sus | 35058704 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853301 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR332 | 20230627 | 1244 | 20230627 | 1904 | 2147065 | 380 | Distribution Circuit | 3rd Party | Other | 92 | 34912 | 37.3494 | -121.6124 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853500 | 0 | EPSS Ckt | Y | 2023 | A & C PH
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316114127327 | 20230628 | 647 | 20230628 | 833 | 2147445 | 106 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 636 | 37.2427 | -121.836 | No | Clear;32-90 F |  |  | 23-0086426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853685 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 41599 | 20230628 | 822 | 20230628 | 905 | 2147537 | 43 | Distribution Circuit | 3rd Party | Metallic Balloon | 96 | 4128 | 37.2974 | -121.833 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0086434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853701 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | JUMPER | FLYING BELLS NORTH OF NEWHALL ST | 20230628 | 1639 | 20230628 | 2328 | 2148289 | 409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 14724 | 37.3374 | -121.9488 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0086821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853853 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | TRANSFORMER | 315908131762 | 20230628 | 2130 | 20230629 | 144 | 2148339 | 254 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 5842 | 37.3639 | -121.9092 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0086853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1853863 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | 316027030385 | 20230629 | 452 | 20230629 | 1308 | 2148590 | 496 | Transformer only | Vegetation | Tree - branch fell on line | 33 | 16368 | 37.3264 | -121.8675 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0086918 | OH | Sus | 31653905 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853910 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 44826 | 20230629 | 1317 | 20230630 | 313 | 2149004 | 836 | Distribution Circuit | Equipment Failure/Involved | Underground | 272 | 121540 | 37.3208 | -121.842 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0087207 | UG | Sus | 45864987 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854114 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | OTHER | J80680 TWD T28332 | 20230629 | 1524 | 20230630 | 316 | 2149312 | 712 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 14 | 9968 | 37.1291 | -121.6523 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087357 | UG | Sus | 35463741 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1854165 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20230629 | 1528 | 20230630 | 58 | 2149116 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 770 | 118644 | 37.1334 | -121.6754 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0087296 | OH | Sus | 31653950 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854131 | 0 | EPSS Ckt | Y | 2023 | C PHASE OC
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316064231408 | 20230629 | 1743 | 20230629 | 1951 | 2149239 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 3456 | 37.3547 | -121.8551 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854154 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 40264 | 20230629 | 1927 | 20230630 | 1507 | 2149303 | 1180 | Distribution Circuit | Equipment Failure/Involved | Underground | 217 | 47153 | 37.2309 | -121.8113 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0087359 | UG | Sus | 35463674 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1854167 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316956420422 | 20230629 | 2122 | 20230630 | 520 | 2148897 | 478 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 478 | 37.0559 | -121.5438 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0087373 | OH | Sus | 35463760 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854187 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 15095 | 20230630 | 1315 | 20230630 | 1721 | 2149931 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 492 | 36.9262 | -121.5256 | No | Clear;Above 90 |  |  | 23-0087755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854426 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1109 | 83531109 | OCB | 1109/2 | 20230630 | 1855 | 20230630 | 1941 | 2150244 | 46 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1961 | 90206 | 37.3662 | -121.8438 | No | Clear;32-90 F |  |  | 23-0087773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1854436 | 0 | Non-EPSS | N | 2023 | SET A AND B RLY CONTROL ALARM
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 14463 | 20230630 | 1915 | 20230630 | 1954 | 2150271 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 546 | 37.3584 | -121.8204 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0087777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854441 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28745 | 20230630 | 1939 | 20230630 | 2024 | 2150284 | 45 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 17 | 765 | 37.2775 | -121.8116 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0087786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1854451 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 1131 | 20230701 | 652 | 20230701 | 752 | s1854591 | 60 | Distribution Circuit | Animal | Squirrel | 10 | 600 | 37.3072 | -121.982 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854591 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 71435 | 20230701 | 1200 | 20230701 | 1501 | 2150776 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 6878 | 37.2659 | -121.9112 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0087911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854577 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 11306 | 20230701 | 1355 | 20230701 | 1408 | 2150834 | 13 | Distribution Circuit | Equipment Failure/Involved | Underground | 509 | 5120 | 37.3516 | -121.8495 | No | Clear;Above 90 | Secondary | Burned Open | 23-0087938 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854590 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 75205 | 20230701 | 1425 | 20230701 | 1508 | 2150870 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 2580 | 37.3071 | -121.9463 | No | Clear;Above 90 |  |  | 23-0087943 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854594 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | OCB | 2108/2 | 20230701 | 1635 | 20230701 | 2157 | 2150981 | 212 | Distribution Circuit | Equipment Failure/Involved | Underground | 3070 | 291755 | 37.403 | -121.9056 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 23-0087961 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854608 | 0 | Non-EPSS | N | 2023 | 51N- C-PHASE TOC & GRD
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 33242 | 20230701 | 1731 | 20230701 | 1916 | 2151068 | 105 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 324 | 31680 | 37.2102 | -121.8734 | No | Clear;Above 90 | Fuse | Burned Open | 23-0087986 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1854629 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 71421 | 20230701 | 1816 | 20230701 | 2209 | 2151162 | 233 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 48 | 11184 | 37.3098 | -121.8981 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0088052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854694 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 11306 | 20230701 | 1817 | 20230702 | 11 | 2151337 | 354 | Distribution Circuit | Equipment Failure/Involved | Underground | 509 | 13520 | 37.3516 | -121.8495 | No | Partly Cloudy;Above 90 | Secondary | Burned/flashed | 23-0087955 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854644 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | TRANSFORMER | 315833530492 | 20230701 | 1854 | 20230701 | 2334 | 2151281 | 280 | Transformer only | Unknown Cause | Patrol - found nothing | 14 | 3920 | 37.3288 | -121.934 | No | Partly Cloudy;32-90 F |  |  | 23-0088075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1854714 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1104 | 82261104 | TRANSFORMER | T10305 | 20230701 | 2003 | 20230703 | 308 | 2151488 | 1865 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 2069 | 37.3557 | -121.9138 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0088092 | UG | Sus | 35464171 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1854730 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 5335BP | 20230702 | 824 | 20230702 | 1227 | 2151916 | 243 | Distribution Circuit | Equipment Failure/Involved | Underground | 199 | 15162 | 37.0905 | -121.6288 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0087982 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1854755 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315877230215 | 20230702 | 949 | 20230702 | 1032 | 2152015 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 817 | 37.3214 | -121.919 | No | Partly Cloudy;32-90 F |  |  | 23-0088153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854782 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315878730746 | 20230702 | 1914 | 20230704 | 450 | 2152603 | 2016 | Transformer only | Animal | Squirrel | 2 | 4032 | 37.3361 | -121.9185 | No | Partly Cloudy-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 23-0088242 | OH | Sus | 31654246 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854871 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | SWITCH | 5578 | 20230703 | 107 | 20230703 | 202 | 2152882 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 366 | 6263 | 37.4269 | -121.9102 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0087961 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1854930 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 77177 | 20230703 | 545 | 20230703 | 1525 | 2152989 | 580 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 17892 | 37.2995 | -121.8126 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0088324 | OH | Sus | 31654210 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1854953 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316140030294 | 20230703 | 1008 | 20230703 | 1258 | 2153217 | 170 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 2380 | 37.3244 | -121.8285 | No | Clear;32-90 F | Secondary | Arcing | 23-0088422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855006 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 317129433087 | 20230704 | 1156 | 20230704 | 1530 | 2154172 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 214 | 37.4064 | -121.4891 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0088769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855173 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | OCB | 1112/2 | 20230704 | 1831 | 20230704 | 1837 | 2154185 | 6 | Distribution Circuit | 3rd Party | Metallic Balloon | 1234 | 7404 | 37.2332 | -121.9012 | No | Clear;32-90 F | Switch (OH) | Arcing | 23-0088771 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855176 | 0 | Non-EPSS | N | 2023 | NA
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316061730475 | 20230705 | 305 | 20230705 | 1232 | 2154343 | 567 | Transformer only | Environmental/External | Fire- Forest/Grass | 10 | 5670 | 37.3291 | -121.8555 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 23-0088812 | OH | Sus | 31654253 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855220 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 71131 | 20230705 | 932 | 20230705 | 1033 | 2154522 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 205 | 12505 | 37.3428 | -121.8456 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0088930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855316 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40363 | 20230705 | 1229 | 20230705 | 1735 | 2154678 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 306 | 37.1277 | -121.661 | No | Clear;32-90 F |  |  | 23-0089140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855365 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317024219006 | 20230705 | 1622 | 20230706 | 621 | 2154774 | 839 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 2517 | 37.0175 | -121.5203 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0089123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855356 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | OTHER | J8941 TWD T65721 | 20230705 | 1830 | 20230706 | 424 | 2154898 | 594 | Distribution Circuit | 3rd Party | Vehicle | 7 | 4158 | 37.313 | -121.7741 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0089148 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855373 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315914630319 | 20230705 | 2244 | 20230706 | 1131 | 2154998 | 767 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 9204 | 37.3242 | -121.9061 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0089189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855402 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 8195 | 20230706 | 55 | 20230706 | 223 | 2155057 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1408 | 37.3426 | -121.7952 | No | Clear;32-90 F |  |  | 23-0089197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855407 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 13017 | 20230706 | 1806 | 20230706 | 1837 | 2155762 | 31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 1798 | 37.3197 | -121.8965 | No | Clear;32-90 F |  |  | 23-0089593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855589 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | SWITCH | 7077 | 20230706 | 2013 | 20230707 | 252 | 2155816 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 57456 | 37.3551 | -121.9005 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0089581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855592 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15525 | 20230707 | 606 | 20230707 | 809 | 2155979 | 123 | Distribution Circuit | Animal | Bird found | 184 | 22632 | 37.3353 | -121.7714 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0089670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1855630 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315710430254 | 20230707 | 1945 | 20230707 | 2035 | 2156570 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 300 | 37.3216 | -121.9754 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0090024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855769 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 42104 | 20230708 | 758 | 20230708 | 930 | s1855843 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1380 | 37.3102 | -121.8445 | No | Clear;32-90 F |  |  | 23-0090079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855843 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | INTERRUPTER | 64850 | 20230708 | 800 | 20230708 | 1208 | 2157147 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 248 | 37.3379 | -121.9088 | No | Clear;32-90 F |  |  | 23-0090106 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855859 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 1295 | 20230708 | 849 | 20230709 | 1813 | 2157004 | 2004 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 86172 | 37.2762 | -121.8089 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0090084 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855847 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | TRANSFORMER | C3244 | 20230708 | 1500 | 20230709 | 2205 | 2157248 | 1865 | Distribution Circuit | Equipment Failure/Involved | Underground | 357 | 233604 | 37.2395 | -121.7699 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0090132 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1855885 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316123731096 | 20230708 | 1739 | 20230708 | 2240 | 2157326 | 301 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 3612 | 37.3463 | -121.8345 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0090153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855896 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | RECLOSER | XR060 | 20230709 | 1725 | 20230710 | 632 | 2157805 | 787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1370 | 288884 | 37.3288 | -121.8324 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0090252 | OH | Sus | 31654946 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | Yes | No | 1855981 | 0 | Non-EPSS | N | 2023 | ABC & GRD
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 31052 | 20230709 | 1930 | 20230711 | 2339 | 2157868 | 3129 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 84360 | 37.2529 | -121.8037 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0090275 | UG | Sus | 45875987 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856006 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 70689 | 20230709 | 2118 | 20230710 | 1059 | 2157889 | 821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2463 | 36.9841 | -121.4768 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0090277 | OH | Sus | 45876079 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1856009 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20230710 | 1452 | 20230711 | 259 | 2158777 | 727 | Distribution Circuit | 3rd Party | Vehicle | 399 | 58325 | 37.1446 | -121.6698 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856228 | 0 | EPSS Ckt | Y | 2023 | GRD INST
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | SWITCH | 73367 | 20230711 | 304 | 20230711 | 316 | 2159201 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 1200 | 37.1839 | -121.7418 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856300 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 9707 | 20230711 | 633 | 20230711 | 727 | 2159306 | 54 | Distribution Circuit | Animal | Bird found | 96 | 5184 | 37.2215 | -121.8512 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0090681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856316 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 28599 | 20230711 | 859 | 20230711 | 1145 | 2159543 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2324 | 37.3916 | -121.8136 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1856518 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315731829716 | 20230711 | 1430 | 20230711 | 2010 | 2159963 | 340 | Transformer only | Vegetation | Tree - grew into line | 36 | 12240 | 37.3071 | -121.9682 | No | Clear;32-90 F | Secondary | Normal | 23-0090917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856562 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | RECLOSER | 49970 | 20230711 | 1456 | 20230711 | 1541 | 2160009 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1592 | 71640 | 37.2698 | -121.8677 | No | Clear;32-90 F | Capacitor | Burned/flashed | 23-0090950 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856574 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | INTERRUPTER | 31626 | 20230712 | 510 | 20230713 | 1315 | 2160317 | 1925 | Distribution Circuit | Equipment Failure/Involved | Underground | 313 | 50469 | 37.4339 | -121.9005 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0091087 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856644 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 772623 | 20230712 | 815 | 20230712 | 920 | 2160475 | 65 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 130 | 37.284 | -121.8132 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856783 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0410 | 82250410 | TRANSFORMER | 315938530454 | 20230712 | 1156 | 20230712 | 2142 | 2161151 | 586 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 4102 | 37.328 | -121.8979 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856921 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 10719 | 20230712 | 1901 | 20230713 | 200 | 2161153 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 11313 | 37.0346 | -121.5824 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856922 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42699 | 20230713 | 1127 | 20230714 | 329 | 2161631 | 962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 23378 | 37.2741 | -121.9074 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0091833 | OH | Sus | 45885794 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857184 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | RECLOSER | XR258 | 20230714 | 230 | 20230714 | 1229 | 2162091 | 599 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 740 | 115726 | 37.2803 | -121.7577 | No | Clear;32-90 F |  |  | 23-0092123 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857291 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20230714 | 656 | 20230714 | 910 | 2162141 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5932 | 793574 | 37.4156 | -121.8881 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0092137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1857311 | 0 | EPSS Ckt | N | 2023 | A- B- C
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 28201 | 20230714 | 1133 | 20230714 | 1545 | s1857772 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 7308 | 37.1409 | -121.6417 | No | Clear;32-90 F |  |  | 23-0092753 |  | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857772 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20230715 | 434 | 20230715 | 1602 | 2163146 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 101683 | 37.1503 | -121.6194 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0092532 | OH | Sus | 31655605 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1857596 | 0 | EPSS Ckt | Y | 2023 | B & G
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315869929821 | 20230715 | 452 | 20230716 | 934 | 2163152 | 1722 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 20664 | 37.3103 | -121.9209 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0092730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857747 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316196631382 | 20230715 | 1737 | 20230715 | 1915 | 2163862 | 98 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 196 | 37.3544 | -121.8095 | No | Clear;Above 90 |  |  | 23-0092719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857738 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316825521550 | 20230715 | 2033 | 20230716 | 1424 | 2163867 | 1071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2686 | 37.0869 | -121.5894 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0092731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857748 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 71149 | 20230716 | 606 | 20230716 | 723 | 2164016 | 77 | Distribution Circuit | Animal | Squirrel | 106 | 6888 | 37.342 | -121.9298 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092768 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857789 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316140531453 | 20230716 | 1526 | 20230716 | 2113 | 2164360 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 5127 | 37.3562 | -121.8288 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092859 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857889 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | SWITCH | 1825 | 20230716 | 1549 | 20230716 | 1753 | 2164397 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 343 | 39445 | 37.3215 | -121.8769 | No | Partly Cloudy;Above 90 | Crossarm- Wood | Broken | 23-0092819 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857880 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | C1794 | 20230716 | 1756 | 20230716 | 1820 | 2164446 | 24 | Transformer only | Equipment Failure/Involved | Underground | 18 | 432 | 37.231 | -121.8133 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0092878 | UG | Sus | 45889319 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1857902 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | T2402 | 20230716 | 2050 | 20230717 | 1340 | 2164780 | 1010 | Distribution Circuit | Equipment Failure/Involved | Underground | 2753 | 75076 | 37.2364 | -121.8942 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0092933 | UG | Sus | 35468115 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857950 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 25177 | 20230717 | 39 | 20230717 | 442 | 2164955 | 178 | Distribution Circuit | Equipment Failure/Involved | Underground | 254 | 49422 | 37.3447 | -121.8277 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0092972 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1857987 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 316443431056 | 20230717 | 304 | 20230717 | 2217 | 2164992 | 1153 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2306 | 37.3466 | -121.7246 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0092991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858003 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR374 | 20230717 | 1044 | 20230717 | 1214 | 2165423 | 90 | Distribution Circuit | Animal | Bird found | 15 | 1350 | 37.4464 | -121.8577 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858175 | 0 | EPSS Ckt | Y | 2023 | B & C PH
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315692129263 | 20230717 | 1439 | 20230717 | 1640 | 2165686 | 121 | Transformer only | Equipment Failure/Involved | Overhead | 49 | 5929 | 37.2943 | -121.9818 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858243 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316608722813 | 20230717 | 1441 | 20230718 | 433 | 2165690 | 832 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5824 | 37.1205 | -121.6642 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0093486 | OH | Sus | 45891103 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858326 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316145730627 | 20230717 | 1544 | 20230718 | 154 | 2165788 | 610 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 12810 | 37.3336 | -121.8267 | No | Clear;Above 90 | Transformer | Broken- wire on ground | 23-0093373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1858249 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316142430667 | 20230717 | 1637 | 20230718 | 502 | 2165790 | 745 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 11920 | 37.3347 | -121.8278 | No | Clear;Above 90 | Transformer | Broken- wire on ground | 23-0093371 | OH | Sus | 45891228 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1858247 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26169 | 20230717 | 1810 | 20230717 | 2214 | 2165925 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2196 | 37.0516 | -121.5524 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0093396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858260 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315880227397 | 20230717 | 1919 | 20230718 | 1331 | 2165988 | 1092 | Distribution Circuit | Vegetation | Tree - grew into line | 20 | 16560 | 37.2439 | -121.9163 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0093410 | OH | Sus | 45891265 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1858269 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315893028789 | 20230717 | 2038 | 20230718 | 1414 | 2165901 | 1056 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 16615 | 37.2821 | -121.9128 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093424 | OH | Sus | 35469531 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858279 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 40305 | 20230718 | 747 | 20230718 | 914 | 2166242 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2175 | 37.0056 | -121.5777 | No | Clear;32-90 F |  |  | 23-0093565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858443 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316828319202 | 20230718 | 1314 | 20230719 | 124 | 2166742 | 730 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 8760 | 37.0223 | -121.587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093834 | OH | Sus | 45892327 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858537 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 26857 | 20230718 | 1819 | 20230718 | 2003 | 2167058 | 104 | Distribution Circuit | Animal | Squirrel | 114 | 8558 | 37.3366 | -121.9172 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0093930 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1858573 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 41249 | 20230718 | 2148 | 20230719 | 206 | 2167320 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 334 | 77735 | 36.9892 | -121.5735 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0093685 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858592 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | JUMPER | FB'S IRO 4418 MORAN DR | 20230719 | 1252 | 20230719 | 2240 | 2168004 | 588 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 18 | 10584 | 37.3063 | -121.9802 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094233 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858855 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | T5222 | 20230719 | 1332 | 20230719 | 1451 | 2168388 | 79 | Transformer only | Equipment Failure/Involved | Underground | 22 | 1738 | 37.2579 | -121.8964 | No | Clear;32-90 F | Service conductor | Broken | 23-0094356 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858910 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17467 | 20230719 | 1429 | 20230720 | 152 | 2168280 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5508 | 37.3666 | -121.8096 | No | Clear;32-90 F | Secondary | Broken | 23-0094293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1858881 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 17397 | 20230720 | 111 | 20230721 | 217 | 2168541 | 1506 | Distribution Circuit | 3rd Party | Vehicle | 2356 | 83945 | 37.2756 | -121.8424 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 23-0094481 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858972 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 17615 | 20230720 | 1008 | 20230720 | 1434 | 2168803 | 266 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 532 | 37.0936 | -121.5994 | No | Partly Cloudy;32-90 F |  |  | 23-0094797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859135 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20230720 | 1045 | 20230720 | 1357 | 2168836 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 3456 | 37.1127 | -121.7585 | No | Clear;32-90 F |  |  | 23-0094762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859123 | 0 | EPSS Ckt | Y | 2023 | N/A
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 28565 | 20230720 | 1554 | 20230720 | 1805 | 2169178 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 142 | 18602 | 37.3979 | -121.8288 | No | Clear;Above 90 |  |  | 23-0094881 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859162 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 247498 | 20230720 | 2250 | 20230721 | 225 | 2169391 | 215 | Distribution Circuit | 3rd Party | Vehicle | 145 | 6461 | 37.354 | -121.7871 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0094920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859222 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20230721 | 1230 | 20230721 | 1417 | 2169969 | 107 | Distribution Circuit | 3rd Party | Metallic Balloon | 387 | 41409 | 37.1503 | -121.6194 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0095258 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859438 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | OCB | 1110/2 | 20230721 | 1418 | 20230721 | 1641 | 2170052 | 143 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2853 | 407979 | 37.3043 | -121.868 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0095347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859460 | 0 | Non-EPSS | N | 2023 | A & C
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | RECLOSER | XR064 | 20230721 | 1706 | 20230721 | 2055 | 2170196 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1017 | 192573 | 37.2239 | -121.7797 | No | Clear;32-90 F |  |  | 23-0095407 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859481 | 0 | EPSS Ckt | Y | 2023 | A & C
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | OTHER | WIRE DOWN SSD 8743 | 20230721 | 1708 | 20230722 | 800 | 2170206 | 892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 361 | 321320 | 37.2375 | -121.7709 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095427 | OH | Sus | 31656451 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1859491 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316859318897 | 20230721 | 1718 | 20230723 | 143 | 2170027 | 1945 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 56405 | 37.014 | -121.5766 | No | Clear;32-90 F | Transformer | Broken | 23-0095412 | OH | Sus | 45897305 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859483 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72957 | 20230721 | 1836 | 20230721 | 2145 | 2170250 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 359 | 67822 | 37.3536 | -121.8295 | No | Clear;Above 90 |  |  | 23-0095450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859511 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | OCB | 2108/2 | 20230721 | 1926 | 20230723 | 715 | 2170325 | 1798 | Distribution Circuit | Equipment Failure/Involved | Underground | 2526 | 195777 | 37.1267 | -121.6595 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0095432 | UG | Sus | 35471864 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859498 | 0 | EPSS Ckt | N | 2023 | B GRD TIME OC
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 4873 | 20230721 | 2002 | 20230722 | 1720 | s1859682 | 1278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 25560 | 37.1259 | -121.6351 | No | Clear;32-90 F |  |  | 23-0095590 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859682 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | SWITCH | 984552 | 20230722 | 1104 | 20230722 | 1132 | 2170791 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 35 | 980 | 37.0422 | -121.5248 | No | Clear;32-90 F | Jumper | Normal | 23-0095543 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859648 | 0 | EPSS Ckt | Y | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20230722 | 1619 | 20230723 | 1450 | 2171005 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 212 | 149330 | 37.4483 | -121.8461 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859676 | 0 | EPSS Ckt | Y | 2023 | A AND C OC
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 49883 | 20230722 | 1842 | 20230722 | 2315 | 2171096 | 206 | Distribution Circuit | Equipment Failure/Involved | Underground | 321 | 62767 | 37.2662 | -121.847 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0095614 | UG | Sus | 45897561 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859705 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42711 | 20230722 | 2007 | 20230722 | 2212 | 2171133 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3125 | 37.279 | -121.9119 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0095622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859712 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | T8577 | 20230722 | 2225 | 20230722 | 2233 | 2171254 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 120 | 37.4427 | -121.9109 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0095642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859731 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | INTERRUPTER | 40010 | 20230723 | 705 | 20230723 | 1254 | 2171381 | 349 | Distribution Circuit | Equipment Failure/Involved | Underground | 449 | 100537 | 37.2368 | -121.8168 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0095666 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1859774 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | INTERRUPTER | 76982 | 20230723 | 1026 | 20230724 | 348 | 2171505 | 1042 | Distribution Circuit | Vegetation | Tree - branch fell on line | 146 | 29321 | 37.1609 | -121.6446 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095689 | OH | Sus | 31656642 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1859788 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | TRANSFORMER | C3699 | 20230723 | 1106 | 20230724 | 311 | 2171442 | 965 | Transformer only | Equipment Failure/Involved | Underground | 37 | 35705 | 37.3798 | -121.8707 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0095769 | UG | Sus | 45897544 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859866 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 71131 | 20230723 | 1159 | 20230723 | 1437 | 2171464 | 158 | Distribution Circuit | 3rd Party | Metallic Balloon | 205 | 32390 | 37.3428 | -121.8456 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 23-0095697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1859795 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 12465 | 20230723 | 1710 | 20230724 | 306 | 2171792 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12516 | 37.4312 | -121.8077 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0095709 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859808 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315886828493 | 20230723 | 1926 | 20230723 | 2331 | 2171866 | 245 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 4655 | 37.274 | -121.9149 | No | Clear;32-90 F |  |  | 23-0095756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1859860 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR044 | 20230723 | 1953 | 20230724 | 239 | 2171876 | 406 | Distribution Circuit | 3rd Party | Vehicle | 306 | 117946 | 37.4385 | -121.8718 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0095727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859828 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316967019762 | 20230723 | 2123 | 20230724 | 1554 | 2171852 | 1111 | Transformer only | Vegetation | Tree - grew into line | 7 | 7777 | 37.038 | -121.54 | No | Clear;32-90 F | Service conductor | Together | 23-0095747 | OH | Sus | 45897701 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1859849 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 70279 | 20230724 | 1529 | 20230724 | 2348 | 2172743 | 499 | Distribution Circuit | 3rd Party | Vehicle | 120 | 59880 | 37.4367 | -121.8851 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0096195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860118 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 15137 | 20230725 | 213 | 20230725 | 307 | 2172996 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 702 | 37.4135 | -121.843 | No | Clear;32-90 F |  |  | 23-0096273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860177 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 4305 | 20230725 | 807 | 20230725 | 1155 | 2173193 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2508 | 37.1743 | -121.696 | No | Clear;32-90 F |  |  | 23-0096471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1860381 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 73111 | 20230725 | 1350 | 20230725 | 1517 | 2173470 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 58 | 37.3013 | -121.8277 | No | Clear;32-90 F |  |  | 23-0096608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1860416 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | JUMPER | COIS @ T10146 TWD T10147 | 20230725 | 1526 | 20230726 | 253 | 2173666 | 643 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 83888 | 37.4358 | -121.8866 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0096414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860422 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1116 | 82921116 | FUSE | 18609 | 20230725 | 1954 | 20230725 | 2042 | 2173869 | 48 | Distribution Circuit | Animal | Squirrel | 10 | 480 | 37.2944 | -121.9642 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0096769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860452 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 25119 | 20230726 | 1420 | 20230727 | 600 | 2174549 | 940 | Distribution Circuit | Equipment Failure/Involved | Underground | 99 | 39480 | 37.2507 | -121.8439 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0097196 | UG | Sus | 31657148 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1860738 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 3965 | 20230726 | 1645 | 20230726 | 1657 | 2174687 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 1956 | 37.2657 | -121.831 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0035345 | UG | Sus | 45605399 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860741 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316200428299 | 20230727 | 912 | 20230727 | 1344 | 2175175 | 272 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 15 | 4080 | 37.2698 | -121.8068 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0097458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1860916 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | T6929 | 20230727 | 1422 | 20230728 | 220 | 2175563 | 718 | Distribution Circuit | Equipment Failure/Involved | Underground | 14 | 10052 | 37.222 | -121.8644 | No | Clear;32-90 F | Stepdown | Failed/Faulted | 23-0097781 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861035 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 40889 | 20230727 | 1752 | 20230727 | 2114 | 2175792 | 202 | Distribution Circuit | Equipment Failure/Involved | Underground | 161 | 25952 | 37.256 | -121.9011 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0097816 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861050 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 18303 | 20230727 | 2026 | 20230727 | 2312 | 2175815 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1660 | 37.3639 | -121.8093 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0097825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861057 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | SWITCH | 24112 | 20230727 | 2204 | 20230728 | 210 | 2175848 | 12 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 198 | 37.2204 | -121.8667 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0097791 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861069 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 15029 | 20230728 | 1327 | 20230728 | 1402 | 2176553 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 35 | 37.0146 | -121.5424 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098150 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861309 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315945727428 | 20230728 | 1650 | 20230729 | 809 | 2176597 | 919 | Transformer only | Vegetation | Tree - grew into line | 16 | 14704 | 37.245 | -121.894 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0098218 | OH | Sus | 45905847 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861338 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0410 | 82250410 | FUSE | 954361 | 20230728 | 2040 | 20230729 | 231 | 2176802 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6669 | 37.3144 | -121.8993 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098226 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861347 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | JUMPER | JUMPERS @ POLE W/ CGC 315845530460 | 20230729 | 1133 | 20230729 | 1700 | 2177102 | 327 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 12753 | 37.3281 | -121.9294 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0098316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861464 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | OCB | 1103/12 | 20230729 | 1147 | 20230729 | 1214 | 2177093 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 8559 | 37.3611 | -121.8645 | No | Partly Cloudy;32-90 F | Capacitor | Burned/flashed | 23-0098318 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861465 | 0 | Non-EPSS | N | 2023 | NONE
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316134531672 | 20230729 | 1337 | 20230730 | 1955 | 2177154 | 1818 | Transformer only | 3rd Party | Vehicle | 45 | 81810 | 37.3622 | -121.831 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0098342 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861481 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316079827598 | 20230729 | 1737 | 20230729 | 1957 | 2177292 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1260 | 37.2501 | -121.848 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0098362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861496 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4509 | 20230729 | 1809 | 20230730 | 1619 | 2177308 | 1330 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 5 | 6650 | 37.049 | -121.558 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0098365 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861499 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | JUMPER | OJ @ 5311 ESCOVER LN | 20230730 | 1637 | 20230731 | 248 | 2177887 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 7943 | 37.2524 | -121.8831 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0098464 | OH | Sus | 45906328 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861609 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 26237 | 20230730 | 1850 | 20230731 | 558 | 2177946 | 620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 27984 | 37.3128 | -121.9133 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1861619 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | SWITCH | 69522 | 20230731 | 1651 | 20230801 | 2135 | 2178825 | 1724 | Distribution Circuit | Equipment Failure/Involved | Underground | 591 | 57495 | 37.3342 | -121.8898 | No | Overcast;32-90 F | Secondary | Broken | 23-0098822 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861891 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | OCB | 1101/2 | 20230731 | 1809 | 20230801 | 150 | 2178915 | 461 | Distribution Circuit | 3rd Party | Metallic Balloon | 593 | 42931 | 37.3043 | -121.8683 | No | Overcast;32-90 F | Insulator | Broken | 23-0098873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861901 | 0 | Non-EPSS | N | 2023 | B & C PHASE
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20230731 | 1814 | 20230731 | 1938 | 2178917 | 84 | Distribution Circuit | Animal | Bird found | 1079 | 70191 | 37.2174 | -121.8338 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0098871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1861900 | 1 | EPSS Ckt | Y | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 44770 | 20230801 | 920 | 20230802 | 132 | 2179340 | 972 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 35850 | 37.311 | -121.7798 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0099085 | UG | Sus | 45907416 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862137 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | 316244230798 | 20230801 | 926 | 20230801 | 1208 | 2179317 | 162 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1944 | 37.3387 | -121.7929 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0099000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862097 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | FB IFO 1534 SAN ANDREAS | 20230801 | 1025 | 20230801 | 1655 | 2179454 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 48360 | 37.2719 | -121.8983 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0099045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862122 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 1307 | 20230801 | 1812 | 20230802 | 157 | 2179816 | 465 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 465 | 37.1361 | -121.6595 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0099317 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862210 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 15505 | 20230802 | 202 | 20230802 | 342 | 2180062 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1000 | 37.314 | -121.7557 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0099382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862258 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 4233 | 20230802 | 908 | 20230803 | 125 | 2180339 | 977 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2500 | 36.9617 | -121.5384 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0099578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862482 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | SWITCH | 10071 | 20230803 | 542 | 20230803 | 622 | 2181129 | 40 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 2800 | 37.3389 | -121.8827 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0098822 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862667 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4351 | 20230803 | 643 | 20230803 | 931 | 2181233 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1344 | 37.0687 | -121.5974 | No | Clear;32-90 F |  |  | 23-0099997 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862723 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 84307 | 20230803 | 908 | 20230803 | 1643 | 2181383 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 18200 | 37.3239 | -121.8698 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0100070 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1862786 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 14167 | 20230803 | 1210 | 20230803 | 1404 | 2181606 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 504 | 57456 | 37.3304 | -121.8355 | No | Clear;32-90 F |  |  | 23-0100144 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862824 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316152233159 | 20230803 | 1259 | 20230804 | 200 | 2181653 | 781 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 7029 | 37.4029 | -121.8255 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862848 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 15505 | 20230803 | 2230 | 20230803 | 2345 | 2181999 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 750 | 37.314 | -121.7557 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0100357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1862919 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20230804 | 755 | 20230804 | 937 | 2182111 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5933 | 441330 | 37.4156 | -121.8881 | No | Partly Cloudy;32-90 F |  |  | 23-0100445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862960 | 0 | EPSS Ckt | N | 2023 | TIME & OC TGT
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | INTERRUPTER | 64850 | 20230805 | 946 | 20230805 | 1331 | 2182990 | 225 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 225 | 37.3379 | -121.9088 | No | Clear;32-90 F | Interrupter | Normal | 23-0100915 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863324 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 28207 | 20230805 | 1106 | 20230806 | 1549 | 2183050 | 417 | Distribution Circuit | Animal | Squirrel | 56 | 23744 | 37.3129 | -121.9055 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0100937 | OH | Sus | 31661965 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863339 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 73111 | 20230805 | 1114 | 20230805 | 1458 | 2183056 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 149 | 37.3013 | -121.8277 | No | Clear;32-90 F |  |  | 23-0100912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863323 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 316006630531 | 20230805 | 1545 | 20230805 | 2302 | 2183212 | 437 | Transformer only | Equipment Failure/Involved | Overhead | 60 | 26220 | 37.3304 | -121.8747 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100930 | OH | Sus | 45913542 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863338 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1109 | 83531109 | FUSE | 82785 | 20230805 | 2258 | 20230805 | 2319 | 2183427 | 21 | Distribution Circuit | 3rd Party | Metallic Balloon | 64 | 1344 | 37.365 | -121.8448 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100969 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863369 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 77336 | 20230806 | 502 | 20230807 | 227 | 2183489 | 1285 | Distribution Circuit | Equipment Failure/Involved | Underground | 67 | 56452 | 37.0074 | -121.6 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0101012 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863424 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 40307 | 20230807 | 726 | 20230807 | 1850 | 2184061 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1368 | 36.9885 | -121.4906 | No | Clear;32-90 F | Insulator | Broken | 23-0101234 | OH | Sus | 45915946 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863687 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | JUMPER | DDE JUMPERS 2 SPANS S/O 13995 | 20230807 | 1437 | 20230808 | 650 | 2184827 | 973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2919 | 37.0164 | -121.542 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863754 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 18751 | 20230807 | 1703 | 20230807 | 1758 | 2184887 | 55 | Distribution Circuit | Vegetation | Tree - grew into line | 127 | 6985 | 37.2797 | -121.8908 | No | Clear;32-90 F | Secondary | Normal | 23-0101422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863770 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | TRANSFORMER | 316086333429 | 20230807 | 1751 | 20230808 | 147 | 2184992 | 476 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 476 | 37.4104 | -121.8486 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101449 | OH | Sus | 45916388 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863784 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42711 | 20230807 | 1839 | 20230807 | 1958 | 2185011 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1975 | 37.279 | -121.9119 | No | Clear;32-90 F |  |  | 23-0101456 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863791 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 72541 | 20230807 | 2115 | 20230807 | 2142 | 2185104 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 1053 | 37.3197 | -121.8205 | No | Clear;32-90 F | Secondary | Bent or Twisted | 23-0101471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863805 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | SWITCH | 70575 | 20230808 | 349 | 20230808 | 540 | 2185171 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 5439 | 37.2583 | -121.7054 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0101503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863835 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 27935 | 20230808 | 738 | 20230808 | 846 | 2185231 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 2967 | 37.2246 | -121.8587 | No | Partly Cloudy;32-90 F |  |  | 23-0101571 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863876 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 545795 | 20230808 | 843 | 20230808 | 1055 | 2185383 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 264 | 37.4188 | -121.9061 | No | Partly Cloudy;32-90 F |  |  | 23-0101666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864023 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315892827906 | 20230808 | 1445 | 20230809 | 330 | 2185909 | 765 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 13005 | 37.2579 | -121.9124 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0101899 | OH | Sus | 45917752 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864091 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OTHER | J82874 TWD T277522 | 20230809 | 905 | 20230809 | 1252 | 2186478 | 227 | Distribution Circuit | Company Initiated | Personnel- company | 13 | 2951 | 36.9936 | -121.5915 | No | Clear;32-90 F |  |  | 23-0099260 | OH | Sus | 35262174 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1864288 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316214228055 | 20230809 | 1233 | 20230809 | 1808 | 2186701 | 335 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 9 | 3015 | 37.263 | -121.802 | No | Clear;32-90 F | Secondary | Broken | 23-0102388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864418 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315964127721 | 20230810 | 55 | 20230810 | 249 | 2187096 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 3876 | 37.2532 | -121.8877 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0102475 | OH | Sus | 45918497 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | Yes | 1864458 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | SWITCH | SW | 20230810 | 520 | 20230810 | 530 | 2187262 | 10 | Distribution Circuit | Company Initiated | Personnel- company | 40 | 400 | 37.3561 | -121.8311 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0097137 | UG | Sus | 35058704 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1864470 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316941720089 | 20230810 | 1032 | 20230810 | 2023 | 2187644 | 591 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1773 | 37.047 | -121.549 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0102670 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1864672 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316199531375 | 20230811 | 1704 | 20230812 | 230 | 2188800 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 12563 | 37.3542 | -121.8086 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0103483 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865060 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | T14422 | 20230811 | 1802 | 20230812 | 1210 | 2188887 | 1088 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 17462 | 37.1349 | -121.6038 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0103511 | UG | Sus | 35480213 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1865083 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 8227 | 20230811 | 2113 | 20230812 | 1604 | 2188956 | 1131 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1131 | 37.4363 | -121.9573 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0103520 | UG | Sus | 45924554 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865091 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | OCB | 1108/2 | 20230811 | 2230 | 20230812 | 2252 | 2188967 | 1462 | Distribution Circuit | Equipment Failure/Involved | Underground | 936 | 188738 | 37.3043 | -121.868 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0103536 | UG | Sus | 45924555 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865108 | 0 | Non-EPSS | N | 2023 | NEU/GRD
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | INTERRUPTER | 43130 | 20230812 | 751 | 20230813 | 50 | 2189030 | 1019 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 1019 | 37.33 | -121.8583 | No | Partly Cloudy;32-90 F | Customer Equipment | Malfunctioning | 23-0103610 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1865214 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | JUMPER | NW/O 3895 | 20230812 | 913 | 20230812 | 1221 | 2189094 | 188 | Distribution Circuit | Vegetation | Tree - grew into line | 37 | 6956 | 37.2468 | -121.8909 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0103582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865183 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20230813 | 1355 | 20230813 | 1552 | 2189652 | 117 | Distribution Circuit | Animal | Bird found | 58 | 6786 | 37.053 | -121.5276 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0103762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865348 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE OC
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 18253 | 20230813 | 1455 | 20230813 | 1954 | 2189669 | 299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 12558 | 37.305 | -121.8805 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0103761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865347 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11209 | 20230813 | 1505 | 20230813 | 1820 | 2189623 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2925 | 37.3758 | -121.7922 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0103751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865341 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 5285 | 20230813 | 2108 | 20230813 | 2322 | 2189877 | 134 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 7370 | 37.1092 | -121.5955 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0103824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1865404 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 13053 | 20230813 | 2330 | 20230814 | 147 | 2189867 | 137 | Distribution Circuit | Vegetation | Tree - grew into line | 488 | 66856 | 37.2455 | -121.8926 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0103794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865374 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 3899 | 20230814 | 1229 | 20230814 | 1420 | 2190518 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1776 | 36.9684 | -121.5282 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0104046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865621 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T25214 | 20230814 | 1421 | 20230815 | 147 | 2190617 | 686 | Distribution Circuit | Equipment Failure/Involved | Underground | 40 | 12656 | 37.2961 | -121.8046 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0104221 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865656 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 469810 | 20230814 | 1647 | 20230814 | 2023 | 2190752 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3672 | 37.2003 | -121.7222 | No | Clear;Above 90 |  |  | 23-0104239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865662 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 25643 | 20230814 | 1930 | 20230815 | 316 | 2190927 | 466 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 466 | 37.3384 | -121.9176 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0104278 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865684 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316118631407 | 20230814 | 2227 | 20230815 | 130 | 2191165 | 183 | Transformer only | Equipment Failure/Involved | Electrical Overload | 26 | 4758 | 37.3551 | -121.8361 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0104308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1865714 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1106 | 82831106 | TRANSFORMER | 316032333721 | 20230815 | 313 | 20230815 | 2009 | 2191211 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 19152 | 37.4181 | -121.8674 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1865727 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | OCB | 2113/2 | 20230815 | 1840 | 20230817 | 250 | 2192139 | 1288 | Distribution Circuit | Equipment Failure/Involved | Underground | 4696 | 1402998 | 37.2448 | -121.7951 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0104798 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Multi-Fault | 0 | No | No | No | 1865992 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 44550 | 20230816 | 236 | 20230816 | 1848 | 2192333 | 919 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 38737 | 37.3258 | -121.82 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0104869 | UG | Sus | 45929404 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866052 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | JUMPER | OJ SOUTH OF 996133 | 20230816 | 1038 | 20230816 | 1502 | 2192765 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7128 | 37.3552 | -121.8358 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0105012 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866230 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315967927583 | 20230816 | 1918 | 20230817 | 450 | 2193274 | 572 | Transformer only | Equipment Failure/Involved | Electrical Overload | 20 | 11440 | 37.2494 | -121.8864 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0105326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866363 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | TRANSFORMER | 315870427585 | 20230816 | 2140 | 20230816 | 2236 | 2193356 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 616 | 37.249 | -121.9199 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 23-0105348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866386 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | SWITCH | 11931 | 20230816 | 2207 | 20230817 | 420 | 2193360 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6341 | 37.4128 | -121.8755 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0105330 | OH | Sus | 35481472 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866372 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | RECLOSER | XR294SB | 20230817 | 357 | 20230817 | 510 | 2193444 | 73 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 17666 | 36.9675 | -121.5525 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0105372 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866414 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | STONE-1105 | 83701105 | SWITCH | 67570 | 20230817 | 2008 | 20230818 | 317 | 2194171 | 429 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1716 | 37.3023 | -121.8657 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0105451 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1866615 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | OCB | 2101/2 | 20230818 | 502 | 20230818 | 1740 | 2194401 | 758 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3247 | 1547532 | 37.2332 | -121.9014 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0105854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1866667 | 0 | EPSS Ckt | Y | 2023 | C GRD INST
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | RECLOSER | XR174 | 20230818 | 505 | 20230818 | 1425 | 2194368 | 560 | Distribution Circuit | Equipment Failure/Involved | Underground | 3222 | 1075155 | 37.225 | -121.8662 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0105853 | UG | Sus | 45933195 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866666 | 0 | Non-EPSS | N | 2023 | A GRD
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 9931 | 20230818 | 939 | 20230818 | 1318 | 2194724 | 219 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 14892 | 37.3618 | -121.8085 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0106113 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866863 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 25419 | 20230818 | 1220 | 20230819 | 125 | 2194903 | 785 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 8952 | 37.2829 | -121.8255 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0106160 | UG | Sus | 45933561 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866888 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316143231256 | 20230818 | 1923 | 20230819 | 420 | 2195312 | 537 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2148 | 37.3509 | -121.8279 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0106286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866932 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 25269 | 20230819 | 733 | 20230819 | 1925 | 2195453 | 712 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 14788 | 37.3267 | -121.8544 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0106335 | UG | Sus | 45933648 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867024 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | T6246 | 20230819 | 950 | 20230820 | 1040 | 2195550 | 1490 | Transformer only | Equipment Failure/Involved | Underground | 21 | 31290 | 37.3008 | -121.8169 | No | Clear;32-90 F | Secondary | Broken | 23-0106371 | UG | Sus | 31664024 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867056 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | SWITCH | X1806 | 20230819 | 1145 | 20230819 | 1204 | 2195640 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 91 | 728 | 37.2135 | -121.8515 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 23-0105853 | UG | Sus | 45933195 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1867051 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315769529661 | 20230819 | 1315 | 20230820 | 1435 | 2195676 | 1520 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 16808 | 37.3057 | -121.9554 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0106495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1867162 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRANSFORMER | 317032116803 | 20230819 | 1512 | 20230819 | 1523 | 2195639 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 11 | 36.9569 | -121.517 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0106405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867078 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 18177 | 20230819 | 2317 | 20230820 | 339 | 2196593 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 10480 | 37.3678 | -121.8288 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0106517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867186 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | SWITCH | 42348 | 20230820 | 1502 | 20230821 | 256 | 2197096 | 714 | Distribution Circuit | 3rd Party | Vehicle | 3943 | 357927 | 37.1255 | -121.6615 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0106682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867335 | 0 | EPSS Ckt | Y | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 7929 | 20230820 | 1909 | 20230820 | 2152 | 2197295 | 163 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 4635 | 37.3534 | -121.903 | No | Overcast;32-90 F | Switch (UG) | Failed/Faulted | 23-0106746 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867394 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315849730141 | 20230820 | 2020 | 20230821 | 1025 | 2197342 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 13520 | 37.3191 | -121.9283 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 23-0106770 | OH | Sus | 31664109 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867418 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 43711 | 20230821 | 126 | 20230821 | 1025 | 2197456 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6468 | 37.3182 | -121.9283 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0106786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867436 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | 42348 | 20230821 | 628 | 20230821 | 1251 | 2197565 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3941 | 700092 | 37.1255 | -121.6615 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0106815 | OH | Sus | 45935185 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1867466 | 0 | EPSS Ckt | Y | 2023 | A GRD
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | JUMPER | 316227231241 | 20230821 | 905 | 20230821 | 1735 | 2197756 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 23970 | 37.3508 | -121.799 | No | Partly Cloudy;32-90 F | Secondary | Bent or Twisted | 23-0106899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867566 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316343522845 | 20230821 | 1844 | 20230822 | 1142 | 2198588 | 1018 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 1018 | 37.1213 | -121.6865 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0107288 | OH | Sus | 45935870 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867788 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1105 | 83701105 | SWITCH | 67558SW | 20230821 | 2032 | 20230822 | 313 | 2198709 | 401 | Distribution Circuit | Equipment Failure/Involved | Underground | 22 | 7250 | 37.3025 | -121.8658 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0107176 | UG | Sus | 35482709 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867783 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | JUMPER | FLYING BELLS IFO 1050 N. REDWOOD AVE. | 20230821 | 2115 | 20230822 | 116 | 2198726 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 6507 | 37.3339 | -121.9469 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867790 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | OCB | 2109/2 | 20230822 | 230 | 20230822 | 340 | 2198834 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4818 | 302500 | 37.3226 | -121.797 | No | Partly Cloudy;32-90 F |  |  | 23-0107338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867825 | 0 | EPSS Ckt | N | 2023 | C- G & 50
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 25419 | 20230822 | 458 | 20230823 | 235 | 2198847 | 1297 | Distribution Circuit | Equipment Failure/Involved | Underground | 126 | 24476 | 37.2829 | -121.8255 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 23-0107344 | UG | Sus | 45935879 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867833 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | OCB | 2109/2 | 20230822 | 635 | 20230822 | 1034 | 2198874 | 239 | Distribution Circuit | Equipment Failure/Involved | Underground | 4818 | 1097070 | 37.3226 | -121.797 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0107357 | UG | Sus | 31664353 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1867839 | 0 | EPSS Ckt | N | 2023 | C/GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5167 | 20230822 | 812 | 20230822 | 2238 | 2198962 | 866 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 6928 | 37.0913 | -121.6573 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0107567 | UG | Sus | 45937071 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868027 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3157 | 20230822 | 927 | 20230822 | 959 | 2199103 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 608 | 37.0608 | -121.665 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0107458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1867959 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 28869 | 20230822 | 1823 | 20230823 | 240 | 2199585 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 28329 | 37.3338 | -121.95 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0107775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868087 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315975527765 | 20230823 | 831 | 20230823 | 2053 | 2199876 | 742 | Transformer only | Vegetation | Tree - branch fell on line | 14 | 10388 | 37.2544 | -121.8838 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0107925 | OH | Sus | 31664600 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868290 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | 316799224513 | 20230823 | 1045 | 20230823 | 1829 | 2200083 | 464 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 464 | 37.1679 | -121.5995 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0108116 | OH | Sus | 31664372 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1868362 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 73111 | 20230823 | 1100 | 20230824 | 246 | 2200097 | 946 | Distribution Circuit | Environmental/External | Water | 4030 | 54256 | 37.3013 | -121.8277 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0108109 | UG | Sus | 45937816 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868360 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 1863 | 20230823 | 1401 | 20230824 | 1409 | 2200653 | 1448 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4 | 2810 | 36.95 | -121.52 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0108320 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1868416 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 43295 | 20230823 | 1518 | 20230825 | 555 | 2200365 | 2198 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 166 | 40298 | 37.3516 | -121.9009 | No | Partly Cloudy;Above 90 | Transformer (UG) | Failed/Faulted | 23-0108298 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868396 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | OCB | XR208 | 20230823 | 1949 | 20230824 | 729 | 2200658 | 700 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4122 | 428839 | 37.4386 | -121.873 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0108324 | OH | Sus | 45938149 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1868417 | 0 | EPSS Ckt | Y | 2023 | 50- GRD & B n
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315682829992 | 20230823 | 2316 | 20230825 | 136 | 2200763 | 1580 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 31172 | 37.3148 | -121.9852 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0108541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868658 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | OCB | 2101/2 | 20230824 | 256 | 20230825 | 16 | 2200812 | 1280 | Distribution Circuit | Equipment Failure/Involved | Underground | 4030 | 420815 | 37.3036 | -121.8398 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0108401 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868488 | 0 | Non-EPSS | N | 2023 | OC GRD
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315780329804 | 20230824 | 825 | 20230825 | 537 | 2200957 | 1272 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 10176 | 37.3096 | -121.9517 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0108774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868758 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OTHER | J6835 TWD 63784 | 20230824 | 1041 | 20230824 | 1531 | 2201223 | 290 | Distribution Circuit | Equipment Failure/Involved | Underground | 155 | 44950 | 37.3061 | -121.8633 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0108277 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868673 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | RECLOSER | 49970 | 20230824 | 1419 | 20230824 | 1426 | 2201417 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1755 | 12285 | 37.2698 | -121.8677 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0108710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868732 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | RECLOSER | XR340 | 20230824 | 1448 | 20230824 | 1543 | 2201466 | 55 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1781 | 92280 | 37.4489 | -121.9108 | No | Clear;32-90 F |  |  | 23-0108728 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868739 | 0 | EPSS Ckt | N | 2023 | SGF RLY
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315894934117 | 20230824 | 2111 | 20230824 | 2250 | 2201704 | 99 | Transformer only | Vegetation | Tree - grew into line | 8 | 792 | 37.4286 | -121.9154 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0108829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1868795 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1109 | 82251109 | OCB | 1109/2 | 20230825 | 146 | 20230828 | 1104 | 2201744 | 4812 | Distribution Circuit | Equipment Failure/Involved | Underground | 470 | 71571 | 37.3282 | -121.9025 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0108885 | UG | Sus | 31664781 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1868849 | 0 | Non-EPSS | N | 2023 | PH INST- PH TIME & GRD
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | TRANSFORMER | C1813 | 20230825 | 858 | 20230825 | 931 | 2202007 | 33 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 561 | 37.262 | -121.8262 | No | Partly Cloudy;32-90 F |  |  | 23-0109020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1869000 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316723223045 | 20230825 | 1212 | 20230825 | 1352 | 2202222 | 100 | Transformer only | 3rd Party | Vehicle | 1 | 100 | 37.1275 | -121.625 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0109219 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869069 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | TRANSFORMER | 315888331046 | 20230825 | 1603 | 20230825 | 1630 | 2202374 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 108 | 37.3441 | -121.9155 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0109279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869086 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | TRANSFORMER | C3243 | 20230825 | 1830 | 20230825 | 1853 | 2202588 | 23 | Transformer only | Equipment Failure/Involved | Underground | 39 | 897 | 37.2368 | -121.7682 | No | Clear;32-90 F | Secondary | Broken | 23-0109331 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869135 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 11859 | 20230826 | 710 | 20230827 | 520 | 2202656 | 1330 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 63324 | 37.306 | -121.7857 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0109378 | UG | Sus | 45941670 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869212 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | SWITCH | 42798 | 20230826 | 1252 | 20230826 | 2250 | 2202584 | 598 | Distribution Circuit | Equipment Failure/Involved | Underground | 56 | 19496 | 37.3412 | -121.8944 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0109333 | UG | Sus | 35484164 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869138 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | TRANSFORMER | C3542 | 20230826 | 1456 | 20230826 | 1632 | 2202918 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 40 | 3840 | 37.3853 | -121.8755 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0109430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869244 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 18189 | 20230826 | 1529 | 20230826 | 1632 | 2202929 | 63 | Distribution Circuit | 3rd Party | Metallic Balloon | 106 | 6678 | 37.3084 | -121.9716 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869247 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 5973 | 20230826 | 1859 | 20230826 | 2052 | 2202992 | 113 | Distribution Circuit | Animal | Squirrel | 6 | 678 | 37.2643 | -121.9206 | No | Clear;32-90 F | Fuse | Normal | 23-0109458 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869265 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR176 | 20230827 | 536 | 20230828 | 441 | 2203138 | 1385 | Distribution Circuit | 3rd Party | Vehicle | 1100 | 172033 | 37.0929 | -121.6472 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869301 | 0 | EPSS Ckt | Y | 2023 | C GRD
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | RECLOSER | XR248 | 20230827 | 1505 | 20230827 | 1511 | 2203371 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 417 | 2502 | 37.2105 | -121.8595 | No | Clear;32-90 F |  |  | 23-0109534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869340 | 0 | EPSS Ckt | N | 2023 | B & G
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 11859 | 20230827 | 1831 | 20230828 | 125 | 2203435 | 414 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 49590 | 37.306 | -121.7857 | No | Clear;32-90 F | Elbow | Broken | 23-0109589 | UG | Sus | 45942011 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869380 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 26247 | 20230827 | 1945 | 20230828 | 1207 | 2203458 | 982 | Distribution Circuit | Equipment Failure/Involved | Underground | 90 | 44752 | 37.3333 | -121.7797 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0109565 | UG | Sus | 31665565 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869358 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 58299 | 20230828 | 450 | 20230828 | 1257 | 2203795 | 487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 25324 | 37.053 | -121.6051 | No | Clear;32-90 F | Jumper | Broken | 23-0109801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869611 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28263 | 20230828 | 1024 | 20230828 | 1625 | 2203961 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3971 | 37.0951 | -121.6721 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0109731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869557 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315905229815 | 20230828 | 1246 | 20230828 | 1306 | 2203803 | 20 | Transformer only | Animal | Squirrel | 12 | 240 | 37.3101 | -121.9091 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0109820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869624 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | SWITCH | 8765 | 20230828 | 1857 | 20230828 | 1927 | 2204435 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 306 | 9180 | 37.3158 | -121.9822 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0109920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1869658 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17555 | 20230829 | 809 | 20230829 | 915 | 2204656 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 2772 | 37.383 | -121.8103 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0110095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1869836 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316009826430 | 20230829 | 1539 | 20230829 | 2319 | 2204924 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2760 | 37.2177 | -121.8712 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0110414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869982 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315698529614 | 20230829 | 1613 | 20230829 | 1827 | 2205264 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2010 | 37.3044 | -121.9797 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0110456 | OH | Sus | 35485378 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1869993 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 28455 | 20230829 | 2135 | 20230830 | 132 | 2205452 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 6399 | 37.428 | -121.9121 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110451 | OH | Sus | 45945118 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870005 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317024117178 | 20230830 | 618 | 20230830 | 1515 | 2205579 | 537 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 537 | 36.9673 | -121.5196 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0110711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870211 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20230830 | 854 | 20230830 | 1055 | 2205737 | 121 | Distribution Circuit | Animal | Squirrel | 213 | 25773 | 37.1869 | -121.8177 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110626 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870144 | 0 | EPSS Ckt | Y | 2023 | A PHASE TARGET
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR246 | 20230830 | 1053 | 20230830 | 1320 | 2205923 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4190 | 380364 | 37.1236 | -121.641 | No | Clear;32-90 F |  |  | 23-0110716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870213 | 0 | EPSS Ckt | Y | 2023 | C & GRD TARGET
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316969719672 | 20230830 | 1209 | 20230830 | 1354 | 2206004 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 420 | 37.0356 | -121.5387 | No | Clear;Above 90 | Secondary | Together | 23-0110868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870259 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 18343 | 20230830 | 1843 | 20230830 | 1958 | 2206383 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1875 | 37.3002 | -121.9193 | No | Clear;32-90 F |  |  | 23-0111001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1870301 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | OTHER | T20905 TWD T20906 | 20230830 | 2154 | 20230831 | 241 | 2206504 | 287 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 2870 | 37.2857 | -121.7377 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0111036 | UG | Sus | 35485798 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1870329 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 8117 | 20230831 | 710 | 20230831 | 956 | 2206610 | 166 | Distribution Circuit | Animal | Bird found | 12 | 1992 | 37.1897 | -121.7117 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0111105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870412 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315879829112 | 20230831 | 1137 | 20230831 | 1533 | 2207012 | 236 | Transformer only | Vegetation | Tree - fell into line | 7 | 1652 | 37.2909 | -121.9175 | No | Clear;32-90 F | Secondary | Normal | 23-0111250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870554 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 40119 | 20230831 | 1607 | 20230831 | 1858 | 2207288 | 171 | Distribution Circuit | 3rd Party | Customer Equipment | 8 | 1326 | 37.301 | -121.8576 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 23-0111523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Three Phase Fault | 0 | No | No | No | 1870620 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28767 | 20230831 | 1615 | 20230901 | 213 | 2207173 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 17940 | 37.279 | -121.8186 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111471 | OH | Sus | 35485918 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870613 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 3381 | 20230831 | 1646 | 20230831 | 2111 | 2207106 | 265 | Distribution Circuit | Vegetation | Tree - grew into line | 308 | 81620 | 37.2982 | -121.9541 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0111468 | OH | Sus | 45947335 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870612 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 70407 | 20230831 | 2326 | 20230901 | 218 | 2207457 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 24596 | 37.156 | -121.6116 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0111546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1870661 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | SWITCH | X1922 | 20230901 | 1101 | 20230901 | 1328 | 2207786 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 431 | 13679 | 37.3379 | -121.8447 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0111659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1870785 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | SWITCH | 28546 | 20230902 | 1530 | 20230902 | 1603 | 2208772 | 33 | Distribution Circuit | Company Initiated | Return Circuit Normal | 31 | 603 | 37.3561 | -121.9053 | No | Overcast;32-90 F | Switch (UG) | Normal | 23-0106746 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1870963 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315901434264 | 20230902 | 2309 | 20230903 | 1415 | 2208939 | 906 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 18 | 16308 | 37.4326 | -121.9129 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0112195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871006 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 28129 | 20230903 | 733 | 20230903 | 917 | 2208998 | 104 | Distribution Circuit | Animal | Squirrel | 33 | 3432 | 37.2904 | -121.8177 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0112217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871028 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 317163031705 | 20230903 | 1405 | 20230903 | 2250 | 2209114 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1050 | 37.3689 | -121.4768 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0112249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871054 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4239 | 20230903 | 2005 | 20230903 | 2240 | 2209205 | 155 | Distribution Circuit | Animal | Bird found | 2 | 310 | 36.9629 | -121.4932 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0112275 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871078 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316154631276 | 20230904 | 2035 | 20230905 | 616 | 2209582 | 565 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 13992 | 37.3514 | -121.8239 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0112408 | OH | Sus | 35486353 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871167 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 3859 | 20230905 | 347 | 20230905 | 804 | 2209645 | 257 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 32108 | 37.288 | -121.8186 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0112423 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871180 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 17725 | 20230905 | 1446 | 20230906 | 127 | 2210232 | 641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 9615 | 37.2229 | -121.8759 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0112766 | OH | Sus | 31667685 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871384 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20230905 | 2257 | 20230906 | 1055 | 2210492 | 718 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 41644 | 37.053 | -121.5276 | No | Clear;32-90 F |  |  | 23-0112854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871421 | 0 | EPSS Ckt | Y | 2023 | B/C
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317074218817 | 20230906 | 1941 | 20230907 | 245 | 2211154 | 424 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 848 | 37.0127 | -121.5029 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871698 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 14989 | 20230907 | 1016 | 20230907 | 1940 | 2211708 | 9 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 17 | 289 | 37.2363 | -121.922 | No | Clear;32-90 F | Fuse | Normal | 23-0113602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1871894 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 247498 | 20230908 | 1305 | 20230908 | 1428 | 2212846 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 11987 | 37.354 | -121.7871 | No | Clear;32-90 F | Jumper | Burned Open | 23-0114203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872194 | 1 | EPSS Ckt | Y | 2023 | NONE
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 28079 | 20230908 | 1932 | 20230909 | 4 | 2212985 | 272 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 7344 | 37.3064 | -121.7817 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0114333 | OH | Sus | 45967431 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872241 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 25269 | 20230908 | 2057 | 20230910 | 123 | 2213239 | 1706 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 49474 | 37.3267 | -121.8544 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0114359 | UG | Sus | 35487528 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872260 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75155 | 20230909 | 336 | 20230909 | 1653 | 2213327 | 797 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 19128 | 37.2978 | -121.9698 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0114532 | OH | Sus | 45968222 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872465 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317032418578 | 20230909 | 1545 | 20230910 | 1250 | 2213905 | 1265 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1265 | 37.0058 | -121.5173 | Yes | Clear;32-90 F | Transformer | Deteriorated | 23-0114503 | OH | Sus | 31668013 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872441 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | JUMPER | FLYING BELLS 1/2 SPAN N/OF CGC 316019430510 | 20230909 | 2132 | 20230910 | 141 | 2214328 | 249 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1245 | 37.3299 | -121.8703 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0114566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1872520 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20230910 | 139 | 20230910 | 1605 | 2214429 | 866 | Distribution Circuit | 3rd Party | Vehicle | 3437 | 783274 | 37.1066 | -121.6618 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0114602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1872539 | 0 | EPSS Ckt | Y | 2023 | A PH OC & GRD
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316979618498 | 20230910 | 1321 | 20230911 | 25 | 2214741 | 664 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1992 | 37.0034 | -121.5354 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0114688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872649 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 19141 | 20230910 | 1746 | 20230911 | 2230 | 2214879 | 1724 | Distribution Circuit | Equipment Failure/Involved | Underground | 30 | 51720 | 37.2418 | -121.8396 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0114731 | UG | Sus | 45968488 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1872698 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 403753 | 20230911 | 1828 | 20230911 | 2104 | 2215955 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2496 | 37.3143 | -121.9804 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0115215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873091 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42699 | 20230911 | 2107 | 20230912 | 329 | 2216010 | 382 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 30178 | 37.2741 | -121.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873103 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 41351 | 20230911 | 2203 | 20230912 | 152 | 2216024 | 229 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 3731 | 37.3027 | -121.7919 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0115163 | UG | Sus | 35488050 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873108 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315714929610 | 20230912 | 944 | 20230912 | 2120 | 2216470 | 696 | Transformer only | Unknown Cause | Patrol - found nothing | 55 | 38280 | 37.3043 | -121.974 | No | Partly Cloudy;32-90 F |  |  | 23-0115426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873331 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | SWITCH | 44014 | 20230912 | 1329 | 20230912 | 1403 | 2216749 | 34 | Distribution Circuit | Equipment Failure/Involved | Underground | 121 | 3190 | 37.3032 | -121.7798 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0109589 | UG | Sus | 45942011 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873391 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315887734185 | 20230912 | 1405 | 20230912 | 1538 | 2216757 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 837 | 37.4304 | -121.9176 | No | Clear;32-90 F | Secondary | Broken | 23-0115570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1873394 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 72127 | 20230912 | 1541 | 20230913 | 312 | 2216848 | 691 | Distribution Circuit | Vegetation | Tree - grew into line | 31 | 21421 | 37.3196 | -121.9233 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0115724 | OH | Sus | 45977250 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873432 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 14795 | 20230912 | 1723 | 20230913 | 302 | 2216872 | 579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 15633 | 37.288 | -121.8923 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0115700 | OH | Sus | 31668475 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873419 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | FUSE | 6831 | 20230912 | 1746 | 20230912 | 1851 | 2216945 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 5260 | 37.3744 | -121.8944 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0115720 | OH | Sus | 31668476 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873428 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2103 | 83892103 | FUSE | 12615 | 20230912 | 1858 | 20230912 | 2121 | 2217025 | 143 | Distribution Circuit | Animal | Squirrel | 9 | 1287 | 37.4066 | -121.9097 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0115742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873444 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 11405 | 20230912 | 2022 | 20230913 | 1528 | 2217087 | 1146 | Distribution Circuit | Equipment Failure/Involved | Underground | 172 | 61252 | 37.3214 | -121.8427 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0115737 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873439 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | JUMPER | FLYING BELLS 2 SPAN EAST OF CGC 315882428598 | 20230912 | 2035 | 20230913 | 220 | 2217089 | 345 | Distribution Circuit | Vegetation | Tree - grew into line | 248 | 33236 | 37.2772 | -121.9157 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0115732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873437 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2102 | 83892102 | OTHER | J5158 TWD T20893 | 20230913 | 111 | 20230913 | 200 | 2217252 | 49 | Distribution Circuit | 3rd Party | Vandalism | 1 | 49 | 37.4035 | -121.8948 | No | Clear;32-90 F | Secondary | Broken | 23-0115726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873510 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | RECLOSER | 819378 | 20230913 | 1321 | 20230913 | 1427 | 2217898 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2651 | 170556 | 37.4308 | -121.8637 | No | Clear;32-90 F |  |  | 23-0116128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873747 | 0 | EPSS Ckt | N | 2023 | C PHASE- GRD TIME
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | JUMPER | 6831 HIGH SIDE JUMPERS | 20230913 | 1845 | 20230913 | 1930 | 2218250 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 360 | 37.3745 | -121.8944 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0115720 | OH | Sus | 31668476 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873790 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28007 | 20230913 | 2144 | 20230914 | 215 | 2218306 | 271 | Distribution Circuit | Vegetation | Tree - grew into line | 102 | 27642 | 37.2615 | -121.8054 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0116329 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1873801 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 9653 | 20230914 | 730 | 20230914 | 1144 | 2218465 | 254 | Distribution Circuit | Equipment Failure/Involved | Underground | 230 | 48426 | 37.3854 | -121.8534 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0116495 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873982 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 75531 | 20230914 | 1148 | 20230915 | 132 | 2218850 | 824 | Distribution Circuit | Animal | Bird found | 33 | 6702 | 37.1229 | -121.6466 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0116721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874073 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | SWITCH | 27798 | 20230915 | 205 | 20230915 | 231 | 2219264 | 26 | Distribution Circuit | Equipment Failure/Involved | Underground | 41 | 1066 | 37.3852 | -121.8594 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0116495 | UG | Sus | 31668952 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874157 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10345 | 20230915 | 850 | 20230915 | 915 | 2219385 | 25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 150 | 37.101 | -121.621 | No | Overcast-Fog;32-90 F |  |  | 23-0117057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874299 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316879819192 | 20230915 | 1317 | 20230915 | 1905 | 2219929 | 348 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1044 | 37.0221 | -121.5696 | No | Clear;32-90 F | Secondary | Broken | 23-0117249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874389 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | FUSE | 26151 | 20230915 | 1924 | 20230916 | 143 | 2220110 | 379 | Distribution Circuit | Vegetation | Tree - grew into line | 211 | 79969 | 37.3433 | -121.89 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874422 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | SWITCH | 12463 | 20230915 | 2131 | 20230916 | 52 | 2220160 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 212 | 37122 | 37.4396 | -121.8236 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0117369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874427 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | RECLOSER | XR326 | 20230915 | 2228 | 20230917 | 257 | 2220189 | 1688 | Distribution Circuit | 3rd Party | Vehicle | 1801 | 644469 | 37.1073 | -121.6349 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0117381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874440 | 0 | EPSS Ckt | N | 2023 | A & C TARGET
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13949 | 20230915 | 2243 | 20230916 | 352 | 2220222 | 309 | Distribution Circuit | 3rd Party | Metallic Balloon | 293 | 90537 | 37.3192 | -121.8566 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0117389 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874449 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 3859 | 20230916 | 1146 | 20230916 | 1402 | 2220612 | 127 | Distribution Circuit | Equipment Failure/Involved | Underground | 130 | 6835 | 37.288 | -121.8186 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0112423 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1874535 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR152 | 20230916 | 1804 | 20230917 | 1013 | 2220749 | 969 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 333 | 201118 | 37.1047 | -121.6625 | No | Clear;32-90 F |  |  | 23-0117491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874565 | 0 | EPSS Ckt | Y | 2023 | GRD///50
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 17599 | 20230917 | 259 | 20230917 | 600 | 2220860 | 181 | Distribution Circuit | 3rd Party | Vehicle | 59 | 10679 | 37.2046 | -121.8417 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0117516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874597 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 8985 | 20230918 | 147 | 20230919 | 116 | 2221156 | 1409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 145833 | 37.3395 | -121.8221 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0117596 | OH | Sus | 31669342 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874679 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 13559 | 20230918 | 401 | 20230918 | 444 | 2221167 | 43 | Distribution Circuit | 3rd Party | Vehicle | 11 | 473 | 37.2973 | -121.8484 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0117599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1874681 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | T12724 | 20230918 | 1200 | 20230918 | 1230 | 2221653 | 30 | Transformer only | Equipment Failure/Involved | Underground | 1 | 30 | 37.1281 | -121.6283 | No | Clear;32-90 F | Secondary | Normal | 23-0117806 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874905 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 75319 | 20230918 | 1530 | 20230918 | 2201 | 2222035 | 391 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 39 | 14717 | 37.2912 | -121.8544 | No | Clear;32-90 F |  |  | 23-0118006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874983 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-2119 | 83802119 | OCB | 2119/2 | 20230918 | 1716 | 20230919 | 2159 | 2221899 | 1393 | Distribution Circuit | 3rd Party | Vandalism | 62 | 20840 | 37.3828 | -121.9262 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0117978 | UG | Sus | 35489990 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874958 | 0 | Non-EPSS | N | 2023 | GRD
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | JUMPER | FLYING BELLS AT 500 E WILLIAMS ST | 20230918 | 2100 | 20230919 | 630 | 2222018 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 27930 | 37.335 | -121.8713 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1874976 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | JUMPER | OPEN JUMPERS @ 1166 BERKSHIRE | 20230919 | 928 | 20230919 | 1206 | 2222268 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 3792 | 37.2801 | -121.8834 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0118098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875112 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 36046 | 20230919 | 1057 | 20230919 | 1146 | 2222404 | 49 | Distribution Circuit | 3rd Party | Other | 21 | 1029 | 37.3724 | -121.8461 | No | Clear;32-90 F | Secondary | Together | 23-0118170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875205 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20230920 | 850 | 20230920 | 1038 | 2223128 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4181 | 218779 | 37.4156 | -121.8881 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0118619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1875461 | 0 | EPSS Ckt | N | 2023 | TIME OC
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 15019 | 20230920 | 1115 | 20230920 | 1121 | 2223411 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 14 | 84 | 37.2998 | -121.9511 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0118812 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1875608 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315971728638 | 20230920 | 2255 | 20230921 | 2140 | 2223741 | 1365 | Distribution Circuit | Vegetation | Tree - grew into line | 23 | 15393 | 37.2783 | -121.8857 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0118993 | OH | Sus | 45985657 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875673 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 354865 | 20230921 | 1427 | 20230921 | 1529 | 2224150 | 62 | Distribution Circuit | 3rd Party | Other | 48 | 2976 | 37.2706 | -121.8819 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1875808 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 26259 | 20230921 | 1743 | 20230921 | 2049 | 2224249 | 186 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 29468 | 37.2715 | -121.831 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0119458 | UG | Sus | 45986851 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1875823 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 25207 | 20230923 | 344 | 20230923 | 1326 | 2225171 | 582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 20370 | 37.2781 | -121.8942 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0119989 | OH | Sus | 45988045 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876148 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | FUSE | 14973 | 20230923 | 1743 | 20230923 | 1848 | 2225570 | 65 | Distribution Circuit | 3rd Party | Metallic Balloon | 24 | 1560 | 37.2467 | -121.913 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0120091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876244 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315690929782 | 20230924 | 2133 | 20230925 | 12 | 2225943 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1431 | 37.309 | -121.9824 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0120158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1876325 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 40220 | 20230925 | 933 | 20230925 | 1042 | 2226394 | 69 | Distribution Circuit | Animal | Bird found | 135 | 6794 | 37.3244 | -121.8065 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0120324 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876565 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20230925 | 1012 | 20230925 | 1211 | 2226487 | 119 | Distribution Circuit | Animal | Bird found | 387 | 46053 | 37.1503 | -121.6194 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0120340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876573 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE OC
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | INTERRUPTER | 43476 | 20230926 | 1140 | 20230927 | 117 | 2227610 | 817 | Distribution Circuit | Equipment Failure/Involved | Underground | 129 | 32725 | 37.2952 | -121.8412 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0120963 | UG | Sus | 45991446 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876969 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | OTHER | J5233 TWD T21706 | 20230926 | 1955 | 20230927 | 208 | 2228028 | 373 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 16785 | 37.2746 | -121.7541 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0121099 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877050 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316046630884 | 20230926 | 2228 | 20230927 | 421 | 2228091 | 353 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 353 | 37.3402 | -121.8609 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0121212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877075 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | OCB | 2105/2 | 20230927 | 1036 | 20230927 | 1314 | 2228518 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6153 | 972174 | 37.2448 | -121.7954 | No | Clear;32-90 F | Recloser | Failed/Faulted | 23-0121454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1877300 | 0 | EPSS Ckt | Y | 2023 | A- B- C
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 26559 | 20230927 | 1048 | 20230928 | 113 | 2228531 | 865 | Distribution Circuit | Equipment Failure/Involved | Underground | 133 | 35076 | 37.14 | -121.6322 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0121518 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877318 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 11829 | 20230927 | 1722 | 20230927 | 1929 | 2228863 | 127 | Distribution Circuit | Vegetation | Tree - grew into line | 122 | 15494 | 37.2944 | -121.8867 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877366 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 4817 | 20230929 | 949 | 20230929 | 1409 | 2230252 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 8840 | 37.1244 | -121.661 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0122462 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1877894 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | OCB | 2105/2 | 20230929 | 1055 | 20230929 | 1306 | 2230335 | 131 | Distribution Circuit | Animal | Squirrel | 6153 | 499544 | 37.2448 | -121.7954 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0122536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877921 | 0 | EPSS Ckt | Y | 2023 | C- B-PH OC INST & GRD TRGTS
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317162017760 | 20230929 | 1114 | 20230929 | 1221 | 2230355 | 67 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 67 | 36.9836 | -121.4726 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0122606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1877945 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 644559 | 20230930 | 658 | 20230930 | 2101 | 2231339 | 843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 41307 | 37.3417 | -121.8683 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0122887 | OH | Sus | 31670897 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1878146 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315865129762 | 20230930 | 925 | 20230930 | 1138 | 2231418 | 133 | Transformer only | Vegetation | Tree - branch fell on line | 29 | 3857 | 37.3086 | -121.9227 | No | Partly Cloudy;32-90 F | Conductor- Overhead | On Ground | 23-0122937 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1878184 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR246 | 20230930 | 1301 | 20230930 | 1827 | 2231580 | 326 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4220 | 150665 | 37.1236 | -121.641 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0122956 | OH | Sus | 31670912 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1878202 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 40914 | 20230930 | 1545 | 20230930 | 2009 | 2231757 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 12936 | 37.2009 | -121.8376 | No | Partly Cloudy;32-90 F |  |  | 23-0123038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1878264 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20231002 | 655 | 20231002 | 1135 | 2232417 | 280 | Distribution Circuit | Animal | Bird found | 401 | 65570 | 37.1263 | -121.7284 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0123190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1878415 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 62626 | 20231002 | 1407 | 20231003 | 203 | 2232999 | 716 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 20993 | 37.1294 | -121.6388 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0123511 | UG | Sus | 45997643 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878647 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | SWITCH | 33630 | 20231002 | 1702 | 20231003 | 625 | 2233147 | 803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 6424 | 37.4487 | -121.888 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0123331 | OH | Sus | 35492735 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878656 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 42125 | 20231002 | 1841 | 20231003 | 1337 | 2233217 | 1136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 16444 | 37.3524 | -121.8604 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0123403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878673 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR208 | 20231002 | 1900 | 20231002 | 2011 | 2233230 | 71 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 959 | 57073 | 37.4386 | -121.873 | No | Clear;32-90 F | Relay | Normal | 23-0123544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1878670 | 0 | EPSS Ckt | N | 2023 | SGF
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | SWITCH | 13516 | 20231003 | 107 | 20231003 | 130 | 2233320 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 163 | 3664 | 37.271 | -121.8345 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0119458 | UG | Sus | 45986851 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1878727 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41715 | 20231003 | 111 | 20231003 | 424 | 2233318 | 193 | Distribution Circuit | Vegetation | Tree - grew into line | 268 | 51724 | 37.3107 | -121.9181 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0123540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878726 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 821285 | 20231003 | 1031 | 20231003 | 2023 | 2233667 | 592 | Distribution Circuit | Vegetation | Tree - grew into line | 72 | 42624 | 37.3292 | -121.9182 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0123849 | OH | Sus | 45998135 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878956 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6917 | 20231003 | 1229 | 20231004 | 325 | 2233696 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 146048 | 37.2668 | -121.8834 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0123811 | OH | Sus | 31671281 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1878939 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 2209 | 20231003 | 2255 | 20231004 | 540 | 2234139 | 405 | Distribution Circuit | Vegetation | Tree - grew into line | 34 | 13770 | 37.2793 | -121.8915 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0124116 | OH | Sus | 45998947 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879067 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 316000629613 | 20231004 | 1245 | 20231004 | 1356 | 2234695 | 71 | Transformer only | Animal | Squirrel | 3 | 213 | 37.3051 | -121.876 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0124446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879351 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR268 | 20231004 | 1551 | 20231004 | 1842 | 2234858 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 11286 | 37.0329 | -121.6831 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0124567 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879369 | 0 | EPSS Ckt | Y | 2023 | C PHASE
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | JUMPER | OJ'S @ IFO 7259 ALEXANDER ST | 20231005 | 959 | 20231005 | 1231 | 2235554 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1064 | 37.0056 | -121.5655 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0124801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879599 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | FUSE | 6740 | 20231005 | 1334 | 20231006 | 643 | 2235787 | 1029 | Distribution Circuit | Equipment Failure/Involved | Underground | 266 | 72646 | 37.3824 | -121.8653 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0125025 | UG | Sus | 46001502 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879696 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316163130031 | 20231005 | 1553 | 20231005 | 1649 | 2235912 | 56 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 18 | 1008 | 37.3172 | -121.8204 | No | Clear;Above 90 | Service conductor | Broken | 23-0125079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879709 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | C342 | 20231005 | 2158 | 20231005 | 2252 | 2236106 | 54 | Transformer only | Equipment Failure/Involved | Underground | 20 | 1080 | 37.3226 | -121.7929 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0125116 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879738 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20231005 | 2228 | 20231005 | 2328 | 2236124 | 60 | Distribution Circuit | 3rd Party | Vehicle | 400 | 24000 | 37.1446 | -121.6698 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0125136 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879757 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE I OC
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 71719 | 20231006 | 58 | 20231006 | 104 | 2236200 | 6 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 3 | 18 | 37.1547 | -121.6738 | No | Clear;32-90 F | Other | Normal | 23-0125148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879776 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 11911 | 20231006 | 755 | 20231006 | 911 | 2236290 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 239 | 18164 | 37.3407 | -121.913 | No | Clear;32-90 F |  |  | 23-0125224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879875 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 599 | 20231006 | 1052 | 20231006 | 1642 | 2236572 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 223 | 78050 | 37.1667 | -121.7069 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0125196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1879963 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | RECLOSER | XR022 | 20231006 | 1105 | 20231006 | 1859 | 2236595 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2480 | 708128 | 37.3087 | -121.9591 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0125381 | OH | Sus | 31671753 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1879968 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20231006 | 1152 | 20231006 | 1629 | 2236650 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 846 | 170518 | 37.0163 | -121.5446 | No | Clear;32-90 F |  |  | 23-0125427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1879978 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 19775 | 20231006 | 1719 | 20231006 | 1914 | 2236973 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 9660 | 37.2597 | -121.8894 | No | Clear;32-90 F |  |  | 23-0125627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880074 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 35272 | 20231006 | 1833 | 20231009 | 449 | 2237007 | 2725 | Distribution Circuit | Equipment Failure/Involved | Underground | 4257 | 484805 | 37.382 | -121.8559 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 23-0125633 | UG | Sus | 31671997 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880080 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | SWITCH | 9575 | 20231006 | 2230 | 20231007 | 108 | 2237226 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1266 | 200028 | 37.2949 | -121.944 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0125553 | OH | Sus | 31671491 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880103 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 25011 | 20231007 | 500 | 20231008 | 440 | 2237301 | 1420 | Distribution Circuit | Equipment Failure/Involved | Underground | 86 | 73576 | 37.2236 | -121.8652 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0125672 | UG | Sus | 46002912 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880122 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 26857 | 20231007 | 713 | 20231007 | 1113 | 2237318 | 240 | Distribution Circuit | Animal | Squirrel | 80 | 19200 | 37.3366 | -121.9172 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0125719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880207 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | XR250 | 20231007 | 719 | 20231007 | 857 | 2237340 | 98 | Distribution Circuit | Animal | Squirrel | 3159 | 309582 | 37.2022 | -121.833 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0125676 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880129 | 0 | EPSS Ckt | Y | 2023 | A PHASE OC & GRD
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 1891 | 20231007 | 731 | 20231007 | 1141 | 2237375 | 250 | Distribution Circuit | Animal | Squirrel | 12 | 3000 | 37.2202 | -121.843 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0125724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880210 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316569920592 | 20231007 | 806 | 20231008 | 1555 | 2237398 | 1909 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3818 | 37.0597 | -121.6673 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880220 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 1489 | 20231007 | 812 | 20231007 | 1055 | 2237402 | 163 | Distribution Circuit | Animal | Squirrel | 18 | 2934 | 37.2595 | -121.8842 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0125721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880208 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 1431 | 20231007 | 1123 | 20231007 | 1552 | 2237636 | 269 | Distribution Circuit | Vegetation | Tree - grew into line | 520 | 103690 | 37.2543 | -121.8821 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0125659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880213 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | JUMPER | OJ IRO 4897 JARVIS AVE | 20231007 | 1757 | 20231008 | 1037 | 2237935 | 1000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 153926 | 37.2555 | -121.8882 | No | Clear;32-90 F | Jumper | Burned Open | 23-0125790 | OH | Sus | 46003188 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1880258 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | RECLOSER | XR360 | 20231007 | 1908 | 20231008 | 1317 | 2237956 | 1089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 62696 | 37.3768 | -121.8983 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0125792 | OH | Sus | 31671901 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1880260 | 0 | Non-EPSS | N | 2023 | B- C PHASE OC
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 3085 | 20231007 | 1917 | 20231008 | 2235 | 2237966 | 1638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 16380 | 37.1626 | -121.6837 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0125793 | OH | Sus | 31671904 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880261 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315665929274 | 20231008 | 214 | 20231008 | 1409 | 2238090 | 715 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6435 | 37.295 | -121.9909 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125831 | OH | Sus | 35494821 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880290 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | T12415 | 20231008 | 853 | 20231008 | 2105 | 2238172 | 732 | Distribution Circuit | Equipment Failure/Involved | Underground | 143 | 25154 | 37.3401 | -121.8189 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0125856 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880323 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | SWITCH | 70531 | 20231008 | 1400 | 20231008 | 1652 | 2238287 | 172 | Distribution Circuit | Vegetation | Tree - grew into line | 85 | 14620 | 37.3013 | -121.9057 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0125741 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880339 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 40616 | 20231009 | 318 | 20231010 | 448 | 2238503 | 1530 | Distribution Circuit | Equipment Failure/Involved | Underground | 231 | 81595 | 37.2602 | -121.8633 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0125908 | UG | Sus | 31672024 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880397 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 11499 | 20231009 | 320 | 20231009 | 2010 | 2238504 | 1010 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 3924 | 37.2738 | -121.8696 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0126246 | UG | Sus | 31671948 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880700 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 40381 | 20231009 | 558 | 20231009 | 647 | 2238546 | 49 | Distribution Circuit | Animal | Squirrel | 1 | 49 | 37.1616 | -121.6846 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0125914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1880409 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20231009 | 1331 | 20231009 | 1539 | 2239095 | 128 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 506 | 47618 | 37.3558 | -121.8299 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0126175 | OH | Sus | 46004142 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880672 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315888829364 | 20231009 | 1419 | 20231009 | 1727 | 2239136 | 188 | Transformer only | Vegetation | Other ground vegetation | 3 | 564 | 37.2978 | -121.9146 | No | Overcast;32-90 F | Secondary | Contaminated | 23-0126158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1880666 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 28507 | 20231009 | 1904 | 20231009 | 2147 | 2239369 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 315 | 30761 | 37.3588 | -121.862 | No | Overcast;32-90 F |  |  | 23-0126279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880715 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 17627 | 20231010 | 315 | 20231010 | 401 | 2239481 | 46 | Distribution Circuit | 3rd Party | Vehicle | 232 | 10672 | 37.3584 | -121.8898 | No | Overcast;32-90 F | Pole-Wood | Normal | 23-0126321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1880752 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10677 | 20231010 | 1512 | 20231010 | 1725 | 2240213 | 133 | Distribution Circuit | 3rd Party | Vehicle | 18 | 2394 | 37.107 | -121.6067 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0126751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881029 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15541 | 20231010 | 1640 | 20231011 | 9 | 2240166 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 8980 | 37.3922 | -121.4894 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0126732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881022 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | OCB | 2108/2 | 20231010 | 1756 | 20231010 | 2052 | 2240230 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3696 | 37.403 | -121.9056 | No | Partly Cloudy;32-90 F |  |  | 23-0126760 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881034 | 0 | Non-EPSS | N | 2023 | 51N RLY TARGET
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | OTHER | T2178 TWD T2179 | 20231010 | 1943 | 20231010 | 2204 | 2240275 | 141 | Distribution Circuit | Equipment Failure/Involved | Underground | 33 | 4653 | 37.2845 | -121.7648 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0126608 | UG | Sus | 35495413 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881041 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | TRANSFORMER | 316107932682 | 20231010 | 2022 | 20231011 | 55 | 2240294 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5040 | 37.3899 | -121.8406 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 23-0126590 | OH | Sus | 35368061 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881047 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 28387 | 20231011 | 1303 | 20231011 | 2323 | 2240941 | 620 | Distribution Circuit | Animal | Squirrel | 1 | 620 | 37.377 | -121.8984 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0127195 | OH | Sus | 31672379 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881385 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 42707 | 20231012 | 1009 | 20231012 | 1259 | 2241674 | 170 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 6800 | 37.2758 | -121.9144 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0127417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881597 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20231012 | 1117 | 20231012 | 1228 | 2241818 | 71 | Distribution Circuit | Company Initiated | Personnel- company | 43 | 3053 | 37.053 | -121.5276 | No | Clear;32-90 F | Fuse | Normal | 23-0127509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1881643 | 0 | EPSS Ckt | Y | 2023 | B & C PH
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | SWITCH | 6016 | 20231013 | 237 | 20231013 | 651 | 2242138 | 246 | Distribution Circuit | Equipment Failure/Involved | Underground | 145 | 16390 | 37.2545 | -121.8417 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0127766 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881728 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 26395 | 20231013 | 802 | 20231013 | 1217 | 2242350 | 255 | Distribution Circuit | Animal | Other | 15 | 3825 | 37.2698 | -121.7975 | No | Clear;32-90 F | Fuse | Burned Open | 23-0128040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881964 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | T9242 | 20231013 | 839 | 20231013 | 2131 | 2242439 | 772 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 13896 | 37.2714 | -121.9051 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0127972 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881937 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | RECLOSER | XR258 | 20231013 | 901 | 20231013 | 919 | 2242492 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 690 | 10640 | 37.2803 | -121.7577 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0127898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881880 | 0 | EPSS Ckt | Y | 2023 | B GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20231013 | 1146 | 20231013 | 1206 | 2242670 | 20 | Distribution Circuit | Company Initiated | Contact with High Voltage- company | 401 | 7746 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128027 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1881957 | 0 | EPSS Ckt | Y | 2023 | A PH INST
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | OTHER | J5343 TWD T21672 | 20231013 | 1904 | 20231013 | 2058 | 2242997 | 114 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 3990 | 37.2805 | -121.7708 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0128128 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882014 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | RECLOSER | 819378 | 20231014 | 419 | 20231014 | 555 | 2243109 | 55 | Distribution Circuit | Equipment Failure/Involved | Underground | 2687 | 130238 | 37.4308 | -121.8637 | No | Clear;32-90 F | Elbow | Burned/flashed | 23-0128246 | UG | Sus | 46013805 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882058 | 0 | EPSS Ckt | N | 2023 | B PHASE & GRD
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 3921 | 20231014 | 723 | 20231014 | 1822 | 2243164 | 659 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2667 | 36.9504 | -121.5229 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0128281 | OH | Sus | 35498131 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882164 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315964028240 | 20231014 | 1033 | 20231014 | 2037 | 2243319 | 604 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 8456 | 37.2674 | -121.8881 | No | Clear;32-90 F | Secondary | Normal | 23-0128325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882190 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | RECLOSER | 93368 | 20231014 | 1306 | 20231014 | 1400 | 2243416 | 54 | Distribution Circuit | 3rd Party | Vehicle | 2127 | 114858 | 37.3466 | -121.8498 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0128312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882178 | 0 | Non-EPSS | N | 2023 | C PHASE & GRD
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 44606 | 20231015 | 300 | 20231017 | 303 | 2243624 | 2883 | Distribution Circuit | Equipment Failure/Involved | Underground | 239 | 355936 | 37.3062 | -121.8281 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0128398 | UG | Sus | 35499482 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882249 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | INTERRUPTER | 64850 | 20231015 | 633 | 20231015 | 1225 | 2243635 | 352 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 352 | 37.3379 | -121.9088 | No | Overcast;32-90 F | Customer Equipment | Malfunctioning | 23-0128413 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1882263 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 26183 | 20231015 | 1356 | 20231015 | 1558 | 2243767 | 122 | Distribution Circuit | Animal | Squirrel | 76 | 9272 | 37.0061 | -121.5825 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0128432 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882281 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | INTERRUPTER | 30886 | 20231016 | 138 | 20231017 | 231 | 2244039 | 1493 | Distribution Circuit | Equipment Failure/Involved | Underground | 237 | 81159 | 37.2412 | -121.8009 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0128497 | UG | Sus | 31672826 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882329 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR070 | 20231016 | 744 | 20231016 | 1024 | 2244122 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 24980 | 37.0428 | -121.6546 | No | Clear;32-90 F |  |  | 23-0128530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1882354 | 0 | EPSS Ckt | Y | 2023 | A & B PH
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 14771 | 20231016 | 1249 | 20231016 | 1413 | 2244526 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 3360 | 37.2759 | -121.8983 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0128707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882530 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316221831702 | 20231016 | 1338 | 20231016 | 1830 | 2244615 | 292 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 6 | 1752 | 37.3633 | -121.801 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0128751 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1882550 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 19407 | 20231016 | 1520 | 20231017 | 119 | 2244665 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 33286 | 37.3043 | -121.8961 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0128808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882566 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315879730009 | 20231016 | 1923 | 20231016 | 2128 | 2244847 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 1625 | 37.3154 | -121.9178 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0128893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882588 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 22641 | 20231017 | 1427 | 20231018 | 244 | 2245534 | 737 | Distribution Circuit | Animal | Squirrel | 16 | 11792 | 37.2552 | -121.9085 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129317 | OH | Sus | 46022195 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882927 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | RECLOSER | XR022 | 20231017 | 1839 | 20231018 | 1545 | 2245666 | 1121 | Distribution Circuit | Equipment Failure/Involved | Underground | 2480 | 389558 | 37.3087 | -121.9591 | No | Clear;32-90 F | Bushing | Failed/Faulted | 23-0129334 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1882931 | 0 | Non-EPSS | N | 2023 | B/GRD
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | SWITCH | 65370 | 20231017 | 2139 | 20231018 | 117 | 2245735 | 218 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 1946 | 37.2373 | -121.8326 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0129320 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1882941 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 49981 | 20231018 | 828 | 20231018 | 1130 | 2245907 | 182 | Distribution Circuit | Animal | Bird found | 3 | 546 | 37.3156 | -121.9046 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0129631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1883172 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 42193 | 20231018 | 906 | 20231018 | 1627 | 2245977 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 25578 | 37.2861 | -121.8966 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0129492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883078 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 3037 | 20231018 | 1037 | 20231018 | 1236 | 2246107 | 119 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 9 | 1071 | 37.1769 | -121.8205 | No | Clear;32-90 F | Fuse | Normal | 23-0129660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883182 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315936230206 | 20231018 | 2113 | 20231019 | 332 | 2246562 | 379 | Transformer only | Equipment Failure/Involved | Underground | 2 | 758 | 37.3212 | -121.8987 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0129897 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883249 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20231019 | 520 | 20231019 | 1426 | 2246599 | 546 | Distribution Circuit | 3rd Party | Vehicle | 846 | 125316 | 37.0163 | -121.5446 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0129948 | OH | Sus | 31673249 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1883286 | 0 | EPSS Ckt | Y | 2023 | A-B-C PHASE
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | INTERRUPTER | 32864 | 20231019 | 859 | 20231020 | 119 | 2246757 | 947 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 9048 | 37.3861 | -121.9159 | No | Clear;32-90 F |  |  | 23-0130118 | OH | Sus | 46026019 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883354 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20231019 | 1222 | 20231019 | 1411 | 2246905 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 771 | 83669 | 37.1334 | -121.6754 | No | Clear;Above 90 |  |  | 23-0130188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883377 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315925528537 | 20231019 | 1252 | 20231019 | 1510 | 2246949 | 138 | Transformer only | Vegetation | Tree - grew into line | 8 | 1104 | 37.2754 | -121.9015 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0130301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883414 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | JUMPER | OJ IFO 1185 BLEWETT | 20231019 | 1933 | 20231020 | 228 | 2247165 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 14525 | 37.3076 | -121.8991 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0130368 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883436 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | OCB | 1112/2 | 20231019 | 1953 | 20231019 | 2033 | 2247172 | 40 | Distribution Circuit | 3rd Party | Metallic Balloon | 1234 | 49360 | 37.2332 | -121.9012 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0130376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883440 | 0 | Non-EPSS | N | 2023 | PHASE TIME OC
SAN JOSE | SAN JOSE | SAN JOSE A-1113 | 82251113 | SWITCH | 10928 | 20231019 | 1955 | 20231020 | 408 | 2246826 | 493 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1972 | 37.3321 | -121.8932 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0130303 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883441 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 35202 | 20231019 | 2003 | 20231020 | 6 | 2247191 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 7290 | 37.3885 | -121.9183 | No | Clear;32-90 F |  |  | 23-0130418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1883470 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 1613 | 20231019 | 2214 | 20231020 | 1400 | 2247221 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1187 | 36.9592 | -121.5375 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 23-0130388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1883452 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 35202SW | 20231020 | 37 | 20231020 | 423 | 2247259 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 5831 | 37.3886 | -121.9183 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0130424 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883474 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 64188 | 20231020 | 454 | 20231021 | 1154 | 2247279 | 1218 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 48128 | 37.3952 | -121.916 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0130694 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883694 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | T16049 | 20231020 | 908 | 20231020 | 1506 | 2247460 | 358 | Transformer only | Company Initiated | Construction Activity/equip- company | 17 | 6086 | 37.3499 | -121.8938 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0130653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883683 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | RECLOSER | XR240 | 20231020 | 923 | 20231020 | 1210 | 2247503 | 126 | Distribution Circuit | Equipment Failure/Involved | Underground | 3201 | 365411 | 37.2512 | -121.8304 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0130532 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883631 | 0 | Non-EPSS | N | 2023 | B PH & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | JUMPER | SOURCE SIDE JUMPER TO 4539 OPEN | 20231021 | 856 | 20231021 | 1013 | 2248104 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 12859 | 37.1187 | -121.6464 | No | Partly Cloudy-Fog;32-90 F | Jumper | Burned Open | 23-0130883 | OH | Sus | 46028078 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1883844 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 30034 | 20231022 | 425 | 20231024 | 1145 | 2248704 | 3120 | Distribution Circuit | Equipment Failure/Involved | Underground | 1668 | 415084 | 37.2992 | -121.8232 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0130992 | UG | Sus | 46028266 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1883960 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | SWITCH | 65216SW | 20231022 | 924 | 20231022 | 1327 | 2248818 | 243 | Distribution Circuit | Animal | Bird found | 10 | 2430 | 37.3201 | -121.9734 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0131035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884004 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 17881 | 20231022 | 1231 | 20231023 | 2318 | 2248931 | 2087 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 20870 | 37.3145 | -121.9785 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0131058 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884025 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 8311 | 20231022 | 1300 | 20231022 | 2149 | 2248946 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 14283 | 37.3552 | -121.792 | No | Clear;32-90 F | Jumper | Burned Open | 23-0131067 | OH | Sus | 46028225 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1884036 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | OCB | 2104/2 | 20231022 | 2009 | 20231023 | 2204 | 2249243 | 1517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 877 | 512719 | 37.3035 | -121.8398 | No | Overcast;32-90 F | Capacitor | Broken- wire on ground | 23-0131092 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1884053 | 0 | Non-EPSS | N | 2023 | PHASE I OC & GRD I
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T12947 | 20231023 | 450 | 20231023 | 603 | 2249437 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 1095 | 37.3381 | -121.7814 | No | Clear;32-90 F |  |  | 23-0131145 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1884110 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 71041 | 20231023 | 942 | 20231023 | 1001 | 2249753 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 156 | 2964 | 37.1201 | -121.6495 | No | Partly Cloudy-Fog;32-90 F | Cutout- fuse holder | Broken | 23-0130883 | OH | Sus | 46028078 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1884291 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | PIERCY 2111 | 83912111 | TRANSFORMER | T25007 | 20231023 | 2038 | 20231023 | 2044 | 2250223 | 6 | Transformer only | 3rd Party | Customer Equipment | 1 | 6 | 37.2568 | -121.7847 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0131581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884392 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315934928703 | 20231023 | 2310 | 20231024 | 38 | 2250256 | 88 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 1320 | 37.28 | -121.8983 | No | Clear;32-90 F |  |  | 23-0131618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1884423 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315933735205 | 20231024 | 1246 | 20231024 | 2130 | 2250726 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7336 | 37.4585 | -121.9022 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884657 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | JUMPER | JUMPER AT 5341 | 20231024 | 1906 | 20231025 | 304 | 2251008 | 478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2921 | 37.3106 | -121.8459 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0132060 | OH | Sus | 46030856 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1884704 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 1867 | 20231025 | 843 | 20231025 | 904 | 2251274 | 21 | Distribution Circuit | Animal | Squirrel | 12 | 252 | 37.2107 | -121.8478 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0132221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884848 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 12359 | 20231025 | 1020 | 20231026 | 1113 | 2251492 | 1248 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 122531 | 37.4062 | -121.8758 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0132365 | UG | Sus | 31674019 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1884961 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 28649 | 20231025 | 1809 | 20231026 | 109 | 2251866 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 21564 | 37.3121 | -121.9892 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0132498 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885039 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10677 | 20231025 | 1852 | 20231025 | 2020 | 2251898 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 636 | 37.107 | -121.6067 | No | Overcast;32-90 F |  |  | 23-0132611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885041 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | SWITCH | X1910 | 20231026 | 1418 | 20231026 | 1537 | 2252588 | 79 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2736 | 44176 | 37.2504 | -121.8416 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885368 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 11173 | 20231027 | 2149 | 20231027 | 2251 | 2253775 | 62 | Distribution Circuit | Animal | Other | 37 | 2294 | 37.4083 | -121.8794 | No | Clear;32-90 F | Fuse | Burned Open | 23-0133454 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885735 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 657273 | 20231028 | 555 | 20231028 | 703 | 2253878 | 68 | Distribution Circuit | 3rd Party | Vehicle | 3 | 226 | 37.1292 | -121.6261 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0133474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1885752 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316891618586 | 20231028 | 1026 | 20231028 | 1502 | 2254142 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1932 | 37.0054 | -121.5656 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0133503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885830 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | OTHER | T9642 | 20231028 | 2158 | 20231029 | 105 | 2254516 | 187 | Distribution Circuit | Company Initiated | Return Circuit Normal | 10 | 1870 | 37.3149 | -121.9785 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0131058 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1885905 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR524 | 20231029 | 451 | 20231029 | 1635 | 2254602 | 704 | Distribution Circuit | Company Initiated | Other Circuits | 47 | 33088 | 37.4495 | -121.8476 | No | Clear;32-90 F | Recloser | Normal | 23-0133651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1885937 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | RECLOSER | XR248 | 20231029 | 1603 | 20231029 | 1713 | 2254999 | 70 | Distribution Circuit | Animal | Squirrel | 417 | 29190 | 37.2105 | -121.8595 | No | Clear;32-90 F | Fuse | Normal | 23-0133722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | Yes | No | No | 1886013 | 0 | EPSS Ckt | Y | 2023 | B PHASE & GRD
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315933028479 | 20231030 | 505 | 20231030 | 542 | 2255197 | 37 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 518 | 37.2739 | -121.8988 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 23-0133775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886056 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315961429405 | 20231030 | 1117 | 20231030 | 1611 | 2255648 | 294 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 4704 | 37.2993 | -121.8897 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0133960 | OH | Sus | 31674444 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886244 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | FUSE | 33224 | 20231030 | 2105 | 20231030 | 2237 | 2256152 | 92 | Distribution Circuit | Equipment Failure/Involved | Underground | 410 | 17986 | 37.2963 | -121.7633 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 23-0134168 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1886346 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | SWITCH | 40084SW | 20231031 | 731 | 20231101 | 4 | 2256312 | 993 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1986 | 37.2508 | -121.8399 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0134249 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1886494 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | RECLOSER | XR058 | 20231031 | 1134 | 20231031 | 1158 | 2256649 | 24 | Distribution Circuit | 3rd Party | Other | 2472 | 59328 | 37.3277 | -121.8313 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 23-0134298 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1886577 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | SWITCH | 10386 | 20231031 | 1607 | 20231031 | 1640 | 2256854 | 33 | Distribution Circuit | Company Initiated | Return Circuit Normal | 410 | 6666 | 37.2955 | -121.7598 | No | Partly Cloudy;32-90 F | Switch (UG) | Normal | 23-0134168 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1886643 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316114127327 | 20231101 | 948 | 20231101 | 1010 | 2257417 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 132 | 37.2427 | -121.836 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0134622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1886892 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41617 | 20231101 | 1354 | 20231101 | 1745 | 2257503 | 231 | Distribution Circuit | Vegetation | Tree - grew into line | 38 | 8778 | 37.3323 | -121.8338 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0134744 | OH | Sus | 46044214 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1886940 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1103 | 83801103 | OCB | 1103/2 | 20231101 | 2056 | 20231101 | 2108 | 2257866 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 588 | 7056 | 37.3828 | -121.9267 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0134932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1886981 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR072 | 20231102 | 826 | 20231103 | 109 | 2258048 | 1003 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2576 | 157349 | 37.2975 | -121.8379 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0135034 | OH | Sus | 46045869 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887068 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | FUSE | 12395 | 20231102 | 842 | 20231102 | 1112 | 2258081 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2850 | 37.3138 | -121.9461 | No | Partly Cloudy;32-90 F |  |  | 23-0135187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887228 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 17099 | 20231103 | 1506 | 20231103 | 1539 | 2259327 | 33 | Distribution Circuit | 3rd Party | Vehicle | 241 | 7953 | 37.3382 | -121.859 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0135731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887615 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 27043 | 20231103 | 2050 | 20231103 | 2145 | 2259581 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 55 | 37.1719 | -121.7243 | No | Clear;32-90 F | Other | Broken | 23-0135806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887646 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 43305 | 20231103 | 2119 | 20231104 | 843 | 2259591 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 13680 | 37.3512 | -121.8542 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0135815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887650 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 5249 | 20231104 | 652 | 20231104 | 909 | 2259699 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 4521 | 37.3631 | -121.8766 | No | Clear;32-90 F |  |  | 23-0135862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887729 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | RECLOSER | 773372 | 20231105 | 8 | 20231107 | 200 | 2260816 | 2992 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 654 | 1190993 | 37.3847 | -121.8366 | No | Overcast;32-90 F | Pole-Wood | Burned/flashed | 23-0136082 | OH | Sus | 35509769 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887963 | 0 | Non-EPSS | N | 2023 | A/C & GRD TRGTS
SAN JOSE | SAN JOSE | TRIMBLE-1111 | 83801111 | INTERRUPTER | 30946 | 20231105 | 721 | 20231105 | 1207 | 2260430 | 286 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 1068 | 37.3912 | -121.9314 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 23-0136001 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887900 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4239 | 20231105 | 741 | 20231105 | 1035 | 2260438 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 348 | 36.9629 | -121.4932 | No | Overcast-Fog;32-90 F |  |  | 23-0135996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1887894 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20231105 | 2210 | 20231106 | 1120 | 2260748 | 790 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1395 | 132790 | 37.0163 | -121.5446 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887955 | 0 | EPSS Ckt | N | 2023 | A/C PH & GRD TRGTS
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41787 | 20231105 | 2245 | 20231106 | 637 | 2260773 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 15104 | 37.3076 | -121.9665 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Burned/flashed | 23-0136089 | OH | Sus | 31675427 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1887967 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | RECLOSER | XR326 | 20231106 | 56 | 20231106 | 1326 | 2260917 | 750 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1802 | 91016 | 37.1073 | -121.6349 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 23-0136090 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1887968 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317116517901 | 20231106 | 719 | 20231106 | 2225 | 2261080 | 906 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2718 | 36.9875 | -121.4883 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888074 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 18271 | 20231106 | 933 | 20231106 | 1219 | 2261371 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 24568 | 37.3638 | -121.8179 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0136212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888161 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315954129453 | 20231106 | 1223 | 20231107 | 554 | 2261447 | 1051 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 32187 | 37.3006 | -121.8922 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 23-0136286 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888202 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1114 | 82921114 | FUSE | 17261 | 20231106 | 1236 | 20231106 | 1445 | 2261699 | 129 | Distribution Circuit | Animal | Squirrel | 235 | 30315 | 37.3015 | -121.9273 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 23-0136371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888241 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 19895 | 20231107 | 1128 | 20231108 | 1436 | 2262847 | 1628 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 66701 | 37.2293 | -121.8732 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0136785 | UG | Sus | 35510308 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1888616 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | SWITCH | 25656 | 20231107 | 1135 | 20231107 | 1645 | 2262854 | 310 | Distribution Circuit | Equipment Failure/Involved | Underground | 189 | 55562 | 37.381 | -121.8541 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0125633 | UG | Sus | 31671997 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888556 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 19197 | 20231107 | 2138 | 20231108 | 220 | 2263244 | 282 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 5076 | 37.2518 | -121.8798 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0136905 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1888676 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | OCB | 2104/2 | 20231108 | 846 | 20231108 | 929 | 2263631 | 37 | Distribution Circuit | 3rd Party | Vehicle | 4080 | 107778 | 37.1267 | -121.6594 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0136973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1888797 | 0 | EPSS Ckt | N | 2023 | GRD INST
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316114127327 | 20231108 | 849 | 20231108 | 956 | 2263642 | 67 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 402 | 37.2427 | -121.836 | No | Clear;32-90 F |  |  | 23-0137025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1888882 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | JUMPER | FB'S @ 102 E SAN FERNANDO ST | 20231108 | 1927 | 20231109 | 156 | 2264610 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3501 | 37.3434 | -121.8697 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0137272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889012 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316110528854 | 20231108 | 2158 | 20231109 | 415 | 2264647 | 377 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6032 | 37.2848 | -121.8381 | No | Clear;32-90 F | Secondary | Broken | 23-0137302 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889045 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316107728905 | 20231108 | 2343 | 20231109 | 415 | 2264660 | 272 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4080 | 37.2862 | -121.8391 | No | Clear;32-90 F | Secondary | Broken | 23-0137308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889049 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | FUSE | 13477 | 20231109 | 428 | 20231109 | 548 | 2264697 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 4640 | 37.4584 | -121.9117 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0137322 | OH | Sus | 31675759 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889065 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 13411 | 20231109 | 1127 | 20231109 | 1220 | 2265201 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 530 | 37.3458 | -121.8708 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0137532 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889296 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | SWITCH | 30564 | 20231109 | 2315 | 20231109 | 2329 | 2265684 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 58 | 812 | 37.4598 | -121.9105 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0137322 | OH | Sus | 31675759 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1889389 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 5147 | 20231110 | 155 | 20231110 | 359 | 2265695 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 485 | 60140 | 37.4341 | -121.8814 | No | Clear;32-90 F |  |  | 23-0137700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1889399 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316823021739 | 20231110 | 1329 | 20231110 | 1950 | 2266218 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 762 | 37.092 | -121.5902 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0137928 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889610 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | RECLOSER | XR346 | 20231111 | 824 | 20231111 | 1212 | 2266607 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 990 | 137360 | 37.3602 | -121.8756 | No | Overcast;32-90 F | Recloser | Malfunctioning | 23-0119799 | OH | Sus | 35392412 | SOUTH BAY AND CENTRAL COAST | NOV | Open Circuit | 0 | No | No | No | 1889695 | 0 | Non-EPSS | N | 2023 | A PH
SAN JOSE | SAN JOSE | MILPITAS-2112 | 82832112 | TRANSFORMER | C4971 | 20231111 | 1000 | 20231111 | 1228 | 2266688 | 148 | Transformer only | Equipment Failure/Involved | Underground | 38 | 5624 | 37.3909 | -121.8816 | No | Overcast;32-90 F | Secondary | Broken | 23-0138063 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1889728 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316828319202 | 20231111 | 1319 | 20231111 | 1417 | 2266800 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 696 | 37.0223 | -121.587 | No | Clear;32-90 F |  |  | 23-0138116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1889770 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 18881 | 20231112 | 308 | 20231112 | 1853 | 2266985 | 945 | Distribution Circuit | 3rd Party | Vehicle | 29 | 27405 | 37.2263 | -121.8681 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0138166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889827 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 70537 | 20231112 | 819 | 20231112 | 1306 | 2267197 | 287 | Distribution Circuit | Animal | Squirrel | 54 | 10751 | 37.3035 | -121.9792 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0138209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889881 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 19895 | 20231112 | 832 | 20231112 | 2125 | 2267070 | 773 | Distribution Circuit | Equipment Failure/Involved | Underground | 62 | 20881 | 37.2293 | -121.8732 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0138189 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889861 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315719229820 | 20231112 | 1533 | 20231113 | 511 | 2267274 | 818 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 8998 | 37.31 | -121.9726 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0138232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889903 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | SWITCH | 12912 | 20231112 | 1646 | 20231112 | 1855 | 2267311 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 2656 | 37.2287 | -121.8692 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0138222 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1889900 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 40505 | 20231113 | 1240 | 20231114 | 328 | 2267907 | 888 | Distribution Circuit | 3rd Party | Vehicle | 191 | 111740 | 37.0927 | -121.5926 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0138448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890182 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315867028750 | 20231113 | 1310 | 20231113 | 2312 | 2267903 | 602 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 6 | 3612 | 37.2809 | -121.9217 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0138502 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1890194 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | JUMPER | FB @ NORMAN & WILLOW | 20231114 | 101 | 20231114 | 335 | 2268513 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 12622 | 37.3003 | -121.9205 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0138631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890278 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | C778 | 20231114 | 943 | 20231115 | 124 | 2268911 | 941 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 28024 | 37.2295 | -121.8289 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0138803 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890477 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | SWITCH | 34516 | 20231115 | 858 | 20231115 | 1735 | 2269568 | 517 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 3102 | 37.392 | -121.9152 | No | Overcast;32-90 F | Switch (UG) | Normal | 23-0138421 | UG | Sus | 35506121 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1890673 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315999429595 | 20231115 | 948 | 20231115 | 1138 | 2269688 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 770 | 37.3046 | -121.8767 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0139298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890791 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316027231380 | 20231115 | 1509 | 20231116 | 311 | 2270029 | 722 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 6 | 4332 | 37.3539 | -121.8678 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0139518 | OH | Sus | 46059111 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890858 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316848020338 | 20231115 | 1724 | 20231116 | 435 | 2270274 | 671 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4697 | 37.0536 | -121.5811 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0139679 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890943 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 4475 | 20231115 | 1737 | 20231116 | 202 | 2270349 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3030 | 36.9564 | -121.5257 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0139655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890921 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | JUMPER | FLYING BELLS IFO 13043 FERHEN DR. | 20231115 | 1755 | 20231116 | 210 | 2270340 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 49995 | 37.2846 | -121.8403 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0139609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890892 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | JUMPER | OJ @ 10380 SINGLETON RD | 20231115 | 2330 | 20231116 | 332 | 2270503 | 242 | Distribution Circuit | Vegetation | Tree - grew into line | 30 | 7260 | 37.2878 | -121.8375 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0139700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1890954 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 40407 | 20231116 | 632 | 20231116 | 743 | 2270583 | 71 | Distribution Circuit | Animal | Bird found | 49 | 3499 | 37.0136 | -121.6512 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0139754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1890979 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 44410 | 20231116 | 1105 | 20231117 | 206 | 2270820 | 791 | Distribution Circuit | Equipment Failure/Involved | Underground | 197 | 72622 | 37.2564 | -121.8214 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0139982 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891079 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | OCB | 1104/12 | 20231116 | 1337 | 20231116 | 1602 | 2270934 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2888 | 212285 | 37.3611 | -121.8645 | No | Overcast;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0140025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1891091 | 0 | Non-EPSS | N | 2023 | A/C
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | INTERRUPTER | 43476 | 20231116 | 1505 | 20231116 | 2011 | 2270980 | 306 | Distribution Circuit | Equipment Failure/Involved | Underground | 129 | 37914 | 37.2952 | -121.8412 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0140189 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891115 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316027231380 | 20231117 | 1137 | 20231117 | 2058 | 2271729 | 561 | Transformer only | Vegetation | Tree - grew into line | 6 | 3366 | 37.3539 | -121.8678 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0140663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891404 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 31914 | 20231117 | 1429 | 20231117 | 1454 | 2271699 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1068 | 16495 | 37.3472 | -121.8679 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0140025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1891392 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | RECLOSER | XR222 | 20231118 | 538 | 20231119 | 47 | 2272020 | 1048 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2176 | 267510 | 37.3154 | -121.9556 | No | Partly Cloudy-Heavy Rain;32-90 F | Crossarm- Wood | Burned/flashed | 23-0140757 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1891472 | 0 | Non-EPSS | N | 2023 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4373 | 20231118 | 1231 | 20231119 | 927 | 2272618 | 1256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 18840 | 37.0718 | -121.5189 | No | Partly Cloudy-Rain;32-90 F | Fuse | Failed/Faulted | 23-0140925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891602 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 4523 | 20231118 | 1632 | 20231118 | 2328 | 2272893 | 416 | Distribution Circuit | 3rd Party | Vehicle | 66 | 27456 | 37.0193 | -121.5204 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0140954 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1891627 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | TRANSFORMER | 315997333149 | 20231120 | 40 | 20231120 | 1108 | 2273771 | 628 | Transformer only | Environmental/External | Water | 12 | 7536 | 37.4023 | -121.8791 | No | Partly Cloudy;32-90 F | Secondary | Together | 23-0141169 | OH | Sus | 46061882 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891829 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 42265 | 20231120 | 111 | 20231120 | 221 | 2273817 | 70 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 420 | 37.3822 | -121.8098 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0141175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891835 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 75005 | 20231120 | 1232 | 20231120 | 1547 | 2274336 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1170 | 37.1151 | -121.6115 | No | Clear;32-90 F |  |  | 23-0141515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1892004 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20231121 | 958 | 20231121 | 1454 | 2274977 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4440 | 37.0697 | -121.5204 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0141749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892158 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | FMC-1111 | 83871111 | SWITCH | 68796 | 20231122 | 1630 | 20231122 | 1636 | 2275919 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 54 | 37.3567 | -121.932 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0142437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892391 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316129230650 | 20231122 | 2052 | 20231123 | 929 | 2275987 | 757 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 12869 | 37.3342 | -121.8324 | No | Clear;32-90 F | Bushing | Burned/flashed | 23-0142482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892423 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | OCB | 2106/2 | 20231123 | 1310 | 20231123 | 2155 | 2276147 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 800 | 83378 | 37.0071 | -121.5569 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0142526 | OH | Sus | 46064336 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1892462 | 0 | EPSS Ckt | N | 2023 | A- B- C & TIME OC RLY
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 19873 | 20231124 | 1559 | 20231124 | 1710 | 2276678 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 142 | 37.2809 | -121.8444 | No | Clear;32-90 F |  |  | 23-0142680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892588 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 316985018519 | 20231125 | 1104 | 20231126 | 147 | 2276967 | 883 | Transformer only | Animal | Squirrel | 1 | 883 | 37.004 | -121.5334 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0142775 | OH | Sus | 31677142 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892669 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20231125 | 2321 | 20231126 | 50 | 2277219 | 89 | Distribution Circuit | 3rd Party | Vehicle | 88 | 7832 | 37.2267 | -121.8632 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0142870 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892715 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1110 | 83801110 | SWITCH | 45710 | 20231126 | 1028 | 20231126 | 1414 | 2277379 | 226 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 282 | 37.392 | -121.9297 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 23-0136001 | UG | Sus | 46047964 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1892746 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 9627 | 20231127 | 749 | 20231127 | 846 | 2277686 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 57 | 37.3192 | -121.8706 | No | Partly Cloudy;32-90 F |  |  | 23-0143026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1892889 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | INTERRUPTER | 64856 | 20231127 | 923 | 20231127 | 1235 | 2277889 | 192 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 192 | 37.3379 | -121.9088 | No | Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 23-0143149 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893042 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | JUMPER | NG POTHEAD @ 40167 | 20231127 | 2147 | 20231128 | 25 | 2278507 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 519 | 82002 | 37.2341 | -121.7662 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0143313 | OH | Sus | 46069649 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893126 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 7997 | 20231128 | 848 | 20231128 | 945 | 2278707 | 57 | Distribution Circuit | Animal | Squirrel | 70 | 3990 | 37.2844 | -121.9189 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0143400 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893313 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | TRANSFORMER | 315814230532 | 20231128 | 1602 | 20231129 | 51 | 2279162 | 529 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2645 | 37.3297 | -121.9404 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0143616 | OH | Sus | 35514163 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893404 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315913828109 | 20231128 | 1702 | 20231129 | 110 | 2279166 | 488 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3416 | 37.2636 | -121.9052 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0143609 | OH | Sus | 46072031 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893399 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | FUSE | 14429 | 20231128 | 2200 | 20231128 | 2242 | 2279294 | 42 | Distribution Circuit | Animal | Other | 37 | 1569 | 37.2643 | -121.877 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0143660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893449 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | FUSE | 70343 | 20231128 | 2302 | 20231128 | 2355 | 2279303 | 53 | Distribution Circuit | 3rd Party | Metallic Balloon | 170 | 9010 | 37.2484 | -121.8122 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0143663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1893453 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | SWITCH | 26001SW | 20231129 | 1728 | 20231130 | 145 | 2280223 | 497 | Distribution Circuit | Equipment Failure/Involved | Underground | 282 | 140154 | 37.0262 | -121.6035 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0143880 | UG | Sus | 35514208 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1893762 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 18883 | 20231129 | 2217 | 20231201 | 211 | 2280297 | 1674 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 164052 | 37.2295 | -121.8675 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0144066 | UG | Sus | 46074160 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1893800 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1114 | 82921114 | SWITCH | 12280 | 20231201 | 110 | 20231201 | 1440 | 2281124 | 784 | Distribution Circuit | Equipment Failure/Involved | Underground | 910 | 416071 | 37.2985 | -121.9319 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0136316 | UG | Sus | 35331475 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1894138 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-2107 | 82952107 | TRANSFORMER | T23051 | 20231201 | 1238 | 20231201 | 1402 | 2281642 | 84 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 336 | 37.2337 | -121.7874 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0144791 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894409 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 40875 | 20231202 | 647 | 20231202 | 838 | 2281983 | 111 | Distribution Circuit | Animal | Bird found | 5 | 555 | 37.111 | -121.6152 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 23-0144894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1894505 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 40178SW | 20231202 | 709 | 20231202 | 1146 | 2281993 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 6371 | 37.1369 | -121.6704 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0144911 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1894555 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 28841 | 20231202 | 932 | 20231202 | 1443 | 2281966 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 10885 | 37.3427 | -121.8063 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0144899 | OH | Sus | 46077549 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | Yes | No | 1894533 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 40288 | 20231202 | 2114 | 20231203 | 1934 | 2282536 | 1146 | Distribution Circuit | Equipment Failure/Involved | Underground | 127 | 85429 | 37.2361 | -121.7939 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0144991 | UG | Sus | 46077639 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894621 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | INTERRUPTER | 30028 | 20231202 | 2358 | 20231203 | 28 | s1895838 | 30 | Distribution Circuit | Company Initiated | Operating error | 485 | 14550 | 37.2365 | -121.794 | No | Clear;32-90 F | Switch (UG) | Normal | 23-0144991 | UG | Sus | 46077639 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895838 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 1891 | 20231203 | 656 | 20231203 | 754 | 2282624 | 58 | Distribution Circuit | Animal | Squirrel | 12 | 696 | 37.2202 | -121.843 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0145010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894643 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | OCB | 2105/2 | 20231203 | 2119 | 20231203 | 2311 | 2282863 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4299 | 192170 | 37.1267 | -121.6595 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0145077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1894720 | 0 | EPSS Ckt | N | 2023 | A/B
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 657273 | 20231204 | 1759 | 20231205 | 1440 | 2283808 | 1241 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 4314 | 37.1292 | -121.6261 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0145407 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895072 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | T26130 | 20231205 | 1724 | 20231206 | 740 | 2284589 | 856 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 8 | 6848 | 37.308 | -121.858 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0145686 | UG | Sus | 46079413 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895392 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 26395 | 20231206 | 735 | 20231206 | 1639 | 2284809 | 544 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 8160 | 37.2698 | -121.7975 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0145846 | UG | Sus | 46079716 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895601 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316875220710 | 20231206 | 1810 | 20231207 | 234 | 2285587 | 504 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1008 | 37.0639 | -121.5718 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1895708 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 54965 | 20231207 | 1032 | 20231207 | 1225 | 2286110 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2260 | 37.3375 | -121.6728 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0146181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895934 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 18935 | 20231207 | 1148 | 20231207 | 1420 | 2286166 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 608 | 37.3908 | -121.803 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0146192 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1895942 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15749 | 20231207 | 1323 | 20231207 | 1427 | 2286273 | 64 | Distribution Circuit | 3rd Party | Metallic Balloon | 227 | 14528 | 37.3675 | -121.8048 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 23-0146249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1895983 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 1049 | 20231207 | 1619 | 20231207 | 1708 | 2286428 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 49 | 37.037 | -121.59 | No | Clear;32-90 F |  |  | 23-0146305 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896006 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 1049 | 20231207 | 1905 | 20231208 | 540 | 2286542 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 635 | 37.037 | -121.59 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896048 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | SWITCH | 10128 | 20231208 | 1807 | 20231208 | 1823 | 2287385 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 8 | 128 | 37.3904 | -121.9164 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0145882 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1896317 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 96883 | 20231209 | 1000 | 20231209 | 1445 | 2287813 | 285 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 3135 | 37.2239 | -121.659 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0146643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896449 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316216731417 | 20231209 | 1024 | 20231209 | 1722 | 2287905 | 418 | Transformer only | 3rd Party | Vehicle | 6 | 2508 | 37.3555 | -121.8026 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1896477 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | SWITCH | 12912 | 20231209 | 1302 | 20231209 | 1319 | 2287973 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 61 | 1037 | 37.2287 | -121.8692 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0144901 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1896490 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 40225 | 20231210 | 914 | 20231210 | 1011 | 2288303 | 57 | Distribution Circuit | Animal | Squirrel | 11 | 627 | 37.254 | -121.9113 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0146742 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896601 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 2023 | 20231210 | 2115 | 20231211 | 1104 | 2288518 | 187 | Distribution Circuit | Equipment Failure/Involved | Underground | 148 | 30285 | 37.3042 | -121.8082 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 23-0146802 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1896661 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 18935 | 20231211 | 901 | 20231211 | 1526 | s1896903 | 385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1540 | 37.3908 | -121.803 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0146892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896903 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316022831031 | 20231211 | 1909 | 20231211 | 2004 | 2289563 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 1650 | 37.3441 | -121.8692 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896939 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316756721398 | 20231211 | 1920 | 20231212 | 118 | 2289650 | 358 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2864 | 37.0825 | -121.6128 | No | Clear;32-90 F | Secondary | Broken | 23-0146963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1896972 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317156517770 | 20231213 | 1117 | 20231214 | 50 | 2290923 | 813 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 813 | 36.9839 | -121.4743 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1897522 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | SWITCH | 13035 | 20231214 | 1056 | 20231214 | 2019 | 2291842 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 110911 | 37.3147 | -121.8825 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0147411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1897847 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | SWITCH | 13188 | 20231216 | 1210 | 20231216 | 1659 | 2293201 | 289 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 16293 | 37.2944 | -121.8419 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0147649 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898379 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 2007 | 20231217 | 1356 | 20231218 | 242 | 2293695 | 766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 46726 | 37.4359 | -121.8839 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147767 | OH | Sus | 46093504 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1898515 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 43947 | 20231217 | 1404 | 20231218 | 527 | 2293697 | 923 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 12922 | 37.4107 | -121.8801 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147832 | OH | Sus | 46093522 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1898594 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20231218 | 935 | 20231219 | 410 | 2294356 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 95908 | 37.1083 | -121.7324 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0147878 | OH | Sus | 46094473 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1898668 | 0 | EPSS Ckt | N | 2023 | GRD T & A PHASE
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 37264 | 20231218 | 1101 | 20231218 | 1203 | 2294458 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1291 | 9862 | 37.0132 | -121.5513 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0147892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898692 | 0 | EPSS Ckt | N | 2023 | NONE
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316866719563 | 20231218 | 1224 | 20231218 | 2156 | 2294370 | 572 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 572 | 37.0329 | -121.5738 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0147911 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898719 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4373 | 20231219 | 617 | 20231219 | 906 | 2295314 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2535 | 37.0718 | -121.5189 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F |  |  | 23-0148065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1898892 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | SWITCH | 13995 | 20231219 | 1025 | 20231219 | 1520 | 2295595 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 885 | 37.0172 | -121.5428 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Deteriorated | 23-0148046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1898941 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316471024510 | 20231220 | 709 | 20231220 | 1643 | 2296322 | 574 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 574 | 37.1667 | -121.7118 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 23-0148244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899173 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4373 | 20231220 | 844 | 20231220 | 1500 | 2296433 | 376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 5640 | 37.0718 | -121.5189 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0148251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899183 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 15503 | 20231221 | 18 | 20231221 | 1010 | 2297262 | 592 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 20128 | 37.3219 | -121.7608 | No | Clear;32-90 F |  |  | 23-0148411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899368 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | T5523 | 20231221 | 154 | 20231221 | 1036 | 2297283 | 522 | Transformer only | Equipment Failure/Involved | Underground | 13 | 6786 | 37.2229 | -121.8792 | No | Overcast;32-90 F | Transformer | Broken | 23-0148455 | UG | Sus | 46098305 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1899435 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20231221 | 301 | 20231221 | 313 | 2297300 | 12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 169 | 2028 | 37.3339 | -121.7556 | No | Partly Cloudy;32-90 F | Jumper | Arcing | 23-0148417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899376 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | RECLOSER | XR294 | 20231221 | 842 | 20231221 | 1034 | 2297462 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 242 | 24097 | 36.9676 | -121.5525 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0148444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899417 | 0 | EPSS Ckt | N | 2023 | A PHASE OC & GRD OC
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | OCB | 1112/2 | 20231221 | 915 | 20231221 | 1736 | 2297498 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2705 | 88812 | 37.3282 | -121.9025 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0148454 | OH | Sus | 31680082 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1899432 | 0 | Non-EPSS | N | 2023 | GRD T
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 316008229532 | 20231221 | 918 | 20231222 | 256 | 2297497 | 1058 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 3174 | 37.303 | -121.8736 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0148509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899506 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1111 | 82261111 | TRANSFORMER | T274844 | 20231222 | 1140 | 20231223 | 220 | 2298355 | 821 | Distribution Circuit | Equipment Failure/Involved | Underground | 123 | 99357 | 37.3351 | -121.8941 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0148603 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1899657 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315659329604 | 20231222 | 1324 | 20231222 | 1508 | 2298392 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1144 | 37.304 | -121.9933 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0148593 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1899648 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316025031002 | 20231224 | 713 | 20231224 | 921 | 2299062 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1152 | 37.3434 | -121.8685 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0148745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1899812 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42493 | 20231226 | 923 | 20231226 | 1740 | s1900003 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1139 | 37.1536 | -121.6575 | No | Clear;32-90 F | Insulator | Broken | 23-0148886 | OH | Sus | 46101201 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900003 | 1 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 17525 | 20231226 | 1234 | 20231226 | 1410 | 2299901 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 96 | 37.0806 | -121.6256 | No | Clear;32-90 F |  |  | 23-0148897 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900015 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 5431 | 20231226 | 1611 | 20231226 | 1827 | 2300095 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2856 | 37.1288 | -121.6774 | No | Overcast;32-90 F |  |  | 23-0148916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900034 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | NORTECH-2107 | 82462107 | FUSE | 35386 | 20231226 | 1805 | 20231227 | 127 | 2300169 | 442 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 3536 | 37.4169 | -121.9553 | No | Overcast;32-90 F |  |  | 23-0148921 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900039 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20231227 | 1835 | 20231227 | 2259 | 2300940 | 264 | Distribution Circuit | Equipment Failure/Involved | Overhead | 213 | 36072 | 37.1869 | -121.8177 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0149036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900214 | 0 | EPSS Ckt | N | 2023 | N/A
SAN JOSE | SAN JOSE | TRIMBLE-2119 | 83802119 | INTERRUPTER | XN004 | 20231227 | 2306 | 20231228 | 45 | 2300991 | 99 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 297 | 37.3777 | -121.9279 | No | Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 23-0149076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900255 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | OCB | 1107/2 | 20231228 | 1219 | 20231228 | 1341 | 2301324 | 82 | Distribution Circuit | Equipment Failure/Involved | Underground | 1256 | 100796 | 37.341 | -121.9019 | No | Overcast;32-90 F | Conductor- Underground | Broken | 23-0149110 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900358 | 0 | Non-EPSS | N | 2023 | PHASE OC INST
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 11695 | 20231228 | 1557 | 20231228 | 1950 | 2301514 | 233 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 15416 | 37.4077 | -121.8539 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0149138 | UG | Sus | 46102814 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900395 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | OTHER | J6093 TWD J6978 | 20231229 | 848 | 20231230 | 249 | 2301885 | 1081 | Distribution Circuit | 3rd Party | Vehicle | 2 | 2162 | 37.2833 | -121.8644 | No | Overcast-Drizzle;32-90 F | Connector or Splice (UG) | Broken | 23-0149202 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900495 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 41555 | 20231229 | 1047 | 20231229 | 1610 | 2301898 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 503 | 37.3911 | -121.9007 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0149210 | OH | Sus | 46106403 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | Yes | 1900502 | 1 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15749 | 20231229 | 1752 | 20231229 | 2002 | 2302210 | 130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 227 | 29510 | 37.3675 | -121.8048 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0149274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900572 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 25309 | 20231229 | 2212 | 20231229 | 2332 | s1900591 | 80 | Distribution Circuit | Animal | Squirrel | 22 | 1760 | 37.4285 | -121.9152 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0149293 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900591 | 0 | Non-EPSS | N | 2023
SAN JOSE | SAN JOSE | FMC-1111 | 83871111 | RECLOSER | 90062 | 20231230 | 937 | 20231230 | 1016 | 2302558 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 39 | 37.35 | -121.9265 | No | Overcast;32-90 F |  |  | 23-0149339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1900647 | 0 | Non-EPSS | N | 2023 | B PHASE & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | JUMPER | OJ LOADSIDE OF CGC#2728 | 20231231 | 1030 | 20231231 | 1536 | 2303175 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4590 | 37.1187 | -121.6463 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0149466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900785 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 14865 | 20231231 | 1818 | 20231231 | 2348 | 2303329 | 330 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3630 | 37.0716 | -121.5688 | No | Overcast;32-90 F |  |  | 24-0005727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900839 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13091 | 20231231 | 1838 | 20240101 | 1335 | 2303335 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 12114 | 37.374 | -121.8091 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0149506 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1900827 | 0 | EPSS Ckt | N | 2023
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41739 | 20240101 | 1400 | 20240101 | 1504 | 2304300 | 64 | Distribution Circuit | 3rd Party | Metallic Balloon | 232 | 14848 | 37.2964 | -121.9136 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0005804 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900907 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 26365 | 20240101 | 1636 | 20240101 | 2055 | 2304371 | 259 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 518 | 36.9893 | -121.5332 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0005822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1900923 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315924029004 | 20240101 | 2140 | 20240102 | 136 | 2304421 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 5115 | 37.2881 | -121.9022 | No | Clear;32-90 F | Secondary | Broken | 24-0005839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1900940 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 2007 | 20240102 | 2009 | 20240102 | 2154 | 2305426 | 105 | Distribution Circuit | 3rd Party | Other | 61 | 6405 | 37.4359 | -121.8839 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0006265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901161 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR074 | 20240102 | 2226 | 20240105 | 851 | 2305530 | 3505 | Distribution Circuit | 3rd Party | Customer Equipment | 349 | 9073 | 37.2887 | -121.8287 | No | Overcast-Drizzle;32-90 F | Metering Equipment | Failed/Faulted | 24-0006278 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901174 | 0 | Non-EPSS | N | 2024 | A PHASE & GRD
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | RECLOSER | XR248 | 20240102 | 2325 | 20240102 | 2331 | 2305438 | 6 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 417 | 2502 | 37.2105 | -121.8595 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0006288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901185 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | HICKS SUB | 8343 | RECLOSER | TEMP LR 2103/2 | 20240103 | 714 | 20240103 | 2146 | 2305750 | 872 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3673 | 170832 | 37.2332 | -121.9013 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0006322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1901211 | 0 | Non-EPSS | N | 2024 | A-B-C-TIME
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | TRANSFORMER | 315915327468 | 20240103 | 1022 | 20240103 | 1154 | 2306260 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1472 | 37.246 | -121.9045 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Broken- wire on ground | 24-0006422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901330 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 26683 | 20240103 | 1408 | 20240103 | 1426 | 2306437 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 180 | 3240 | 37.3186 | -121.9892 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0006562 | OH | Sus | 31680986 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901381 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | TRANSFORMER | T5384 | 20240103 | 1644 | 20240103 | 1706 | 2306632 | 22 | Transformer only | Equipment Failure/Involved | Underground | 16 | 352 | 37.3869 | -121.8423 | No | Overcast;32-90 F | Secondary | Deteriorated | 24-0006625 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901399 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | TRANSFORMER | T21185 | 20240104 | 637 | 20240104 | 823 | 2306774 | 106 | Transformer only | Equipment Failure/Involved | Underground | 10 | 1060 | 37.3984 | -121.9089 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0006718 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901467 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20240104 | 731 | 20240104 | 1105 | 2306798 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 3210 | 37.0697 | -121.5204 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0006874 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901606 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | SWITCH | FLYING BELLS .5 SP/W/O 26683 | 20240104 | 945 | 20240104 | 1610 | 2307061 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 12018 | 37.3212 | -121.9867 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0006562 | OH | Sus | 31680986 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1901590 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1111 | 83871111 | RECLOSER | 90062 | 20240104 | 955 | 20240104 | 1320 | 2307012 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 205 | 37.35 | -121.9265 | No | Clear;32-90 F | Customer Equipment | Malfunctioning | 24-0006801 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901574 | 0 | Non-EPSS | N | 2024 | B-C-GRD
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 71273 | 20240104 | 1542 | 20240105 | 252 | 2307298 | 670 | Distribution Circuit | 3rd Party | Vehicle | 241 | 160906 | 37.316 | -121.9766 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0007079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | Yes | No | 1901650 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | T13860 | 20240105 | 715 | 20240106 | 5 | 2307594 | 1010 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 17216 | 37.4463 | -121.9123 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0007332 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901851 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR070 | 20240105 | 1056 | 20240105 | 1317 | 2307869 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 3867 | 37.0428 | -121.6546 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0007325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901849 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 61388 | 20240105 | 2216 | 20240105 | 2329 | 2308270 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 5276 | 37.3311 | -121.8522 | No | Clear;32-90 F |  |  | 24-0007549 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1901933 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 61388 | 20240106 | 821 | 20240106 | 1024 | 2308435 | 123 | Distribution Circuit | 3rd Party | Metallic Balloon | 148 | 17334 | 37.3311 | -121.8522 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0007576 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1901971 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | OTHER | T870637 TWD 83450 | 20240106 | 1007 | 20240106 | 1342 | 2308542 | 215 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 215 | 37.3697 | -121.883 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0007411 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1901979 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 25673 | 20240106 | 1502 | 20240106 | 1703 | 2308820 | 121 | Distribution Circuit | Vegetation | Tree - grew into line | 57 | 6141 | 37.4033 | -121.8513 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0007643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902024 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 19147 | 20240106 | 2137 | 20240107 | 1412 | 2308760 | 995 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 2655 | 37.3685 | -121.887 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0007708 | UG | Sus | 46132060 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902081 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 13989 | 20240107 | 1034 | 20240107 | 1125 | 2309178 | 51 | Distribution Circuit | Animal | Squirrel | 286 | 14586 | 37.3629 | -121.8621 | No | Clear;32-90 F | Fuse | Normal | 24-0007748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1902119 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 41623 | 20240107 | 1423 | 20240107 | 1826 | 2309254 | 243 | Distribution Circuit | 3rd Party | Vehicle | 15 | 3645 | 37.3095 | -121.8313 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0007767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902130 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | RECLOSER | 819378 | 20240107 | 1535 | 20240107 | 2354 | 2309282 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 258 | 13158 | 37.4308 | -121.8637 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0002459 | UG | Sus | 35463207 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902133 | 0 | EPSS Ckt | N | 2024 | A- G- 51 (TIME)
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315999429595 | 20240107 | 1632 | 20240108 | 213 | 2309235 | 581 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4067 | 37.3046 | -121.8767 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0007775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902137 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316127030376 | 20240107 | 2212 | 20240107 | 2330 | 2309396 | 78 | Transformer only | Unknown Cause | Patrol - found nothing | 10 | 780 | 37.3266 | -121.833 | No | Clear;32-90 F |  |  | 24-0007801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902163 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 40195 | 20240108 | 1052 | 20240108 | 1230 | 2309769 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 20090 | 37.1239 | -121.6405 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0007952 | OH | Sus | 46133117 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1902370 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T24043 | 20240108 | 2203 | 20240109 | 550 | 2310214 | 467 | Distribution Circuit | 3rd Party | Vehicle | 2042 | 13174 | 37.326 | -121.7692 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0008238 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1902453 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 18151 | 20240109 | 1732 | 20240109 | 2329 | 2311054 | 357 | Distribution Circuit | Vegetation | Tree - grew into line | 152 | 54264 | 37.2219 | -121.8721 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0008672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1902714 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | C2366 | 20240109 | 2032 | 20240110 | 151 | 2311160 | 319 | Transformer only | Equipment Failure/Involved | Underground | 23 | 7337 | 37.3528 | -121.7966 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0008706 | UG | Sus | 46134986 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1902730 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 92999 | 20240109 | 2334 | 20240109 | 2348 | 2311262 | 14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 33 | 37.3368 | -121.8171 | No | Partly Cloudy;32-90 F |  |  | 24-0008745 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1902771 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 100000013390 | 20240110 | 807 | 20240110 | 942 | 2311371 | 95 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 95 | 36.9966 | -121.5014 | No | Overcast-Fog;32-90 F |  |  | 24-0008858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1902920 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | RECLOSER | XR112 | 20240110 | 1915 | 20240111 | 217 | 2312246 | 422 | Distribution Circuit | Equipment Failure/Involved | Underground | 1398 | 57066 | 37.3091 | -121.8151 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Burned/flashed | 24-0009301 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1903074 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 11021 | 20240110 | 2202 | 20240110 | 2330 | 2312434 | 88 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 1496 | 37.1002 | -121.6213 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0009366 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903125 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20240110 | 2305 | 20240111 | 27 | 2312501 | 82 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 6 | 492 | 37.2181 | -121.7422 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0009375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903130 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR586 | 20240111 | 641 | 20240111 | 1107 | 2312639 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 463 | 57754 | 37.0279 | -121.5275 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0009436 | OH | Sus | 46145953 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903176 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | INTERRUPTER | 30040 | 20240111 | 748 | 20240111 | 1138 | 2312678 | 230 | Distribution Circuit | Equipment Failure/Involved | Underground | 336 | 35412 | 37.1414 | -121.607 | No | Overcast-Strong Winds;32-90 F | Transformer (UG) | Burned/flashed | 24-0009470 | UG | Sus | 46146342 | SOUTH BAY AND CENTRAL COAST | JAN | Multi-Fault | 0 | No | No | No | 1903213 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316127030376 | 20240111 | 2031 | 20240111 | 2147 | 2313361 | 76 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 760 | 37.3266 | -121.833 | No | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0009933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903446 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | RECLOSER | 524360 | 20240111 | 2209 | 20240112 | 255 | 2313403 | 286 | Distribution Circuit | Vegetation | Tree - grew into line | 145 | 39214 | 36.9756 | -121.5564 | No | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0009906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1903454 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 26517 | 20240114 | 1338 | 20240114 | 1452 | 2315431 | 74 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 2442 | 37.0787 | -121.6557 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0010695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903982 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 23341 | 20240114 | 1505 | 20240115 | 9 | 2315458 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 58208 | 37.3229 | -121.9249 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0010703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1903981 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 6265 | 20240115 | 904 | 20240115 | 1334 | 2315715 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 7290 | 37.3394 | -121.7685 | No | Clear;32-90 F |  |  | 24-0010799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904063 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | RECLOSER | XR154 | 20240115 | 2109 | 20240116 | 1051 | 2315988 | 822 | Distribution Circuit | Equipment Failure/Involved | Underground | 788 | 43113 | 37.2487 | -121.8754 | No | Partly Cloudy;32-90 F | Switch (UG) | Burned/flashed | 24-0010847 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904097 | 0 | EPSS Ckt | N | 2024 | C PHASE & GRD
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | FUSE | 75461 | 20240116 | 1044 | 20240116 | 1152 | 2316427 | 68 | Distribution Circuit | 3rd Party | Metallic Balloon | 59 | 3985 | 37.3386 | -121.88 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0011042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904301 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | SWITCH | 24642 | 20240116 | 2119 | 20240117 | 720 | 2317103 | 601 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 4224 | 37.3709 | -121.8934 | No | Overcast-Rain;32-90 F | Transformer (UG) | Failed/Faulted | 24-0011140 | UG | Sus | 35523918 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904420 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | FUSE | 86879 | 20240116 | 2320 | 20240117 | 41 | 2317164 | 81 | Distribution Circuit | 3rd Party | Vehicle | 100 | 8100 | 37.3416 | -121.8876 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Normal | 24-0011402 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1904434 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315871829343 | 20240116 | 2343 | 20240117 | 158 | 2317172 | 135 | Transformer only | Company Initiated | Construction Activity/equip- company | 9 | 1215 | 37.2972 | -121.9203 | No | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0011386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904429 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | TRANSFORMER | T1473 | 20240117 | 849 | 20240118 | 147 | 2317370 | 1018 | Distribution Circuit | Equipment Failure/Involved | Underground | 257 | 34352 | 37.3841 | -121.8935 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0011556 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904615 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | T5257 | 20240117 | 912 | 20240117 | 2130 | 2317436 | 738 | Transformer only | Equipment Failure/Involved | Underground | 28 | 20664 | 37.303 | -121.8205 | No | Overcast;32-90 F | Secondary | Deteriorated | 24-0011506 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904566 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315981928137 | 20240117 | 1330 | 20240117 | 2022 | 2317709 | 412 | Transformer only | Vegetation | Tree - grew into line | 8 | 3296 | 37.2646 | -121.882 | No | Clear;32-90 F | Transformer | Bent or Twisted | 24-0011834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904675 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | TRANSFORMER | 100000124946 | 20240117 | 1504 | 20240117 | 1735 | 2317638 | 151 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 755 | 37.252 | -121.9147 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0011745 | OH | Sus | 46160756 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1904661 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 54800 | 20240120 | 516 | 20240120 | 1041 | 2319550 | 229 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 36516 | 37.3391 | -121.7853 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0012887 | UG | Sus | 31682066 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905217 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | RECLOSER | XR256 | 20240120 | 1428 | 20240120 | 2355 | 2319987 | 567 | Distribution Circuit | 3rd Party | Vehicle | 342 | 79533 | 37.3474 | -121.8108 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0012948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905269 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | SAN JOSE B-1117 | 82261117 | OCB | 1117/2 | 20240120 | 2225 | 20240121 | 1814 | 2320199 | 1189 | Distribution Circuit | Equipment Failure/Involved | Underground | 721 | 117217 | 37.3411 | -121.9017 | No | Overcast;32-90 F | Other | Failed/Faulted | 24-0013033 | UG | Sus | 46166440 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905306 | 0 | Non-EPSS | N | 2024 | PRI GRD
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | TRANSFORMER | T9298 | 20240121 | 705 | 20240122 | 130 | 2320283 | 1105 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 4618 | 37.3875 | -121.9246 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 24-0013087 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1905351 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 40306 | 20240122 | 300 | 20240122 | 1758 | 2320889 | 253 | Distribution Circuit | Equipment Failure/Involved | Underground | 2337 | 157875 | 37.2263 | -121.777 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0013188 | UG | Sus | 46170084 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905437 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | INTERRUPTER | 6542 | 20240122 | 755 | 20240123 | 547 | 2321035 | 1094 | Distribution Circuit | Equipment Failure/Involved | Underground | 613 | 329711 | 37.2915 | -121.7592 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0013312 | UG | Sus | 35525618 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905521 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 30995 | 20240122 | 1207 | 20240122 | 1817 | 2321389 | 370 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 28 | 10360 | 37.2871 | -121.9226 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0013538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905619 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20240122 | 1630 | 20240122 | 2219 | 2321664 | 349 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 6 | 2094 | 37.2181 | -121.7422 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0013639 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905662 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | INTERRUPTER | 30900 | 20240123 | 23 | 20240123 | 417 | 2321898 | 234 | Distribution Circuit | Equipment Failure/Involved | Underground | 451 | 71747 | 37.2761 | -121.8331 | No | Overcast-Fog;32-90 F | Conductor- Underground | Deteriorated | 24-0013663 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905676 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | INTERRUPTER | 30900 | 20240123 | 555 | 20240124 | 138 | 2321950 | 1183 | Distribution Circuit | Equipment Failure/Involved | Underground | 451 | 30634 | 37.2761 | -121.8331 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0013774 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Open Circuit | 0 | No | No | No | 1905816 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 25589 | 20240123 | 1110 | 20240123 | 1206 | 2322344 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 392 | 37.0343 | -121.7081 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0013903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1905870 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 71273 | 20240123 | 1156 | 20240123 | 1315 | 2322379 | 79 | Distribution Circuit | 3rd Party | Vehicle | 241 | 19039 | 37.316 | -121.9766 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0013914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1905874 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OCB | 2107/2 | 20240124 | 747 | 20240125 | 239 | 2322832 | 1132 | Distribution Circuit | Environmental/External | Lightning | 263 | 51226 | 37.0071 | -121.5569 | No | Overcast-Fog-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1905962 | 0 | EPSS Ckt | N | 2024 | B-C 51
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | RECLOSER | XR344 | 20240124 | 932 | 20240124 | 1344 | 2322960 | 195 | Distribution Circuit | Equipment Failure/Involved | Underground | 2419 | 472827 | 37.3742 | -121.8729 | No | Overcast-Rain;32-90 F | Elbow | Failed/Faulted | 24-0014280 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906031 | 0 | Non-EPSS | N | 2024 | B & G
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | TRANSFORMER | 316664018765 | 20240124 | 1128 | 20240124 | 2312 | 2323102 | 704 | Transformer only | Environmental/External | Lightning | 2 | 1408 | 37.01 | -121.6437 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0014412 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906071 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 71047 | 20240124 | 1130 | 20240125 | 209 | 2323107 | 879 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 7032 | 37.0197 | -121.6612 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0014588 | UG | Sus | 46171491 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906105 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 71273 | 20240124 | 1157 | 20240124 | 1429 | 2323133 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 24434 | 37.316 | -121.9766 | No | Overcast;32-90 F |  |  | 24-0014524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906092 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | SWITCH | 34598 | 20240124 | 1400 | 20240125 | 503 | -2322960 | 19 | Distribution Circuit | Equipment Failure/Involved | Underground | 2419 | 19924 | 37.3873 | -121.8827 | No | Overcast-Rain;32-90 F | Switch (UG) | Failed/Faulted | 24-0014280 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906093 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 71273 | 20240124 | 1542 | 20240124 | 2057 | 2323314 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 50635 | 37.316 | -121.9766 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0014653 | OH | Sus | 46171447 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1906110 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 15019 | 20240125 | 412 | 20240125 | 1440 | 2323581 | 628 | Distribution Circuit | 3rd Party | Customer Equipment | 14 | 8792 | 37.2998 | -121.9511 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0006763 | OH | Sus | 47028501 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1906168 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316426522195 | 20240125 | 1123 | 20240125 | 1528 | 2324094 | 245 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 490 | 37.1031 | -121.7268 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0015116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906397 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 43483 | 20240125 | 1207 | 20240126 | 328 | 2324078 | 921 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 2578 | 37.1536 | -121.6576 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0015150 | UG | Sus | 46171891 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906405 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | RECLOSER | XR068 | 20240125 | 1843 | 20240126 | 252 | 2324335 | 489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1626 | 69292 | 37.2221 | -121.8674 | No | Partly Cloudy;32-90 F | Transformer (OH) | Arcing | 24-0015326 | OH | Sus | 46172600 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906446 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | TRANSFORMER | 316686518900 | 20240126 | 720 | 20240126 | 1440 | 2324487 | 440 | Transformer only | Environmental/External | Lightning | 1 | 440 | 37.0135 | -121.636 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015465 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906599 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | RECLOSER | XR024 | 20240126 | 1008 | 20240126 | 1014 | 2324763 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 570 | 3420 | 37.395 | -121.8571 | No | Partly Cloudy;32-90 F | Capacitor | Broken | 24-0015515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906663 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 28856 | 20240127 | 336 | 20240127 | 2014 | 2325354 | 998 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 11579 | 37.3098 | -121.8128 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0015817 | UG | Sus | 35526553 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1906797 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | X1818 | 20240127 | 1520 | 20240128 | 907 | 2325673 | 1067 | Distribution Circuit | 3rd Party | Vehicle | 1762 | 71753 | 37.1024 | -121.6271 | No | Clear;32-90 F | Pole-Wood | Broken- wire on object | 24-0015881 | OH | Sus | 31682608 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | Yes | No | 1906862 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | TRANSFORMER | C1695 | 20240127 | 2239 | 20240127 | 2339 | 2325931 | 60 | Transformer only | Equipment Failure/Involved | Underground | 18 | 1080 | 37.2267 | -121.7994 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0015921 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1906885 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15569 | 20240129 | 1222 | 20240129 | 1232 | 2327311 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 10 | 37.3422 | -121.722 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0016222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907214 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | RECLOSER | XR326 | 20240129 | 1234 | 20240129 | 1249 | 2327345 | 15 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1796 | 26940 | 37.1073 | -121.6349 | No | Clear;32-90 F | Jumper | Normal | 24-0016237 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907219 | 0 | EPSS Ckt | N | 2024 | C GRD
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 4311 | 20240129 | 1720 | 20240129 | 2248 | 2327572 | 328 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 10496 | 37.1801 | -121.7022 | No | Partly Cloudy;32-90 F |  |  | 24-0016416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907288 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | OCB | 2103/2 | 20240129 | 1823 | 20240129 | 1841 | 2327620 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6132 | 110376 | 37.0072 | -121.557 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 24-0016401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907279 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR092 | 20240129 | 2029 | 20240129 | 2158 | 2327645 | 89 | Distribution Circuit | Equipment Failure/Involved | Underground | 1919 | 70642 | 37.3237 | -121.7968 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0016417 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1907289 | 0 | EPSS Ckt | N | 2024 | A-B-C
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 3705 | 20240130 | 849 | 20240130 | 1045 | 2327980 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 116 | 37.2984 | -121.8553 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0016575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907499 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | SWITCH | 27854 | 20240130 | 1709 | 20240130 | 1729 | 2328566 | 20 | Distribution Circuit | Company Initiated | Return Circuit Normal | 162 | 3240 | 37.3415 | -121.8179 | No | Overcast;32-90 F | Switch (UG) | Normal | 24-0016417 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | None | 0 | No | No | No | 1907587 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | OCB | 1110/2 | 20240130 | 1724 | 20240130 | 1822 | 2328541 | 58 | Distribution Circuit | 3rd Party | Vehicle | 4627 | 157078 | 37.3282 | -121.9025 | No | Overcast;32-90 F | Anchor or Guy | Bent or Twisted | 24-0016888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | No | No | 1907585 | 0 | Non-EPSS | N | 2024 | SET A RLY A-B-C
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | T12526 | 20240131 | 227 | 20240131 | 1218 | 2328781 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 169 | 17377 | 37.4381 | -121.8739 | No | Partly Cloudy;32-90 F | Transformer (UG) | Deteriorated | 24-0017000 | UG | Sus | 35527352 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1907661 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | FUSE | 11583 | 20240131 | 830 | 20240131 | 924 | 2329071 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 2160 | 37.3374 | -121.9248 | No | Overcast;32-90 F |  |  | 24-0017128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1907804 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315776929828 | 20240131 | 1620 | 20240131 | 2115 | 2328846 | 295 | Transformer only | Vegetation | Tree - grew into line | 8 | 2360 | 37.3102 | -121.9528 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Normal | 24-0017507 | OH | Sus | 31682695 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1907953 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11881 | 20240131 | 1624 | 20240201 | 820 | 2330012 | 956 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 23900 | 37.3882 | -121.8132 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1907974 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12537 | 20240131 | 1830 | 20240131 | 2018 | 2330233 | 108 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 125 | 13500 | 37.3269 | -121.8307 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0017646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1908049 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 14901 | 20240131 | 2003 | 20240201 | 1401 | 2330394 | 1078 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 58639 | 37.0763 | -121.5775 | No | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 24-0017706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1908100 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 65026 | 20240201 | 46 | 20240202 | 534 | 2330713 | 935 | Distribution Circuit | Equipment Failure/Involved | Underground | 99 | 123192 | 37.4227 | -121.9086 | No | Overcast-Rain;32-90 F | Transformer (UG) | Broken | 24-0017756 | UG | Sus | 35528608 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908154 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | TRANSFORMER | 315937532120 | 20240201 | 52 | 20240201 | 1612 | 2330719 | 920 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 11040 | 37.3738 | -121.8992 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Contaminated | 24-0017882 | OH | Sus | 46176247 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908246 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316848818738 | 20240201 | 1136 | 20240201 | 2210 | 2331264 | 634 | Transformer only | Vegetation | Tree - grew into line | 8 | 5072 | 37.0096 | -121.5788 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0018030 | OH | Sus | 46176496 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908312 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | SWITCH | 33988SW | 20240201 | 1234 | 20240201 | 1705 | 2331364 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 17073 | 37.1404 | -121.603 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0018161 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908343 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316887020585 | 20240201 | 1315 | 20240202 | 230 | 2332089 | 795 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1590 | 37.0604 | -121.5679 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0018394 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908456 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | C2942 | 20240201 | 1414 | 20240202 | 441 | 2331460 | 867 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 56355 | 37.2528 | -121.8283 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0018263 | UG | Sus | 35528613 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908369 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | SWITCH | 33376SW | 20240201 | 1831 | 20240202 | 322 | 2331901 | 531 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 25317 | 37.2218 | -121.8805 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0018374 | UG | Sus | 35528632 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908444 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316151532680 | 20240202 | 210 | 20240202 | 343 | 2332066 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 651 | 37.3899 | -121.8255 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Normal | 24-0018391 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908453 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315963528647 | 20240202 | 933 | 20240202 | 1140 | 2332327 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1778 | 37.2785 | -121.8884 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0018492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908564 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41517 | 20240202 | 1424 | 20240203 | 114 | 2332646 | 650 | Distribution Circuit | Vegetation | Tree - grew into line | 31 | 20150 | 37.3306 | -121.8358 | No | Overcast;32-90 F | Fuse | Normal | 24-0018745 | OH | Sus | 46178270 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908656 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 25647 | 20240202 | 1445 | 20240203 | 720 | 2332841 | 995 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1990 | 37.336 | -121.9187 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0018837 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908699 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | T14084 | 20240202 | 1547 | 20240203 | 1005 | 2333639 | 1098 | Transformer only | Equipment Failure/Involved | Underground | 7 | 7686 | 37.2218 | -121.8808 | No | Clear;32-90 F | Secondary | Broken | 24-0018931 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1908832 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 43379 | 20240203 | 602 | 20240203 | 930 | 2333551 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 624 | 37.1508 | -121.6 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0018917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908822 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 3261 | 20240203 | 648 | 20240203 | 801 | 2333421 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 657 | 37.1076 | -121.5874 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 24-0018908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1908775 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | JUMPER | FLYING BELLS 1 S/E/O 34409 | 20240203 | 750 | 20240203 | 1424 | 2333438 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 394 | 37.1849 | -121.7588 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0018906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1908770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 34940 | 20240204 | 212 | 20240204 | 1516 | 2334244 | 784 | Distribution Circuit | Equipment Failure/Involved | Underground | 325 | 244099 | 37.4259 | -121.9133 | Yes | Overcast-Rain;32-90 F | Conductor- Underground | Broken | 24-0019117 | UG | Sus | 35528897 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909004 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | FUSE | 11583 | 20240204 | 456 | 20240204 | 705 | 2334392 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 5160 | 37.3374 | -121.9248 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909059 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 70553 | 20240204 | 543 | 20240204 | 1448 | 2335482 | 545 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 493 | 268685 | 37.3677 | -121.8052 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0019984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909818 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 89634 | 20240204 | 545 | 20240209 | 1332 | 2334501 | 7667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 77996 | 37.2184 | -121.7395 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019151 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909038 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28657 | 20240204 | 550 | 20240207 | 1850 | 2334506 | 5100 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 237387 | 37.3035 | -121.9819 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0019212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909103 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | OCB | 1105/12 | 20240204 | 619 | 20240204 | 722 | 2334601 | 63 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4289 | 267837 | 37.3611 | -121.8645 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019167 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909056 | 0 | Non-EPSS | N | 2024 | B & C
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316146030949 | 20240204 | 621 | 20240204 | 1431 | 2334607 | 490 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 11 | 5390 | 37.3424 | -121.8267 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Normal | 24-0020118 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909947 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 73139 | 20240204 | 624 | 20240204 | 813 | 2334613 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 5123 | 37.4117 | -121.8729 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909136 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 3835 | 20240204 | 627 | 20240205 | 1408 | 2335139 | 1901 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 258536 | 37.037 | -121.5394 | Yes | Partly Cloudy-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0019304 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909190 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316147927527 | 20240204 | 643 | 20240204 | 1446 | 2334690 | 483 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 6 | 2898 | 37.2485 | -121.8245 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 24-0020072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909900 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 13647 | 20240204 | 644 | 20240206 | 1950 | 2334694 | 3666 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 146640 | 37.4049 | -121.8779 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0022031 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911745 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 12975 | 20240204 | 646 | 20240204 | 1059 | 2334699 | 253 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 273 | 69168 | 37.2859 | -121.8428 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909161 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | OTHER | WIRE DOWN 3410 PICCADILLY DR | 20240204 | 650 | 20240205 | 1940 | 2334720 | 2210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3122 | 115460 | 37.2716 | -121.8827 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1909732 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20240204 | 653 | 20240204 | 905 | 2334772 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3349 | 269391 | 37.2332 | -121.9012 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909080 | 0 | Non-EPSS | N | 2024 | PH TIME
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | RECLOSER | 333750 | 20240204 | 655 | 20240206 | 1036 | 2335785 | 2360 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 989 | 2075257 | 37.3916 | -121.8112 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | No | No | 1909267 | 0 | EPSS Ckt | N | 2024 | A-B-C-TIME
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 14763 | 20240204 | 657 | 20240204 | 810 | 2334781 | 73 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 156 | 11230 | 37.3901 | -121.8141 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0019247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909138 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2112 | 82952112 | OCB | 2112/2 | 20240204 | 706 | 20240204 | 1529 | 2334836 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1169 | 588007 | 37.2448 | -121.7952 | Yes | Clear;32-90 F | Circuit Breaker | Normal | 24-0019200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909091 | 0 | Non-EPSS | N | 2024 | GRD TIME
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | OCB | 2102/2 | 20240204 | 733 | 20240204 | 1314 | 2334935 | 260 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 5877 | 1323487 | 37.3036 | -121.8398 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019220 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909111 | 0 | Non-EPSS | N | 2024 | PH TIME
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | FUSE | 14745 | 20240204 | 745 | 20240204 | 1725 | 2335027 | 580 | Distribution Circuit | Animal | Squirrel | 41 | 9771 | 37.3083 | -121.9332 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0019478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909353 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 28565 | 20240204 | 745 | 20240205 | 1700 | 2335692 | 1995 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 283290 | 37.3979 | -121.8288 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020465 | OH | Sus | 35528891 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910291 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11885 | 20240204 | 748 | 20240204 | 910 | 2335047 | 82 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 2706 | 37.3827 | -121.8171 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019287 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909175 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 316958117927 | 20240204 | 750 | 20240207 | 1942 | 2368751 | 5032 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 100640 | 36.9877 | -121.5426 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0024710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913756 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | RECLOSER | XR098 | 20240204 | 752 | 20240204 | 1200 | 2335101 | 248 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1046 | 259408 | 37.3437 | -121.8074 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909144 | 0 | EPSS Ckt | N | 2024 | B C
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | RECLOSER | 819378 | 20240204 | 806 | 20240204 | 1840 | 2335200 | 589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2687 | 305959 | 37.4308 | -121.8637 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909154 | 0 | EPSS Ckt | N | 2024 | C PH TIME
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | TRANSFORMER | 316229030060 | 20240204 | 817 | 20240206 | 1917 | 2365635 | 3540 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 24780 | 37.3183 | -121.7978 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Arcing | 24-0023761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913144 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 11071 | 20240204 | 834 | 20240205 | 1950 | 2335467 | 2116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 218 | 461288 | 37.2781 | -121.8248 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Broken | 24-0020363 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1910191 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 43099 | 20240204 | 834 | 20240205 | 2020 | 2346468 | 2146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 278980 | 37.2755 | -121.8207 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Fuse | Burned Open | 24-0020369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910197 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | JUMPER | 2 PH WIRE DOWN | 20240204 | 835 | 20240208 | 1036 | 2356838 | 5881 | Distribution Circuit | Equipment Failure/Involved | Overhead | 220 | 92236 | 37.2972 | -121.8388 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911325 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | RECLOSER | XR240 | 20240204 | 845 | 20240204 | 1454 | 2335624 | 369 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2936 | 1083384 | 37.2512 | -121.8304 | Yes | Clear;32-90 F |  |  | 24-0019321 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909205 | 0 | Non-EPSS | N | 2024 | B & C
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 30034 | 20240204 | 848 | 20240204 | 2309 | 2335682 | 861 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1515 | 1304415 | 37.2992 | -121.8232 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0020297 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910126 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR566 | 20240204 | 848 | 20240206 | 939 | 2335670 | 2931 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 756198 | 37.2919 | -121.8284 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909209 | 0 | Non-EPSS | N | 2024 | A & C
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 28593 | 20240204 | 849 | 20240205 | 1253 | 2335685 | 1684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 48836 | 37.3916 | -121.8211 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021616 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911420 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 25157 | 20240204 | 858 | 20240207 | 1525 | 2362392 | 4707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 106033 | 37.3762 | -121.8011 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0022803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912437 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | OTHER | WIRE DOWN W/OF 11931 | 20240204 | 858 | 20240206 | 1204 | 2335800 | 3066 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1429 | 84598 | 37.4125 | -121.8761 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1910523 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 469810 | 20240204 | 900 | 20240207 | 1931 | 2335839 | 2568 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 80617 | 37.2003 | -121.7222 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019344 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1909226 | 0 | EPSS Ckt | N | 2024 | A-B-C
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 40907 | 20240204 | 900 | 20240207 | 2024 | 2341754 | 5004 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 5004 | 37.0642 | -121.5595 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0020016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909850 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | JUMPER | WIRE DOWN S/OF 316156027645 | 20240204 | 902 | 20240207 | 1326 | 2338761 | 4584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 223 | 249883 | 37.2515 | -121.822 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019743 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909591 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | JUMPER | CENTER PHASE OJ TO 15507 | 20240204 | 903 | 20240205 | 1450 | 2335869 | 1787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 257328 | 37.324 | -121.9237 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 24-0022115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1911805 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 180327 | 20240204 | 905 | 20240206 | 1743 | 2335914 | 3398 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 84950 | 37.2841 | -121.8123 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0023672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913073 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1106 | 82831106 | OCB | 1106/2 | 20240204 | 907 | 20240204 | 1322 | 2335958 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1810 | 461550 | 37.4156 | -121.888 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1909236 | 0 | Non-EPSS | N | 2024 | A- B- INST OC
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | OCB | 1111/2 | 20240204 | 917 | 20240208 | 1754 | 2335933 | 6023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2105 | 2631635 | 37.3662 | -121.8437 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019371 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909255 | 0 | EPSS Ckt | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 26297 | 20240204 | 918 | 20240205 | 103 | 2336136 | 945 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 107730 | 37.4526 | -121.8892 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911116 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | OCB | 2104/2 | 20240204 | 923 | 20240204 | 2200 | 2336199 | 757 | Distribution Circuit | Equipment Failure/Involved | Overhead | 332 | 62836 | 37.0072 | -121.557 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909269 | 0 | EPSS Ckt | N | 2024 | PH OC
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 11037 | 20240204 | 927 | 20240205 | 1928 | 2336274 | 2041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 713 | 1455233 | 37.4365 | -121.8811 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0019952 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909784 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20240204 | 928 | 20240205 | 916 | 2336305 | 1428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3357 | 173866 | 37.2332 | -121.9012 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Arcing | 24-0019388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909273 | 0 | Non-EPSS | N | 2024 | b c
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13081 | 20240204 | 930 | 20240205 | 1917 | 2336333 | 2027 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 56756 | 37.3769 | -121.815 | Yes | Overcast-Rain-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0022641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912272 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 42281 | 20240204 | 935 | 20240205 | 1405 | 2336404 | 1710 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 71820 | 37.3945 | -121.8326 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022091 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911788 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 8195 | 20240204 | 945 | 20240204 | 1812 | 2336541 | 507 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 8112 | 37.3426 | -121.7952 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910175 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316215331322 | 20240204 | 1001 | 20240204 | 1826 | 2334961 | 505 | Transformer only | Vegetation | Tree - grew into line | 14 | 7070 | 37.3529 | -121.8031 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909977 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 43067 | 20240204 | 1008 | 20240204 | 1742 | 2336914 | 454 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1362 | 37.1027 | -121.5858 | Yes | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0020601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910421 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315684629515 | 20240204 | 1029 | 20240204 | 1907 | 2337243 | 518 | Transformer only | Vegetation | Tree - grew into line | 11 | 5698 | 37.3017 | -121.9846 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Normal | 24-0020633 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1910452 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | RECLOSER | XR238 | 20240204 | 1054 | 20240207 | 1258 | 2337609 | 4426 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 3884659 | 37.3565 | -121.9077 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1909417 | 0 | Non-EPSS | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | 316128929317 | 20240204 | 1058 | 20240206 | 1812 | 2337703 | 3314 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 62966 | 37.2976 | -121.8319 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Together | 24-0023711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913103 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | TRANSFORMER | 316020433984 | 20240204 | 1211 | 20240205 | 1737 | 2338967 | 1766 | Transformer only | Equipment Failure/Involved | Overhead | 34 | 39719 | 37.4253 | -121.8717 | Yes | Strong Winds-Rain-Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0019684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1909539 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 32231 | 20240204 | 1226 | 20240205 | 1024 | 2339120 | 1318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 464 | 611552 | 37.3414 | -121.8689 | Yes | Overcast-Drizzle;32-90 F | Fuse | Normal | 24-0021750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911506 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 71013 | 20240204 | 1226 | 20240207 | 908 | 2339122 | 4122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 20610 | 37.4482 | -121.8857 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0024026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913339 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240204 | 1250 | 20240204 | 1436 | 2336631 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 400 | 42400 | 37.1263 | -121.7284 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0019749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1909597 | 0 | EPSS Ckt | N | 2024 | B & C
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 11141 | 20240204 | 1303 | 20240204 | 1326 | 2338324 | 23 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 6 | 138 | 37.1046 | -121.617 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909606 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 889515 | 20240204 | 1354 | 20240204 | 2010 | 2336292 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 9024 | 37.3584 | -121.8628 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0019901 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1909735 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20240204 | 1451 | 20240206 | 1614 | 2353388 | 2963 | Distribution Circuit | Equipment Failure/Involved | Overhead | 370 | 289943 | 37.1334 | -121.6754 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910785 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 73391 | 20240204 | 1514 | 20240205 | 2051 | 2342944 | 1777 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 42600 | 37.3634 | -121.7982 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0022714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912349 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20240204 | 1524 | 20240207 | 1554 | 2343239 | 4350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3346 | 3675418 | 37.2332 | -121.9012 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910034 | 0 | Non-EPSS | N | 2024 | GRD TIME TGT
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 75517 | 20240204 | 1526 | 20240205 | 1739 | 2356092 | 1573 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 53482 | 37.2664 | -121.8988 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1911214 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | RECLOSER | XR150 | 20240204 | 1528 | 20240205 | 1612 | 2343499 | 1484 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 879 | 1304436 | 37.2977 | -121.8704 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0022264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911917 | 0 | Non-EPSS | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 265693 | 20240204 | 1528 | 20240204 | 1926 | 2341560 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 37128 | 37.3002 | -121.991 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0020816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910634 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | OCB | 1109/2 | 20240204 | 1529 | 20240204 | 2023 | 2343523 | 294 | Distribution Circuit | 3rd Party | Other | 2999 | 881706 | 37.2332 | -121.9012 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910085 | 0 | Non-EPSS | N | 2024 | AB PHASE INST
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 26531 | 20240204 | 1531 | 20240207 | 1649 | 2343704 | 4398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 194 | 352362 | 37.2725 | -121.8988 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911023 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20240204 | 1531 | 20240205 | 1211 | 2344087 | 1240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 154432 | 37.2174 | -121.8338 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911667 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | OCB | 1101/2 | 20240204 | 1531 | 20240208 | 1235 | 2343921 | 5584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3672 | 7837651 | 37.3043 | -121.8683 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910086 | 0 | Non-EPSS | N | 2024 | NO TARGETS
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | OCB | 1114/2 | 20240204 | 1533 | 20240207 | 2033 | 2343883 | 4620 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2837 | 1556544 | 37.2332 | -121.9011 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1910041 | 0 | Non-EPSS | N | 2024 | GRD TIME TGT & LOCK OUT
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | FUSE | 27099 | 20240204 | 1535 | 20240205 | 23 | 2343892 | 528 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 520 | 274560 | 37.2472 | -121.9028 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911129 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315930028497 | 20240204 | 1536 | 20240207 | 1130 | 2343949 | 4074 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 24444 | 37.2743 | -121.8999 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 24-0024077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913364 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240204 | 1537 | 20240205 | 1233 | 2348286 | 1256 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4291 | 5389496 | 37.2814 | -121.8603 | Yes | Overcast-Rain-Strong Winds;32-90 F | Other | Arcing | 24-0020499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910322 | 0 | Non-EPSS | N | 2024 | A C
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | OCB | 1110/2 | 20240204 | 1537 | 20240206 | 1551 | 2344183 | 2894 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3609 | 6968266 | 37.3043 | -121.868 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0020401 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910228 | 0 | Non-EPSS | N | 2024 | A & B PHASE
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | OCB | 1101/2 | 20240204 | 1540 | 20240208 | 1150 | 2342343 | 5530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2818 | 1298594 | 37.2448 | -121.7956 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0020228 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910053 | 0 | Non-EPSS | N | 2024 | B & C PHASE OC
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | OCB | 5246 | 20240204 | 1540 | 20240207 | 1420 | 2344310 | 3689 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10992 | 4839752 | 37.2522 | -121.8238 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910090 | 0 | Non-EPSS | N | 2024 | PH INST
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRIP-SAVER | 13943 | 20240204 | 1540 | 20240206 | 1029 | 2363126 | 2569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 192 | 493248 | 37.3207 | -121.8423 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023189 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912708 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1115 | 82261115 | OCB | 1115/2 | 20240204 | 1542 | 20240204 | 1739 | 2345328 | 117 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 1638 | 37.341 | -121.9017 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020427 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910254 | 0 | Non-EPSS | N | 2024 | UNKNOWN
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR072 | 20240204 | 1543 | 20240205 | 1043 | 2344532 | 1140 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2574 | 2934360 | 37.2975 | -121.8379 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910265 | 0 | Non-EPSS | N | 2024 | B C GRD
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | 316006026771 | 20240204 | 1543 | 20240205 | 1432 | 2344249 | 1369 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 6845 | 37.2271 | -121.8729 | Yes | Clear-Strong Winds;32-90 F | Secondary | Arcing | 24-0022187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911862 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1115 | 82261115 | RECLOSER | XR448 | 20240204 | 1543 | 20240204 | 1739 | 2345200 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1027 | 119132 | 37.3348 | -121.9041 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910224 | 0 | Non-EPSS | N | 2024 | A & B PHASE GRD
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 20011 | 20240204 | 1543 | 20240207 | 1838 | 2344298 | 4495 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 474979 | 37.3069 | -121.7874 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0021946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911675 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316163130031 | 20240204 | 1543 | 20240208 | 1720 | 2344253 | 5857 | Transformer only | Vegetation | Tree - fell into line | 18 | 105426 | 37.3172 | -121.8204 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0023472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912907 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 11847 | 20240204 | 1544 | 20240205 | 1709 | 2344285 | 1525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 45750 | 37.2841 | -121.8976 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0022452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912094 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6917 | 20240204 | 1544 | 20240208 | 1835 | 2344284 | 5931 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 701241 | 37.2668 | -121.8834 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0023795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | No | No | 1913173 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | FUSE | 2737 | 20240204 | 1544 | 20240205 | 1539 | 2344429 | 1435 | Distribution Circuit | Vegetation | Tree - branch fell on line | 165 | 236775 | 37.2642 | -121.8715 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911911 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 2835 | 20240204 | 1544 | 20240208 | 1225 | 2344324 | 5561 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 208229 | 37.2689 | -121.9136 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911718 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1114 | 82261114 | OCB | 1114/2 | 20240204 | 1544 | 20240204 | 1932 | 2345041 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2427 | 553356 | 37.341 | -121.9017 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910252 | 0 | Non-EPSS | N | 2024 | B&C PAHSE OC
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | JUMPER | OJ E/O 17897 | 20240204 | 1547 | 20240206 | 1031 | 2362510 | 2564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 85015 | 37.2933 | -121.8935 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1912447 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 408/2 | 20240204 | 1550 | 20240205 | 1545 | 2344578 | 1435 | Distribution Circuit | Vegetation | Tree - branch fell on line | 636 | 912660 | 37.3281 | -121.9026 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911968 | 0 | Non-EPSS | N | 2024 | B PHASE GRD
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | RECLOSER | 95808 | 20240204 | 1550 | 20240205 | 1311 | 2344707 | 1281 | Distribution Circuit | Vegetation | Tree - bark fell into line | 788 | 1009428 | 37.304 | -121.8803 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911361 | 0 | Non-EPSS | N | 2024 | B & C
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 25205 | 20240204 | 1553 | 20240206 | 1024 | 2344726 | 2551 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 84183 | 37.2777 | -121.8951 | Yes | Clear;32-90 F |  |  | 24-0023148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912681 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | OCB | 1108/2 | 20240204 | 1553 | 20240204 | 2307 | 2344875 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3463 | 1502942 | 37.2332 | -121.9013 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910095 | 0 | Non-EPSS | N | 2024 | NO SCADA TARGETS
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | OCB | 2106/2 | 20240204 | 1553 | 20240205 | 1706 | 2344866 | 1513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5996 | 8707250 | 37.3226 | -121.7971 | Yes | Overcast-Rain-Strong Winds;32-90 F | Sectionalizer | Burned/flashed | 24-0020471 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910296 | 0 | Non-EPSS | N | 2024 | A C 51
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | OCB | 1110/2/NORM | 20240204 | 1554 | 20240206 | 921 | 2344954 | 2487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2090 | 1906884 | 37.2601 | -121.8898 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910156 | 0 | Non-EPSS | N | 2024 | ABC INST
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 72625 | 20240204 | 1554 | 20240205 | 1722 | 2356088 | 1528 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 53480 | 37.264 | -121.8984 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021379 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911212 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | FUSE | 72623 | 20240204 | 1554 | 20240205 | 1730 | 2356090 | 1536 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 56832 | 37.2647 | -121.8987 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911213 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | RECLOSER | XR338 | 20240204 | 1555 | 20240205 | 1038 | 2344934 | 1123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1158 | 1300434 | 37.3227 | -121.919 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0020276 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910105 | 0 | Non-EPSS | N | 2024 | A B
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41715 | 20240204 | 1557 | 20240205 | 1506 | 2344966 | 1389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 193747 | 37.3107 | -121.9181 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020612 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910433 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316120929796 | 20240204 | 1557 | 20240208 | 1638 | 2344891 | 5801 | Transformer only | Vegetation | Tree - grew into line | 6 | 34806 | 37.3107 | -121.8349 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Together | 24-0024482 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913595 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | RECLOSER | 637958 | 20240204 | 1558 | 20240206 | 1441 | 2345127 | 2803 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3884 | 3762662 | 37.2669 | -121.8218 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020524 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910347 | 0 | Non-EPSS | N | 2024 | A B C GRD
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 410/2 | 20240204 | 1558 | 20240205 | 1915 | 2345010 | 1637 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1035 | 1694295 | 37.3281 | -121.9026 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020585 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1910407 | 0 | Non-EPSS | N | 2024 | PHASE OC- INST B & C- TIME GR
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | FUSE | 11583 | 20240204 | 1558 | 20240205 | 1210 | 2344959 | 1212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 48480 | 37.3374 | -121.9248 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911630 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | 315966927302 | 20240204 | 1559 | 20240206 | 815 | 2345052 | 2416 | Transformer only | Unknown Cause | Patrol - found nothing | 16 | 38656 | 37.2417 | -121.8867 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0023006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1912589 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15741 | 20240204 | 1559 | 20240208 | 1121 | 2339557 | 5482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 43856 | 37.1992 | -121.8221 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0026154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915074 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 30927 | 20240204 | 1602 | 20240206 | 1207 | 2345217 | 2645 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 142830 | 37.2899 | -121.9228 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023153 | OH | Sus | 35528578 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912685 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316142628895 | 20240204 | 1602 | 20240206 | 2017 | 2365789 | 3135 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 53295 | 37.2861 | -121.827 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0023830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913205 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A SUB | 8225 | OCB | 405/2 | 20240204 | 1603 | 20240205 | 1832 | 2345165 | 1589 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 594 | 943866 | 37.3281 | -121.9025 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0020578 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910401 | 0 | Non-EPSS | N | 2024 | C OC TIME
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 72439 | 20240204 | 1604 | 20240206 | 710 | 2345316 | 2346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 53958 | 37.2731 | -121.8853 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912557 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315714329884 | 20240204 | 1604 | 20240208 | 1153 | 2345300 | 5509 | Transformer only | Vegetation | Tree - grew into line | 6 | 33054 | 37.3118 | -121.9742 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 24-0024599 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913669 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13489 | 20240204 | 1608 | 20240209 | 1129 | 2345489 | 6921 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 537116 | 37.3167 | -121.8442 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911878 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | FUSE | 17775 | 20240204 | 1609 | 20240205 | 1635 | s1910117 | 1466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 181784 | 37.3948 | -121.8673 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0020288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1910117 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 13097 | 20240204 | 1610 | 20240205 | 304 | 2345566 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 26814 | 37.3488 | -121.8768 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911258 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1106 | 82831106 | OCB | 1106/2 | 20240204 | 1610 | 20240205 | 1248 | 2345615 | 1238 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1810 | 2240780 | 37.4156 | -121.888 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910338 | 0 | Non-EPSS | N | 2024 | A B 50
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 4365 | 20240204 | 1612 | 20240206 | 1616 | 2345696 | 2884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 103824 | 37.3173 | -121.9596 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910826 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316117731865 | 20240204 | 1612 | 20240207 | 2217 | 2345668 | 4685 | Transformer only | Equipment Failure/Involved | Electrical Overload | 14 | 65590 | 37.3674 | -121.8368 | Yes | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken- wire on object | 24-0023388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912851 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | TRANSFORMER | 315818129570 | 20240204 | 1615 | 20240207 | 1948 | 2368753 | 4533 | Distribution Circuit | Vegetation | Tree - grew into line | 37 | 167721 | 37.303 | -121.9389 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Other | Failed/Faulted | 24-0024712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913758 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 72087 | 20240204 | 1616 | 20240206 | 2053 | 2345971 | 3157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 126280 | 37.3158 | -121.9749 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021898 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1911631 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 28563 | 20240204 | 1616 | 20240205 | 1743 | 2345988 | 1527 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 10689 | 37.3013 | -121.872 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Fuse | Burned Open | 24-0022463 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912102 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28007 | 20240204 | 1622 | 20240205 | 1449 | 2346245 | 1347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 137394 | 37.2615 | -121.8054 | Yes | Clear;32-90 F |  |  | 24-0022166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911844 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28691 | 20240204 | 1623 | 20240207 | 1526 | 2346154 | 4263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 85260 | 37.2976 | -121.997 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911714 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20240204 | 1626 | 20240205 | 1024 | 2346381 | 1078 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 33418 | 37.1602 | -121.666 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Fuse | Burned Open | 24-0021161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910986 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315925728695 | 20240204 | 1627 | 20240204 | 1655 | 2336730 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 336 | 37.2797 | -121.9015 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Service conductor | Broken | 24-0020176 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1910003 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | TRANSFORMER | 316160030028 | 20240204 | 1629 | 20240208 | 1232 | 2346386 | 5523 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 60753 | 37.3171 | -121.8215 | Yes | Strong Winds-Rain-Overcast;32-90 F | Other | Broken- wire on ground | 24-0023512 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912934 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 70383 | 20240204 | 1630 | 20240205 | 1054 | 2346441 | 1104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 263 | 290129 | 37.3101 | -121.9305 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0021789 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911542 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13947 | 20240204 | 1631 | 20240206 | 1112 | 2346941 | 2561 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 64025 | 37.3192 | -121.8576 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023217 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912725 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315915628420 | 20240204 | 1631 | 20240208 | 1454 | 2346134 | 5663 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 62429 | 37.2721 | -121.9049 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0021845 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911587 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | RECLOSER | XR064 | 20240204 | 1633 | 20240208 | 109 | 2346606 | 4836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 518607 | 37.2239 | -121.7797 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0020434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1910260 | 0 | EPSS Ckt | N | 2024 | A B C
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | OCB | 2105/2 | 20240204 | 1633 | 20240206 | 2043 | 2346237 | 3107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2144 | 2939158 | 37.3035 | -121.8398 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1910250 | 0 | Non-EPSS | N | 2024 | G- C- 50 & SET A TRIP
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 42225 | 20240204 | 1633 | 20240207 | 1200 | 2356825 | 4047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 133551 | 37.2909 | -121.8492 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1911324 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 14773 | 20240204 | 1638 | 20240208 | 1800 | 2346911 | 5842 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 97726 | 37.2771 | -121.8985 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0021976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911701 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 75209 | 20240204 | 1655 | 20240206 | 1338 | 2347721 | 2683 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 50977 | 37.3055 | -121.944 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0021871 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911608 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | FUSE | 72847 | 20240204 | 1727 | 20240205 | 1143 | 2348875 | 1096 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 23016 | 37.3428 | -121.88 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911637 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 72477 | 20240204 | 1729 | 20240205 | 1903 | 2348983 | 1534 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 125788 | 37.3115 | -121.9457 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0022631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912261 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | INTERRUPTER | 32134 | 20240204 | 1746 | 20240205 | 1727 | 2361156 | 1421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 194677 | 37.3011 | -121.8585 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912083 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316212031881 | 20240204 | 1800 | 20240208 | 1132 | 2350034 | 5372 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 32232 | 37.3682 | -121.8044 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0024104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913376 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | RECLOSER | 685706 | 20240204 | 1808 | 20240205 | 1544 | 2352764 | 1296 | Distribution Circuit | Vegetation | Tree - branch fell on line | 432 | 559872 | 37.2884 | -121.8822 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1910755 | 0 | Non-EPSS | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11939 | 20240204 | 1814 | 20240205 | 1508 | 2350553 | 1254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 130866 | 37.2222 | -121.8624 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911842 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20240204 | 1817 | 20240207 | 2222 | 2350572 | 4565 | Distribution Circuit | Equipment Failure/Involved | Overhead | 401 | 280672 | 37.1438 | -121.669 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1911278 | 0 | EPSS Ckt | N | 2024 | A- B & TIME
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 12143 | 20240204 | 1915 | 20240205 | 1132 | 2351651 | 977 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3908 | 37.1059 | -121.662 | Yes | Clear;32-90 F |  |  | 24-0021893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911628 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 18275 | 20240204 | 1920 | 20240207 | 1232 | 2353129 | 3912 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 23472 | 37.4198 | -121.7824 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0024307 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913507 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240204 | 1955 | 20240206 | 1705 | 2364432 | 2710 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 400 | 1084000 | 37.1263 | -121.7284 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0023376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912842 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | FUSE | 70115 | 20240204 | 2046 | 20240207 | 1909 | 2354067 | 4223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 231756 | 37.2446 | -121.9039 | Yes | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0024468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913586 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316861821720 | 20240204 | 2128 | 20240209 | 317 | 2351880 | 6109 | Transformer only | Equipment Failure/Involved | Underground | 3 | 18327 | 37.0916 | -121.577 | Yes | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken | 24-0026788 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915490 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | SWITCH | 40349 | 20240204 | 2220 | 20240204 | 2230 | 2355503 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 120 | 36.966 | -121.5381 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0019384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911073 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 28143 | 20240204 | 2300 | 20240206 | 1958 | 2355549 | 2698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 78242 | 37.2424 | -121.8331 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 24-0023786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913167 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 14299 | 20240205 | 2 | 20240205 | 1442 | 2358320 | 880 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 103840 | 37.3637 | -121.7802 | No | Overcast-Rain;32-90 F |  |  | 24-0022085 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1911785 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315655730054 | 20240205 | 41 | 20240205 | 1205 | 2355717 | 684 | Transformer only | Environmental/External | Water | 19 | 12996 | 37.3164 | -121.9947 | No | Overcast-Drizzle;32-90 F | Service conductor | Burned Open | 24-0021362 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911196 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315933327149 | 20240205 | 144 | 20240207 | 1838 | 2356204 | 3894 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 38940 | 37.2372 | -121.898 | No | Strong Winds-Clear;32-90 F | Transformer | Broken | 24-0023049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912619 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | FUSE | 28141 | 20240205 | 216 | 20240207 | 1535 | 2356316 | 3679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 191850 | 37.2451 | -121.8417 | No | Clear;32-90 F | Jumper | Broken | 24-0022704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912338 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | OTHER | WIRE DOWN 1 SPAN SS/O K870 | 20240205 | 825 | 20240207 | 1859 | 2362536 | 3514 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1446 | 128076 | 37.2392 | -121.8251 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022816 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1912452 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 409895 | 20240205 | 849 | 20240208 | 1229 | 2358623 | 4540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 109020 | 37.0614 | -121.6655 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912698 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | JUMPER | 1 P/SW/O CGC 316109329201 | 20240205 | 950 | 20240207 | 1456 | 2358530 | 3186 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 143370 | 37.2941 | -121.839 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0021717 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1911484 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 316085333045 | 20240205 | 1005 | 20240206 | 1056 | 2358641 | 1491 | Transformer only | Vegetation | Tree - grew into line | 8 | 11928 | 37.3998 | -121.8487 | No | Clear;32-90 F | Transformer | Normal | 24-0023230 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912734 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | FUSE | 98585 | 20240205 | 1106 | 20240205 | 1142 | 2359206 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 1872 | 37.3375 | -121.8784 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0021908 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1911639 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315999730495 | 20240205 | 1139 | 20240206 | 1212 | 2359295 | 1473 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 42717 | 37.3294 | -121.877 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0023323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912802 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 786125 | 20240205 | 1224 | 20240208 | 930 | 2361260 | 4146 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 207300 | 37.3106 | -121.9758 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0024249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913464 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 64046 | 20240205 | 1250 | 20240208 | 1652 | 2359879 | 4562 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 265252 | 37.2758 | -121.8453 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023332 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1912808 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 22415 | 20240205 | 1250 | 20240206 | 1538 | 2364774 | 1608 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 102809 | 37.2789 | -121.8683 | No | Overcast-Fog;32-90 F |  |  | 24-0023549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912965 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 72925 | 20240205 | 1335 | 20240206 | 1145 | 2360021 | 1330 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 167580 | 37.3077 | -121.8887 | No | Overcast;32-90 F |  |  | 24-0023239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912741 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316214228055 | 20240205 | 1553 | 20240207 | 235 | 2360795 | 2082 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 18738 | 37.263 | -121.802 | No | Clear;32-90 F | Secondary | Normal | 24-0023931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913292 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0408 | 82250408 | TRANSFORMER | 315957029926 | 20240205 | 1609 | 20240206 | 1659 | 2360904 | 1490 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 5960 | 37.3135 | -121.8914 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Deteriorated | 24-0023615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913022 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | OTHER | J3123 TWD C2079 | 20240205 | 1717 | 20240207 | 1650 | 2364849 | 2689 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 132257 | 37.3208 | -121.8034 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0023535 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1912953 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | OCB | 1101/2/NORM | 20240205 | 1849 | 20240207 | 1817 | 2358374 | 1969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11467 | 1375087 | 37.2601 | -121.89 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0022627 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912256 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 65845 | 20240205 | 2023 | 20240209 | 1106 | 2365893 | 5203 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 11057 | 37.3144 | -121.8657 | No | Partly Cloudy;32-90 F | Bus | Deteriorated | 24-0023877 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913248 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316776720346 | 20240205 | 2127 | 20240208 | 936 | 2362257 | 3609 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 3609 | 37.0536 | -121.6056 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0023868 | OH | Sus | 35528891 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913241 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 40889 | 20240205 | 2211 | 20240206 | 350 | 2362549 | 339 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 54579 | 37.256 | -121.9011 | No | Clear;32-90 F |  |  | 24-0022900 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912536 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316189528145 | 20240206 | 521 | 20240208 | 1745 | 2362979 | 3624 | Transformer only | Equipment Failure/Involved | Electrical Overload | 12 | 43488 | 37.2654 | -121.8104 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0023951 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913306 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316184732188 | 20240206 | 549 | 20240207 | 2026 | 2363005 | 2317 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 13902 | 37.3765 | -121.814 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0023898 | OH | Sus | 35528891 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913264 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316194332255 | 20240206 | 721 | 20240208 | 1244 | 2363165 | 3203 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 6406 | 37.3784 | -121.8108 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024141 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913402 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | OCB | 2101/2 | 20240206 | 924 | 20240206 | 938 | 2363420 | 14 | Distribution Circuit | Vegetation | Tree - fell into line | 4036 | 56504 | 37.3036 | -121.8398 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912641 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316024230905 | 20240206 | 950 | 20240206 | 1400 | 2358844 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4850 | 37.3407 | -121.8686 | No | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 24-0023082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912642 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | JUMPER | OJ | 20240206 | 1043 | 20240207 | 137 | 2366020 | 894 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 161070 | 37.3745 | -121.7987 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0023920 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913284 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 316012333498 | 20240206 | 1136 | 20240208 | 1509 | 2364133 | 3093 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 62476 | 37.4119 | -121.8742 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024450 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913579 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 43157 | 20240206 | 1159 | 20240206 | 1656 | 2335983 | 297 | Distribution Circuit | Vegetation | Tree - grew into line | 119 | 35343 | 37.3904 | -121.8326 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Together | 24-0023272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912765 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28259 | 20240206 | 1214 | 20240206 | 1343 | 2364264 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 356 | 37.116 | -121.6878 | No | Clear;32-90 F |  |  | 24-0023324 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1912803 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315999730495 | 20240206 | 1229 | 20240207 | 1534 | 2364318 | 1625 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 47125 | 37.3294 | -121.877 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 24-0024466 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913585 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 96741 | 20240206 | 1248 | 20240206 | 1306 | 2364404 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 54 | 37.3208 | -121.8762 | No | Partly Cloudy;32-90 F |  |  | 24-0023364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1912834 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | OCB | 1105/2 | 20240206 | 1317 | 20240207 | 1640 | 2364383 | 1622 | Distribution Circuit | Vegetation | Tree - grew into line | 2208 | 139242 | 37.341 | -121.9019 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Together | 24-0023399 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1912862 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 558681 | 20240206 | 1502 | 20240207 | 1653 | 2364807 | 1551 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 303996 | 37.2983 | -121.983 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0024020 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913336 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315967529648 | 20240206 | 1603 | 20240208 | 1704 | 2365030 | 2941 | Transformer only | Vegetation | Tree - fell into line | 10 | 29410 | 37.306 | -121.8877 | No | Partly Cloudy;32-90 F | Anchor or Guy | Normal | 24-0026071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915037 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 3695 | 20240206 | 1723 | 20240208 | 1417 | 2365756 | 2694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 84744 | 37.1029 | -121.725 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024132 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1913396 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13955 | 20240206 | 1832 | 20240206 | 1842 | 2365560 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 429 | 4290 | 37.3265 | -121.8473 | No | Partly Cloudy;32-90 F |  |  | 24-0023727 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913118 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2113 | 82832113 | OCB | 2113/2 | 20240206 | 2219 | 20240208 | 1133 | 2365928 | 278 | Distribution Circuit | Equipment Failure/Involved | Underground | 1585 | 442236 | 37.4156 | -121.8882 | No | Partly Cloudy;32-90 F | Switch (UG) | Failed/Faulted | 24-0023907 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913271 | 0 | Non-EPSS | N | 2024 | 50 G & B
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15911 | 20240207 | 39 | 20240207 | 55 | 2366007 | 16 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 704 | 37.1925 | -121.8011 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Arcing | 24-0023918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913282 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 13647 | 20240207 | 404 | 20240207 | 1112 | 2366068 | 428 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 17120 | 37.4049 | -121.8779 | No | Overcast;32-90 F |  |  | 24-0024153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913408 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 33306 | 20240207 | 758 | 20240208 | 1711 | 2366378 | 1993 | Distribution Circuit | Equipment Failure/Involved | Underground | 154 | 57504 | 37.3029 | -121.8071 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0024203 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913440 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 15431 | 20240207 | 828 | 20240207 | 1121 | 2366447 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 865 | 37.38 | -121.7965 | No | Overcast-Drizzle;32-90 F |  |  | 24-0024172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913422 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0407 | 82250407 | TRANSFORMER | 315896630385 | 20240207 | 857 | 20240208 | 1940 | 2366523 | 2083 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 29162 | 37.3259 | -121.9123 | No | Overcast-Rain;32-90 F | Jumper | Deteriorated | 24-0026556 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915277 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316189428083 | 20240207 | 913 | 20240208 | 1846 | 2366583 | 2013 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 54351 | 37.2637 | -121.8104 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0025936 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1914956 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 26801 | 20240207 | 918 | 20240207 | 1451 | 2366402 | 333 | Distribution Circuit | Vegetation | Tree - grew into line | 62 | 20646 | 37.3011 | -121.9751 | No | Overcast;32-90 F | Secondary | Together | 24-0023982 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913317 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315851829733 | 20240207 | 930 | 20240207 | 1707 | 2366633 | 457 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 16 | 7312 | 37.3077 | -121.9273 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0024597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913668 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 55397 | 20240207 | 930 | 20240207 | 1200 | 2338564 | 150 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 10050 | 37.3623 | -121.8647 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0024040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913344 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 71015 | 20240207 | 1022 | 20240207 | 2049 | 2366813 | 627 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 6270 | 37.3274 | -121.7665 | No | Overcast-Rain;32-90 F |  |  | 24-0024733 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315801929594 | 20240207 | 1113 | 20240207 | 1404 | 2367008 | 171 | Transformer only | Vegetation | Tree - grew into line | 12 | 2052 | 37.3038 | -121.9445 | No | Overcast;32-90 F | Secondary | Normal | 24-0024162 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913415 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | SWITCH | 43009 | 20240207 | 1124 | 20240207 | 1958 | 2367032 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 610 | 54745 | 37.0565 | -121.6616 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0023974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913423 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316015926290 | 20240207 | 1152 | 20240207 | 1556 | 2367121 | 244 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 1220 | 37.2139 | -121.8694 | No | Overcast-Rain;32-90 F | Secondary | Normal | 24-0024214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913447 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316238432339 | 20240207 | 1249 | 20240208 | 2111 | 2367286 | 1942 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6470 | 37.3808 | -121.7956 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024577 | OH | Sus | 35528891 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913651 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 28005 | 20240207 | 1303 | 20240207 | 1552 | 2367336 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3549 | 37.2132 | -121.8694 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0024288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913492 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315930828678 | 20240207 | 1333 | 20240208 | 1724 | 2367239 | 1671 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 26736 | 37.2793 | -121.8997 | No | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 24-0026515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915244 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316164227639 | 20240207 | 1517 | 20240207 | 1826 | 2367879 | 189 | Transformer only | Company Initiated | Return Circuit Normal | 14 | 2646 | 37.2513 | -121.8189 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0024671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913728 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 71353 | 20240207 | 1556 | 20240207 | 1906 | 2367992 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 15960 | 37.305 | -121.9924 | No | Clear;32-90 F |  |  | 24-0024677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1913733 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | JUMPER | OJ BET 68599 AND 68892 | 20240207 | 1559 | 20240207 | 1653 | 2368000 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 773 | 41742 | 37.3519 | -121.8239 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0024530 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Open Circuit | 0 | No | No | No | 1913620 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315999730495 | 20240207 | 1640 | 20240209 | 332 | 2367938 | 2092 | Transformer only | Equipment Failure/Involved | Overhead | 29 | 60668 | 37.3294 | -121.877 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024586 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913657 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316868218361 | 20240207 | 1705 | 20240207 | 1819 | 2368271 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 39 | 2886 | 36.9993 | -121.5734 | No | Clear;32-90 F |  |  | 24-0024652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1913711 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 18723 | 20240207 | 1727 | 20240207 | 1817 | 2368249 | 50 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 450 | 37.3919 | -121.8435 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0024573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1913648 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316098130492 | 20240207 | 2347 | 20240208 | 31 | 2363032 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 30 | 1320 | 37.3297 | -121.843 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0025212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914237 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | FUSE | 16181 | 20240208 | 144 | 20240208 | 636 | 2369056 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 876 | 37.3045 | -121.8524 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0025331 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914353 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | SWITCH | 9870 | 20240208 | 155 | 20240208 | 259 | 2369061 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 825 | 9886 | 37.2268 | -121.7853 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020434 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1914470 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316787722661 | 20240208 | 229 | 20240208 | 358 | 2369081 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 89 | 37.1173 | -121.6028 | No | Overcast-Fog;32-90 F | Transformer (OH) | Arcing | 24-0025596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914617 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | SWITCH | 67330 | 20240208 | 652 | 20240209 | 1151 | 2369084 | 1716 | Distribution Circuit | Equipment Failure/Involved | Underground | 51 | 87516 | 37.3614 | -121.8905 | No | Clear;32-90 F | Transformer (UG) | Contaminated | 24-0025950 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1914966 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | T25721 | 20240208 | 712 | 20240208 | 949 | 2369170 | 157 | Transformer only | 3rd Party | Other | 2 | 314 | 37.3123 | -121.9737 | No | Partly Cloudy;32-90 F | Other | Normal | 24-0026087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915047 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316168928564 | 20240208 | 911 | 20240208 | 1212 | 2353136 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 2896 | 37.277 | -121.8179 | No | Partly Cloudy;32-90 F | Secondary | Together | 24-0026041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915016 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 100000071187 | 20240208 | 915 | 20240208 | 927 | 2369128 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 84 | 37.2904 | -121.8858 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0026055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915023 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41741 | 20240208 | 1125 | 20240208 | 1151 | 2369810 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 832 | 37.299 | -121.9136 | No | Partly Cloudy;32-90 F | Service conductor | Bent or Twisted | 24-0026174 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915080 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316206428222 | 20240208 | 1144 | 20240208 | 1458 | 2369949 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1746 | 37.2704 | -121.8049 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0026234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915109 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | JUMPER | FLYING BELLS AT 2534 MAYWOOD AVE | 20240208 | 1148 | 20240208 | 1300 | 2369957 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 4680 | 37.3093 | -121.9384 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0026086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915111 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 25677 | 20240208 | 1157 | 20240208 | 1854 | 2369988 | 417 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2502 | 36.9771 | -121.5639 | No | Partly Cloudy;32-90 F |  |  | 24-0026501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915235 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2114 | 83802114 | INTERRUPTER | 43464 | 20240208 | 1212 | 20240210 | 108 | 2370050 | 2216 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2216 | 37.397 | -121.9353 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0026263 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915124 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 27191 | 20240208 | 1313 | 20240208 | 1513 | 2370216 | 120 | Distribution Circuit | 3rd Party | Other | 1 | 120 | 37.1481 | -121.6319 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0026446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915204 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | T10525 | 20240208 | 1407 | 20240209 | 1936 | 2370322 | 1769 | Transformer only | Environmental/External | Water | 15 | 26535 | 37.2673 | -121.9216 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0026357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915176 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 75926 | 20240208 | 1450 | 20240208 | 2222 | 2369645 | 452 | Distribution Circuit | Equipment Failure/Involved | Underground | 127 | 17647 | 37.3499 | -121.8281 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0025133 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915250 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315887128396 | 20240208 | 1632 | 20240208 | 1718 | 2370564 | 46 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 28 | 1288 | 37.2714 | -121.9147 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0026518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915247 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 72537 | 20240208 | 1632 | 20240208 | 1712 | 2370714 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 1080 | 37.3188 | -121.822 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915246 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2109 | 83892109 | TRANSFORMER | T11464 | 20240208 | 1728 | 20240209 | 1349 | 2370721 | 1221 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2442 | 37.3933 | -121.8899 | No | Partly Cloudy;32-90 F |  |  | 24-0026522 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1915253 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316127030376 | 20240208 | 1822 | 20240209 | 1652 | 2370810 | 1350 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 13500 | 37.3266 | -121.833 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026636 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915353 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20240209 | 206 | 20240209 | 400 | 2371115 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 510 | 58140 | 37.3557 | -121.83 | No | Clear;32-90 F |  |  | 24-0026790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1915493 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 8001 | 20240209 | 751 | 20240209 | 1043 | 2371211 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 9851 | 37.3237 | -121.8347 | No | Partly Cloudy;32-90 F |  |  | 24-0026886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915544 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | FUSE | 75241 | 20240209 | 1051 | 20240210 | 1323 | 2371574 | 1592 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4776 | 37.3249 | -121.861 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0027149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915678 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | OTHER | J6254 TWD J5976 | 20240209 | 1201 | 20240209 | 1847 | 2371689 | 406 | Distribution Circuit | Equipment Failure/Involved | Underground | 145 | 33718 | 37.3182 | -121.8458 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0022208 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915588 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 3705 | 20240209 | 1405 | 20240209 | 1415 | 2371929 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 10 | 37.2984 | -121.8553 | No | Partly Cloudy;32-90 F |  |  | 24-0027076 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915633 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 43243 | 20240209 | 1418 | 20240209 | 1616 | 2371951 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 18290 | 37.3478 | -121.8572 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0027079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915635 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | TRANSFORMER | 315850630659 | 20240209 | 1450 | 20240209 | 1840 | 2371605 | 230 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 920 | 37.3332 | -121.9283 | No | Overcast;32-90 F | Transformer | Deteriorated | 24-0027109 | OH | Sus | 35528891 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915653 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 316170034635 | 20240209 | 1451 | 20240210 | 1415 | 2371986 | 1404 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 1404 | 37.4436 | -121.8205 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0027142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915671 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315892228521 | 20240209 | 1455 | 20240209 | 1841 | 2372002 | 226 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 2712 | 37.2748 | -121.913 | No | Partly Cloudy;32-90 F |  |  | 24-0027089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915641 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 2829 | 20240209 | 1550 | 20240209 | 1712 | 2372044 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 4485 | 37.2683 | -121.914 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0027101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915648 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | TRANSFORMER | 316114927362 | 20240209 | 1653 | 20240209 | 1810 | 2372163 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 616 | 37.2437 | -121.8357 | No | Clear;32-90 F | Secondary | Broken | 24-0027146 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915675 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 63858 | 20240210 | 935 | 20240210 | 2243 | 2372557 | 672 | Distribution Circuit | Equipment Failure/Involved | Underground | 23 | 15274 | 37.02 | -121.5992 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0027354 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915826 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315954128196 | 20240210 | 1008 | 20240210 | 1104 | 2372591 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 840 | 37.2661 | -121.8914 | No | Clear;32-90 F | Secondary | Normal | 24-0027335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915819 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 70299 | 20240210 | 1009 | 20240210 | 1130 | 2372571 | 81 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 114 | 9234 | 37.3524 | -121.8118 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915814 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 12461 | 20240210 | 1038 | 20240210 | 1415 | 2372637 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 217 | 37.44 | -121.8264 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0027349 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915823 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | TRANSFORMER | T22677 | 20240210 | 1543 | 20240211 | 1151 | 2372868 | 1208 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 6040 | 37.2829 | -121.8707 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0027449 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915890 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316143726140 | 20240210 | 1618 | 20240210 | 1710 | 2372891 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 104 | 37.2115 | -121.8255 | No | Clear;32-90 F | Secondary | Broken | 24-0027442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1915882 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 316216931021 | 20240210 | 1735 | 20240211 | 528 | 2372946 | 713 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 5161 | 37.3447 | -121.8024 | No | Clear;32-90 F | Secondary | Burned Open | 24-0027557 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915994 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 33306 | 20240210 | 1844 | 20240210 | 1931 | 2373006 | 47 | Distribution Circuit | Equipment Failure/Involved | Underground | 154 | 6778 | 37.3029 | -121.8071 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0027111 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1915897 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | MTR#1007368359 | 20240211 | 1122 | 20240212 | 1141 | 2373283 | 1459 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 17508 | 37.3258 | -121.8738 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027603 | OH | Sus | 46189701 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1916031 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315790230510 | 20240211 | 1423 | 20240211 | 1451 | 2373348 | 28 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 252 | 37.3289 | -121.9487 | No | Partly Cloudy;32-90 F |  |  | 24-0027618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916041 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315795430510 | 20240211 | 1423 | 20240211 | 1455 | 2373353 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 864 | 37.3289 | -121.9471 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0027619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916042 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316140531453 | 20240211 | 1645 | 20240212 | 1414 | 2373326 | 1289 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 14179 | 37.3562 | -121.8288 | No | Clear;32-90 F | Transformer | Arcing | 24-0027639 | OH | Sus | 46189704 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916059 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 28035 | 20240212 | 634 | 20240212 | 826 | 2373581 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 672 | 37.0137 | -121.6429 | No | Clear;32-90 F |  |  | 24-0027750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1916138 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315854030812 | 20240212 | 850 | 20240212 | 1930 | 2373701 | 640 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 12628 | 37.3375 | -121.9273 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0027770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916167 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | 316691423967 | 20240212 | 1517 | 20240212 | 1635 | 2374240 | 78 | Transformer only | 3rd Party | Vehicle | 2 | 156 | 37.1526 | -121.6362 | No | Clear;32-90 F | Fuse | Broken | 24-0028065 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916304 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315740629378 | 20240213 | 307 | 20240213 | 1007 | 2374504 | 420 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 3780 | 37.2978 | -121.9653 | No | Partly Cloudy;32-90 F | Transformer (OH) | Deteriorated | 24-0028138 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916366 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316119830339 | 20240213 | 1012 | 20240213 | 1407 | 2374999 | 235 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 2820 | 37.3255 | -121.8354 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028264 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916517 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 40145 | 20240213 | 1339 | 20240214 | 1346 | 2375295 | 1166 | Distribution Circuit | Equipment Failure/Involved | Underground | 543 | 139580 | 37.266 | -121.8346 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0028462 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916598 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 12303 | 20240213 | 1558 | 20240214 | 204 | 2375426 | 606 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 16936 | 37.3644 | -121.8267 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0028575 | UG | Sus | 46190313 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916615 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | SWITCH | 909746 | 20240215 | 300 | 20240216 | 423 | 2376840 | 1523 | Distribution Circuit | Equipment Failure/Involved | Underground | 149 | 13375 | 37.3231 | -121.9112 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0029269 | UG | Sus | 31684219 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1916990 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T25253 | 20240215 | 415 | 20240215 | 1123 | 2376832 | 428 | Transformer only | Equipment Failure/Involved | Underground | 8 | 3424 | 37.3172 | -121.7746 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0029272 | UG | Sus | 46190963 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1916993 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315707829425 | 20240215 | 1857 | 20240215 | 2250 | 2377603 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1622 | 37.2992 | -121.9766 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0029694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917136 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | OCB | 2113/2 | 20240216 | 237 | 20240216 | 1523 | 2377734 | 766 | Distribution Circuit | Equipment Failure/Involved | Underground | 6037 | 961961 | 37.2448 | -121.7951 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0029739 | UG | Sus | 46191847 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917178 | 0 | EPSS Ckt | N | 2024 | GRD TIME
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315931727056 | 20240216 | 952 | 20240216 | 1350 | 2377456 | 238 | Transformer only | Vegetation | Tree - grew into line | 12 | 2856 | 37.2345 | -121.8984 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0029715 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917158 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | FUSE | 40559 | 20240216 | 1445 | 20240216 | 1527 | 2378369 | 42 | Distribution Circuit | Company Initiated | Return Circuit Normal | 615 | 25830 | 37.2531 | -121.8313 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0029739 | OH | Sus | 46191847 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917399 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | SWITCH | 28122 | 20240216 | 1458 | 20240216 | 1505 | 2378410 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 526 | 3682 | 37.256 | -121.8405 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0029739 | OH | Sus | 46191847 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1917400 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | FUSE | 75461 | 20240217 | 808 | 20240217 | 918 | 2378705 | 70 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 4103 | 37.3386 | -121.88 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0030148 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917476 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | RECLOSER | XR416 | 20240218 | 545 | 20240218 | 1242 | 2379388 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 963 | 183871 | 37.3008 | -121.9698 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917645 | 1 | Non-EPSS | N | 2024 | C GRD
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | T20546 | 20240218 | 610 | 20240218 | 1933 | 2379396 | 803 | Transformer only | Equipment Failure/Involved | Underground | 10 | 8030 | 37.2246 | -121.8545 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0030409 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917673 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316214731873 | 20240218 | 1209 | 20240218 | 2200 | 2379580 | 591 | Transformer only | Vegetation | Tree - grew into line | 6 | 3546 | 37.368 | -121.8035 | No | Clear;32-90 F | Other | Normal | 24-0030490 | OH | Sus | 46192780 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917730 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 8727 | 20240218 | 1238 | 20240218 | 1542 | 2379596 | 184 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 426 | 78384 | 37.3741 | -121.8379 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0030445 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917692 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1116 | 82921116 | SWITCH | 97758 | 20240218 | 1257 | 20240218 | 1313 | 2379634 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 315 | 3864 | 37.2954 | -121.9626 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0030367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917695 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 25881 | 20240218 | 1739 | 20240218 | 1925 | 2379881 | 106 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 3146 | 37.2225 | -121.8498 | No | Overcast-Rain;32-90 F | Transformer (UG) | Deteriorated | 24-0030410 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917740 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 14167 | 20240218 | 2053 | 20240218 | 2323 | 2380188 | 150 | Distribution Circuit | 3rd Party | Metallic Balloon | 168 | 25225 | 37.3304 | -121.8355 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 24-0030572 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917812 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 14167 | 20240218 | 2345 | 20240219 | 130 | 2380228 | 105 | Distribution Circuit | 3rd Party | Metallic Balloon | 168 | 17657 | 37.3304 | -121.8355 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Contaminated | 24-0030589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917829 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 25881 | 20240219 | 100 | 20240219 | 1051 | 2380247 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 44325 | 37.2225 | -121.8498 | No | Overcast-Heavy Rain;32-90 F | Elbow | Failed/Faulted | 24-0030689 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917915 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20240219 | 456 | 20240219 | 1332 | 2380299 | 419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3360 | 538619 | 37.2332 | -121.9012 | No | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0030611 | OH | Sus | 31684742 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917851 | 0 | Non-EPSS | N | 2024 | GRD TARGET
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 25031 | 20240219 | 655 | 20240219 | 852 | 2380388 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 195 | 37.0624 | -121.597 | No | Clear;32-90 F |  |  | 24-0030671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917898 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 28001 | 20240219 | 1014 | 20240219 | 1930 | 2380663 | 556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 166 | 92296 | 37.2101 | -121.8605 | No | Partly Cloudy-Drizzle;32-90 F | Secondary | Broken- wire on ground | 24-0030933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918103 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28259 | 20240219 | 1220 | 20240219 | 1355 | 2381094 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 380 | 37.116 | -121.6878 | No | Clear;32-90 F |  |  | 24-0030907 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918076 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6927 | 20240219 | 1240 | 20240219 | 1950 | 2381212 | 430 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1290 | 37.267 | -121.8786 | No | Clear;32-90 F |  |  | 24-0031067 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918183 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | SWITCH | 416981 | 20240219 | 1337 | 20240219 | 1344 | 2381460 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 448 | 3136 | 37.2665 | -121.9087 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0030611 | OH | Sus | 31684742 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1918055 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | FUSE | 28717 | 20240219 | 1341 | 20240219 | 2239 | 2381190 | 538 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 145 | 78010 | 37.2452 | -121.8131 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0030973 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918118 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 42601 | 20240219 | 1346 | 20240219 | 2248 | 2381500 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3212 | 37.1602 | -121.666 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0030940 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918099 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 27987 | 20240219 | 1355 | 20240219 | 1919 | 2381544 | 324 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 10368 | 37.2229 | -121.8763 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0031061 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918177 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | TRANSFORMER | 316080327549 | 20240219 | 1400 | 20240219 | 1911 | 2381376 | 311 | Transformer only | Environmental/External | Water | 11 | 3421 | 37.2487 | -121.8478 | No | Clear;32-90 F | Transformer | Together | 24-0030926 | OH | Sus | 46192776 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918089 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | OCB | 1113/2 | 20240219 | 1406 | 20240220 | 1355 | 2381568 | 1429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1816 | 252121 | 37.2332 | -121.9012 | No | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0030906 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918075 | 0 | Non-EPSS | N | 2024 | PH TIME
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 14173 | 20240219 | 1417 | 20240219 | 1712 | 2381877 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 21678 | 37.2174 | -121.8338 | No | Clear-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0031014 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918144 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2102 | 83432102 | OCB | 2102/2 | 20240219 | 1438 | 20240219 | 1710 | 2381530 | 152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3915 | 438491 | 37.2332 | -121.9014 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0030927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918092 | 0 | Non-EPSS | N | 2024 | A C GRD
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | INTERRUPTER | 60902 | 20240219 | 1444 | 20240219 | 1620 | 2381647 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 327 | 31392 | 37.2508 | -121.8769 | No | Clear-Strong Winds;32-90 F |  |  | 24-0030992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918128 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315944529090 | 20240219 | 1455 | 20240219 | 1951 | 2381684 | 296 | Transformer only | Vegetation | Tree - fell into line | 11 | 3256 | 37.2906 | -121.8953 | No | Overcast;32-90 F | Secondary | Together | 24-0031071 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918186 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315873327449 | 20240219 | 1658 | 20240219 | 1856 | 2381873 | 118 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 826 | 37.2454 | -121.9189 | No | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0031013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918143 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRIP-SAVER | 70393 | 20240219 | 1718 | 20240219 | 1733 | 2381905 | 15 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 1140 | 37.2387 | -121.8485 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0031025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918153 | 0 | Non-EPSS | N | 2024 | NA
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 7027 | 20240219 | 1729 | 20240219 | 1855 | 2381913 | 86 | Distribution Circuit | 3rd Party | Metallic Balloon | 54 | 4644 | 37.3132 | -121.8777 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0031053 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918170 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | JUMPER | OJ CGC 315894129187 | 20240219 | 1843 | 20240219 | 2348 | 2382013 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4270 | 37.293 | -121.9125 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0031062 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918178 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 14299 | 20240220 | 420 | 20240220 | 604 | 2382390 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 12272 | 37.3637 | -121.7802 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0031157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918260 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315896128659 | 20240220 | 1031 | 20240220 | 1211 | 2382807 | 100 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 15 | 1500 | 37.2786 | -121.9117 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0031326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1918390 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | 316003226788 | 20240220 | 1047 | 20240220 | 1221 | 2382828 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 188 | 37.2275 | -121.8739 | No | Overcast;32-90 F | Transformer (OH) | Broken | 24-0031335 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918397 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 43221 | 20240220 | 1047 | 20240220 | 1530 | 2382832 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 849 | 37.32 | -121.9052 | No | Partly Cloudy;32-90 F |  |  | 24-0031542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1918458 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315985628338 | 20240220 | 1241 | 20240220 | 1445 | 2382978 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 2928 | 37.2702 | -121.8807 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0031426 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918422 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | VASONA-1108 | 83771108 | TRANSFORMER | 315876527585 | 20240220 | 1251 | 20240220 | 1509 | 2382987 | 138 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 16 | 2208 | 37.249 | -121.9177 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0031437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918425 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | FUSE | 44051 | 20240220 | 1359 | 20240220 | 1525 | 2383041 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 3268 | 37.2463 | -121.8855 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0031486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918443 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315774729355 | 20240220 | 1740 | 20240221 | 552 | 2383311 | 732 | Transformer only | Equipment Failure/Involved | Electrical Overload | 67 | 49044 | 37.2974 | -121.9536 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 24-0031767 | OH | Sus | 31684655 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918584 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | JUMPER | OJ @ S WHITE RD & SIENNA DR | 20240220 | 1924 | 20240221 | 258 | 2383493 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10896 | 37.3526 | -121.8155 | No | Clear;32-90 F | Secondary | Broken | 24-0031806 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1918590 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20240222 | 644 | 20240222 | 901 | 2384863 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 7672 | 37.1869 | -121.8177 | No | Clear;32-90 F |  |  | 24-0032520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919132 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 42497 | 20240222 | 924 | 20240222 | 1349 | 2385087 | 265 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 108 | 28620 | 37.3314 | -121.9439 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0032470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1919067 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | TRANSFORMER | 315965729701 | 20240222 | 1022 | 20240222 | 2326 | 2385189 | 784 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 5488 | 37.3074 | -121.8883 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0032693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919218 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240222 | 1306 | 20240222 | 1334 | 2385402 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 776 | 21728 | 37.133 | -121.6122 | No | Clear;32-90 F |  |  | 24-0032643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919188 | 0 | EPSS Ckt | N | 2024 | C- GRD
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 25463 | 20240222 | 1644 | 20240223 | 413 | 2385595 | 557 | Distribution Circuit | Equipment Failure/Involved | Underground | 360 | 207196 | 37.4277 | -121.9093 | No | Partly Cloudy;32-90 F | Transformer (UG) | Contaminated | 24-0032817 | UG | Sus | 46194254 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919253 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | RIVER OAKS-2102 | 82342102 | OCB | 2102/2 | 20240223 | 1118 | 20240223 | 1229 | 2386200 | 71 | Distribution Circuit | Company Initiated | Other Circuits | 3632 | 257872 | 37.4112 | -121.9272 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0033173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919578 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | C2228 | 20240223 | 1145 | 20240223 | 1230 | 2386244 | 45 | Transformer only | Equipment Failure/Involved | Underground | 18 | 810 | 37.2189 | -121.8755 | No | Overcast;32-90 F | Bus | Deteriorated | 24-0033192 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919587 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 17323 | 20240224 | 1005 | 20240224 | 1120 | 2386782 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 470 | 35250 | 37.3292 | -121.8503 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0033431 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919748 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317099817987 | 20240224 | 2232 | 20240225 | 2315 | 2387170 | 1483 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 8898 | 36.9899 | -121.4941 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0033577 | OH | Sus | 31685020 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919843 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | TRANSFORMER | 315926727207 | 20240225 | 1308 | 20240225 | 1833 | 2387389 | 325 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2600 | 37.2388 | -121.9003 | No | Clear;32-90 F | Transformer | Arcing | 24-0033633 | OH | Sus | 46199563 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1919896 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 27041 | 20240225 | 1802 | 20240225 | 2111 | 2387556 | 189 | Distribution Circuit | 3rd Party | Metallic Balloon | 3 | 567 | 37.1646 | -121.6934 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0033686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1919934 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | SWITCH | 7577 | 20240226 | 207 | 20240226 | 335 | 2387666 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 6512 | 37.3328 | -121.8244 | No | Partly Cloudy;32-90 F | Capacitor | Broken | 24-0033603 | OH | Sus | 31685061 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1919940 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 28853 | 20240226 | 1045 | 20240226 | 1547 | 2388043 | 302 | Distribution Circuit | Vegetation | Tree - grew into line | 99 | 29898 | 37.2985 | -121.9478 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0033817 | OH | Sus | 46199799 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920152 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0403 | 82250403 | FUSE | 25689 | 20240226 | 1410 | 20240226 | 1449 | 2388198 | 39 | Distribution Circuit | Vegetation | Tree - grew into line | 52 | 2028 | 37.3287 | -121.9172 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0033970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920195 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315974628426 | 20240226 | 1615 | 20240227 | 128 | 2388372 | 553 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 2765 | 37.2725 | -121.8846 | No | Clear;32-90 F | Secondary | Broken | 24-0034084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920220 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 14167 | 20240226 | 2220 | 20240227 | 355 | 2388563 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 505 | 169175 | 37.3304 | -121.8355 | No | Partly Cloudy;32-90 F | Jumper | Deteriorated | 24-0034110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920250 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240227 | 855 | 20240227 | 919 | 2388785 | 24 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 776 | 18624 | 37.133 | -121.6122 | No | Clear;32-90 F |  |  | 24-0034243 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920372 | 0 | EPSS Ckt | N | 2024 | C PHASE & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | JUMPER | HIGH SIDE JUMPERS @ 27901 | 20240227 | 1919 | 20240228 | 37 | 2389457 | 318 | Distribution Circuit | 3rd Party | Vehicle | 1 | 318 | 37.1463 | -121.644 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0034613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920562 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316014026477 | 20240227 | 2203 | 20240228 | 309 | 2389497 | 306 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 3672 | 37.2191 | -121.8697 | No | Clear;32-90 F | Secondary | Broken | 24-0034637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920587 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR586 | 20240228 | 1439 | 20240228 | 1541 | 2390232 | 62 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 326 | 17728 | 37.0279 | -121.5275 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0035034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920862 | 0 | EPSS Ckt | N | 2024 | B GRD
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | SWITCH | 25098 | 20240228 | 2306 | 20240228 | 2345 | 2390477 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 298 | 11416 | 37.3713 | -121.8945 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0034976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1920915 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | FUSE | 16181 | 20240229 | 334 | 20240229 | 400 | 2390504 | 26 | Distribution Circuit | Animal | Bird found | 1 | 26 | 37.3045 | -121.8524 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0035209 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1920924 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | SWITCH | 24620 | 20240229 | 700 | 20240229 | 712 | 2390591 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 30 | 275 | 37.3697 | -121.8944 | No | Overcast;32-90 F | Pole-Wood | Normal | 24-0034976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1920946 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 3579 | 20240229 | 912 | 20240229 | 1055 | 2390861 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 515 | 37.0137 | -121.6375 | No | Clear;32-90 F |  |  | 24-0035420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1921076 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20240301 | 348 | 20240301 | 1205 | 2391741 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 9753 | 37.0838 | -121.7753 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921249 | 0 | EPSS Ckt | N | 2024 | A & GRD
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 1137 | 20240301 | 925 | 20240301 | 1234 | 2391894 | 189 | Distribution Circuit | Vegetation | Tree - grew into line | 56 | 10584 | 37.3236 | -121.8321 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0035948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921277 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | T15230 | 20240301 | 953 | 20240301 | 2225 | 2391920 | 752 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1504 | 37.1233 | -121.6292 | Yes | Overcast;32-90 F | Secondary | Burned/flashed | 24-0036044 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921302 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315920735329 | 20240301 | 1000 | 20240301 | 1451 | 2391921 | 291 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 1746 | 37.4618 | -121.9067 | Yes | Overcast;32-90 F | Secondary | Broken- wire on ground | 24-0035977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921285 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316123431898 | 20240301 | 1601 | 20240301 | 1724 | 2392485 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1162 | 37.3684 | -121.8349 | Yes | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0036256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921377 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28259 | 20240301 | 1721 | 20240301 | 1820 | 2392589 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 236 | 37.116 | -121.6878 | Yes | Clear;32-90 F |  |  | 24-0036388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921433 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | JUMPER | HIGH SIDE JUMPERS AT 509329 | 20240301 | 1832 | 20240302 | 35 | 2392820 | 363 | Distribution Circuit | Company Initiated | Improper Construction | 11 | 3993 | 37.2564 | -121.9075 | Yes | Clear-Strong Winds;32-90 F | Jumper | Normal | 24-0036612 | OH | Sus | 46202031 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1921653 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 1899 | 20240301 | 1913 | 20240301 | 2153 | 2392665 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 120 | 19200 | 37.3341 | -121.7797 | Yes | Clear;32-90 F |  |  | 24-0036468 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921512 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN LEANDRO-1114 | 13111114 | JUMPER | OJ AT CGC:100000029671 | 20240301 | 1915 | 20240301 | 2016 | 2392945 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 988 | 43277 | 37.7188 | -122.1319 | Yes | Overcast-Rain;32-90 F | Jumper | Burned Open | 24-0036413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1921458 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 27067 | 20240301 | 2038 | 20240302 | 830 | 2393429 | 712 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 10680 | 37.018 | -121.5869 | Yes | Clear;32-90 F |  |  | 24-0036739 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921773 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10541 | 20240301 | 2142 | 20240302 | 7 | 2393660 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 7250 | 37.1035 | -121.6165 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0036605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921646 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28259 | 20240301 | 2200 | 20240302 | 810 | 2393783 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2440 | 37.116 | -121.6878 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0036725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921761 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | SWITCH | XR594 | 20240302 | 155 | 20240302 | 323 | -2394211 | 88 | Distribution Circuit | Company Initiated | Return Circuit Normal | 307 | 27016 | 37.0622 | -121.5882 | No | Partly Cloudy-Rain;32-90 F | Switch (OH) | Normal | 24-0036646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921703 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 37264 | 20240302 | 205 | 20240302 | 320 | 2394211 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 622 | 45168 | 37.0132 | -121.5513 | No | Overcast-Rain;32-90 F |  |  | 24-0036646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921690 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 41791 | 20240302 | 216 | 20240302 | 1025 | 2394231 | 489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 18039 | 37.3189 | -121.9634 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0036659 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921704 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1081 | 20240302 | 338 | 20240302 | 1053 | 2394300 | 435 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 16530 | 36.9982 | -121.5243 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0036850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921857 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OTHER | WIRE DOWN W/OF FUCO 4887 | 20240302 | 548 | 20240302 | 1815 | 2394389 | 747 | Distribution Circuit | Vegetation | Tree - bark fell into line | 596 | 193519 | 37.0136 | -121.6402 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036682 | OH | Sus | 31685289 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1921726 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 40566 | 20240302 | 919 | 20240302 | 1718 | 2394599 | 479 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 25866 | 37.325 | -121.8036 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0036832 | UG | Sus | 46202328 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1921844 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315918935341 | 20240302 | 1249 | 20240302 | 1350 | 2394931 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 37.4621 | -121.9074 | No | Overcast;32-90 F | Secondary | Broken | 24-0036916 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1921900 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20240302 | 1259 | 20240302 | 1943 | 2394945 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 510 | 49872 | 37.3557 | -121.83 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036958 | OH | Sus | 35535051 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1921924 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315803129365 | 20240303 | 1700 | 20240303 | 1821 | 2396275 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 1296 | 37.2975 | -121.944 | No | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0037245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922158 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 100000119260 | 20240303 | 2048 | 20240303 | 2211 | 2396365 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 581 | 37.2974 | -121.8957 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0037327 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1922232 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 71669 | 20240304 | 934 | 20240304 | 1604 | 2396632 | 390 | Distribution Circuit | 3rd Party | Vehicle | 40 | 14132 | 37.0978 | -121.6078 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0037384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922279 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40723 | 20240304 | 1040 | 20240304 | 1049 | 2396706 | 9 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 9 | 37.0643 | -121.6922 | No | Clear;32-90 F |  |  | 24-0037486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922292 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1102 | 82261102 | INTERRUPTER | 89694 | 20240304 | 1155 | 20240304 | 1802 | 2396783 | 367 | Distribution Circuit | 3rd Party | Customer Equipment | 18 | 2046 | 37.3386 | -121.8941 | No | Clear;32-90 F | Bus | Burned Open | 24-0037586 | OH | Sus | 46202982 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922314 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 27139 | 20240304 | 1840 | 20240305 | 227 | 2397126 | 467 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 11883 | 37.3219 | -121.8177 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0037623 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922362 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1113 | 83371113 | TRANSFORMER | C750 | 20240305 | 957 | 20240305 | 1019 | 2397548 | 22 | Transformer only | Equipment Failure/Involved | Underground | 21 | 462 | 37.3105 | -121.9942 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0038078 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922587 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1113 | 83371113 | TRANSFORMER | C750 | 20240305 | 1020 | 20240305 | 1112 | 2397629 | 52 | Transformer only | Equipment Failure/Involved | Underground | 21 | 1092 | 37.3105 | -121.9942 | No | Overcast;32-90 F | Transformer (UG) | Normal | 24-0038119 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922594 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | 315958227310 | 20240305 | 2055 | 20240306 | 531 | 2398002 | 516 | Transformer only | Equipment Failure/Involved | Electrical Overload | 15 | 7740 | 37.2419 | -121.8896 | No | Partly Cloudy;32-90 F | Transformer | Burned/flashed | 24-0038411 | OH | Sus | 31685677 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922682 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | JUMPER | OJ @ 2562 VAN WINKLE | 20240306 | 709 | 20240306 | 1251 | 2398139 | 342 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 6498 | 37.3509 | -121.8299 | No | Clear;32-90 F | Secondary | Arcing | 24-0038655 | OH | Sus | 46203880 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922919 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316398026275 | 20240306 | 1453 | 20240307 | 1540 | 2398654 | 1487 | Transformer only | Environmental/External | Lightning | 2 | 2974 | 37.2151 | -121.7381 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0039022 | OH | Sus | 46204066 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923058 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41527 | 20240306 | 1500 | 20240306 | 1816 | 2398228 | 196 | Distribution Circuit | Vegetation | Tree - grew into line | 98 | 19208 | 37.3378 | -121.837 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0038857 | OH | Sus | 46203891 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1922964 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | FUSE | 44812 | 20240306 | 1502 | 20240307 | 548 | 2398662 | 548 | Distribution Circuit | Equipment Failure/Involved | Underground | 368 | 161358 | 37.2236 | -121.7674 | No | Clear-Lightning;32-90 F | Conductor- Underground | Broken | 24-0038939 | UG | Sus | 46204067 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1922992 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | FUSE | 31806 | 20240306 | 1505 | 20240308 | 237 | 2398663 | 2132 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 81931 | 37.2216 | -121.7641 | No | Clear-Lightning;32-90 F | Conductor- Underground | Broken | 24-0039031 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923068 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26637 | 20240306 | 2304 | 20240307 | 1711 | 2398890 | 1087 | Distribution Circuit | 3rd Party | Vehicle | 276 | 113852 | 37.1078 | -121.6009 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0039023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1923060 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 28863 | 20240307 | 621 | 20240307 | 843 | 2398954 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 178 | 25276 | 37.3213 | -121.96 | No | Overcast;32-90 F |  |  | 24-0039104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923122 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 5915 | 20240307 | 825 | 20240307 | 1305 | 2399040 | 280 | Distribution Circuit | Animal | Squirrel | 1 | 280 | 37.3626 | -121.9043 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 24-0039330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923283 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 18593 | 20240307 | 959 | 20240307 | 1218 | 2399241 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3475 | 37.2414 | -121.8481 | No | Clear;32-90 F |  |  | 24-0039285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923275 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 5281 | 20240307 | 1114 | 20240307 | 1222 | 2399331 | 68 | Distribution Circuit | Animal | Squirrel | 8 | 544 | 37.0904 | -121.5948 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0039290 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923276 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | TRANSFORMER | T6828 | 20240307 | 1220 | 20240308 | 228 | 2399388 | 848 | Distribution Circuit | Equipment Failure/Involved | Underground | 139 | 36076 | 37.2242 | -121.7705 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0039420 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923302 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316547525440 | 20240307 | 1327 | 20240307 | 1340 | 2399440 | 13 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 52 | 37.1934 | -121.6907 | No | Partly Cloudy;32-90 F |  |  | 24-0039359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1923292 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | SWITCH | 70575 | 20240307 | 2137 | 20240308 | 150 | 2399706 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 12397 | 37.2583 | -121.7054 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0039577 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923373 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | RECLOSER | XR278 | 20240308 | 734 | 20240308 | 744 | 2399830 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2087 | 20870 | 37.2782 | -121.8789 | No | Clear;32-90 F |  |  | 24-0039642 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923411 | 0 | Non-EPSS | N | 2024 | A & C
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 5249 | 20240308 | 738 | 20240308 | 905 | 2399971 | 87 | Distribution Circuit | Animal | Bird found | 33 | 2871 | 37.3631 | -121.8766 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0039686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1923489 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 25203 | 20240308 | 1131 | 20240308 | 1350 | 2400140 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2780 | 37.3257 | -121.6679 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0039761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923559 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316089530717 | 20240308 | 2343 | 20240309 | 1550 | 2400523 | 967 | Transformer only | Equipment Failure/Involved | Electrical Overload | 12 | 11604 | 37.3358 | -121.846 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0040050 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923666 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | OCB | 1110/2 | 20240309 | 533 | 20240309 | 644 | 2400554 | 71 | Distribution Circuit | Equipment Failure/Involved | Underground | 1654 | 19966 | 37.2332 | -121.9012 | No | Overcast-Fog;32-90 F | Interrupter | Broken | 24-0029690 | UG | Sus | 35383245 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923674 | 0 | Non-EPSS | N | 2024 | C PHASE- GRD
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | OTHER | WIRE DOWN SSD CGC 316132125748 | 20240309 | 1404 | 20240309 | 2038 | 2400867 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 177 | 18463 | 37.2013 | -121.8282 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0040114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | Yes | 1923781 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 10131 | 20240309 | 2049 | 20240309 | 2059 | 2401024 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 175 | 1750 | 37.192 | -121.8007 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0040114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923820 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316126727285 | 20240310 | 12 | 20240310 | 319 | 2401035 | 187 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 2431 | 37.2416 | -121.8316 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0040170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923827 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 43043 | 20240310 | 715 | 20240310 | 930 | 2401113 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 405 | 37.1276 | -121.5997 | No | Overcast-Fog;32-90 F |  |  | 24-0040183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1923853 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 75209 | 20240311 | 1516 | 20240311 | 1937 | 2401697 | 261 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 4959 | 37.3055 | -121.944 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0040597 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924149 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20240311 | 1639 | 20240311 | 2124 | 2402049 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 48450 | 37.3339 | -121.7556 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0040409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924164 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316798223920 | 20240312 | 921 | 20240312 | 1424 | 2402576 | 303 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2424 | 37.1516 | -121.5996 | No | Overcast-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0040841 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924353 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 42775 | 20240312 | 1125 | 20240312 | 1340 | 2402686 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 5130 | 37.2714 | -121.7684 | No | Clear;32-90 F |  |  | 24-0041040 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924412 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20240312 | 2127 | 20240313 | 129 | 2403084 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 15488 | 37.0838 | -121.7753 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0041212 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924471 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 1691 | 20240312 | 2310 | 20240313 | 50 | 2403095 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 100 | 37.1593 | -121.6959 | No | Overcast;32-90 F |  |  | 24-0041268 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924496 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 26665 | 20240313 | 218 | 20240313 | 439 | 2403113 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 16638 | 37.3108 | -121.8686 | No | Partly Cloudy;32-90 F |  |  | 24-0041271 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1924499 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316398026275 | 20240313 | 901 | 20240313 | 1708 | 2403341 | 487 | Transformer only | Company Initiated | Construction Activity/equip- company | 2 | 974 | 37.2151 | -121.7381 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0041423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1924683 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41767 | 20240313 | 1629 | 20240313 | 2149 | 2403534 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 8782 | 37.2954 | -121.9467 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0041686 | OH | Sus | 31686195 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924754 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | JUMPER | FLYING BELLS @ 2147 TERILYN AVE | 20240313 | 1637 | 20240313 | 1914 | 2403756 | 157 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 2041 | 37.3243 | -121.8352 | No | Clear;32-90 F | Secondary | Normal | 24-0041666 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924748 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41765 | 20240313 | 2343 | 20240314 | 327 | 2403977 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 262 | 58688 | 37.2955 | -121.9476 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0041785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924818 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 315982234520 | 20240314 | 1211 | 20240314 | 2016 | 2405027 | 485 | Transformer only | Vegetation | Tree - bark fell into line | 15 | 7275 | 37.4398 | -121.8852 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0042309 | OH | Sus | 31686646 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1925196 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | TRANSFORMER | 100000121173 | 20240314 | 1808 | 20240314 | 2303 | 2405433 | 295 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 2360 | 37.4058 | -121.8545 | No | Clear;32-90 F | Transformer | Arcing | 24-0042427 | OH | Sus | 46211789 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925245 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240315 | 701 | 20240315 | 1014 | 2405721 | 193 | Distribution Circuit | Animal | Bird found | 577 | 33583 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0042552 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925337 | 0 | EPSS Ckt | N | 2024 | A B 51
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 71015 | 20240315 | 754 | 20240315 | 906 | 2405791 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 720 | 37.3274 | -121.7665 | No | Clear;32-90 F |  |  | 24-0042617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925414 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 2007 | 20240315 | 1026 | 20240316 | 48 | 2406141 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 52582 | 37.4359 | -121.8839 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0042752 | OH | Sus | 46212413 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925546 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T22033 | 20240315 | 1031 | 20240315 | 1737 | 2406149 | 426 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 2982 | 37.2981 | -121.7928 | No | Clear;32-90 F |  |  | 24-0043002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1925646 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | TRANSFORMER | 316033032981 | 20240315 | 1139 | 20240315 | 1901 | 2406265 | 442 | Transformer only | Vegetation | Tree - grew into line | 12 | 5304 | 37.3977 | -121.8668 | No | Clear;32-90 F | Transformer | Arcing | 24-0042739 | OH | Sus | 46212398 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925541 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 64046 | 20240315 | 1212 | 20240315 | 1501 | 2406445 | 169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 158 | 26702 | 37.2758 | -121.8453 | No | Clear;32-90 F |  |  | 24-0042842 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925589 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 8985 | 20240315 | 1217 | 20240316 | 0 | 2406450 | 690 | Distribution Circuit | Equipment Failure/Involved | Underground | 127 | 50431 | 37.3395 | -121.8221 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0042813 | UG | Sus | 35537908 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925575 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 9743 | 20240315 | 1228 | 20240315 | 1646 | 2406461 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 26316 | 37.2702 | -121.8679 | No | Clear;32-90 F |  |  | 24-0042977 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Open Circuit | 0 | No | No | No | 1925635 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 316078833024 | 20240315 | 1323 | 20240316 | 1045 | 2406091 | 1282 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 15384 | 37.3992 | -121.8509 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0042829 | OH | Sus | 46212532 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925581 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 42959 | 20240315 | 1804 | 20240315 | 2027 | 2406875 | 143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 88 | 12584 | 37.2874 | -121.9102 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0043008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925651 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | OCB | 1112/2 | 20240315 | 2146 | 20240316 | 355 | 2406972 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 2712 | 465534 | 37.3282 | -121.9025 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0043039 | OH | Sus | 31686706 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925675 | 0 | Non-EPSS | N | 2024 | A- B- C PHASE OC
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13949 | 20240316 | 657 | 20240316 | 1033 | 2407045 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 293 | 63288 | 37.3192 | -121.8566 | No | Clear;32-90 F |  |  | 24-0043113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925791 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 316079933001 | 20240316 | 1045 | 20240316 | 1103 | 2407197 | 18 | Transformer only | Equipment Failure/Involved | Substation | 18 | 324 | 37.3986 | -121.8506 | No | Clear;32-90 F | Secondary | Broken | 24-0043111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925789 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | TRANSFORMER | T5056 | 20240316 | 1122 | 20240318 | 322 | 2407231 | 2400 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 31200 | 37.2587 | -121.8181 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0043141 | UG | Sus | 31686810 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925809 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20240316 | 1440 | 20240316 | 1629 | 2407348 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 654 | 37.2181 | -121.7422 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0043143 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925822 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 2463 | 20240316 | 1620 | 20240316 | 1815 | 2407410 | 115 | Distribution Circuit | 3rd Party | Metallic Balloon | 429 | 45795 | 37.1974 | -121.8319 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043170 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1925833 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | RECLOSER | XR424 | 20240316 | 1945 | 20240317 | 1954 | 2407494 | 1449 | Distribution Circuit | Equipment Failure/Involved | Underground | 91 | 26739 | 37.0415 | -121.5856 | No | Clear;32-90 F | Insulator | Broken | 24-0043182 | UG | Sus | 31686672 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1925844 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 15137 | 20240317 | 738 | 20240317 | 1003 | 2407639 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1885 | 37.4135 | -121.843 | No | Clear;32-90 F |  |  | 24-0043234 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925913 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 4353 | 20240317 | 909 | 20240317 | 2210 | 2407672 | 781 | Distribution Circuit | Animal | Bird found | 8 | 1197 | 37.0819 | -121.6094 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043251 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925932 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 40220 | 20240317 | 1135 | 20240317 | 1845 | 2407789 | 430 | Distribution Circuit | Animal | Squirrel | 135 | 58050 | 37.3244 | -121.8065 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925954 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13949 | 20240317 | 1257 | 20240318 | 204 | 2407736 | 787 | Distribution Circuit | Animal | Squirrel | 304 | 225676 | 37.3192 | -121.8566 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0043258 | OH | Sus | 35538115 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1925944 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316134026340 | 20240317 | 1750 | 20240317 | 2020 | 2407850 | 150 | Transformer only | Animal | Squirrel | 2 | 300 | 37.2158 | -121.829 | No | Clear;32-90 F | Fuse | Burned Open | 24-0043289 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1925964 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 21261 | 20240318 | 1116 | 20240319 | 106 | 2408363 | 830 | Distribution Circuit | 3rd Party | Vehicle | 15 | 12450 | 37.267 | -121.8867 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0043540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926270 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 75165 | 20240318 | 1159 | 20240318 | 1301 | 2408464 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 62 | 37.2914 | -121.8578 | No | Clear;32-90 F |  |  | 24-0043583 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926301 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316003726686 | 20240318 | 1250 | 20240319 | 102 | 2408382 | 732 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 5856 | 37.2248 | -121.8737 | No | Clear;32-90 F | Transformer | Broken- wire on object | 24-0043600 | OH | Sus | 31686849 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1926305 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316194032378 | 20240318 | 1345 | 20240318 | 1410 | 2408508 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 25 | 37.3818 | -121.8108 | No | Clear;32-90 F | Secondary | Broken | 24-0043615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1926311 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 75319 | 20240318 | 1939 | 20240318 | 1958 | 2408841 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 741 | 37.2912 | -121.8544 | No | Clear;32-90 F |  |  | 24-0043776 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926367 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 1687 | 20240319 | 750 | 20240319 | 937 | 2408981 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 321 | 37.4318 | -121.9634 | No | Overcast;32-90 F |  |  | 24-0043961 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926577 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 17283 | 20240319 | 1027 | 20240319 | 1334 | 2409276 | 187 | Distribution Circuit | Animal | Bird found | 6 | 1122 | 37.2195 | -121.9069 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0044168 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR |  | 0 | No | No | No | 1926666 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 42161 | 20240319 | 1410 | 20240319 | 1935 | 2409487 | 325 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1557 | 37.188 | -121.7916 | No | Clear;32-90 F |  |  | 24-0044347 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926703 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 14875 | 20240320 | 636 | 20240320 | 830 | 2409860 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3990 | 37.058 | -121.5674 | No | Overcast-Fog;32-90 F |  |  | 24-0044447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1926771 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 11991 | 20240320 | 1029 | 20240321 | 335 | 2410190 | 1026 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 51 | 52326 | 37.41 | -121.8757 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0044601 | OH | Sus | 46214115 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1926952 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 1617 | 20240320 | 1219 | 20240321 | 409 | 2410328 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 318 | 121227 | 37.307 | -121.9134 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0044695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1926974 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316106831707 | 20240320 | 2100 | 20240321 | 551 | 2410583 | 531 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4248 | 37.3631 | -121.8405 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0044912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927051 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 34940 | 20240321 | 1704 | 20240321 | 2038 | 2411393 | 214 | Distribution Circuit | Equipment Failure/Involved | Underground | 325 | 43306 | 37.4259 | -121.9133 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0045324 | UG | Sus | 46214730 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927249 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315925030200 | 20240322 | 1039 | 20240322 | 1731 | 2411921 | 412 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 7416 | 37.3206 | -121.9023 | No | Partly Cloudy;32-90 F | Transformer | Leaking | 24-0034244 | OH | Sus | 35493184 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927483 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315992828926 | 20240322 | 1152 | 20240322 | 1528 | 2411961 | 216 | Transformer only | Vegetation | Tree - grew into line | 12 | 2592 | 37.2863 | -121.8786 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0045643 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927500 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRIP-SAVER | 26793 | 20240322 | 1401 | 20240322 | 1642 | 2412074 | 161 | Distribution Circuit | Vegetation | Tree - grew into line | 278 | 44758 | 37.301 | -121.9653 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0045708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927529 | 0 | Non-EPSS | N | 2024 | NO TARGETS
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 15291 | 20240322 | 1627 | 20240322 | 1853 | 2412237 | 146 | Distribution Circuit | 3rd Party | Metallic Balloon | 198 | 28908 | 37.3078 | -121.9023 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0045826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927562 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | TRANSFORMER | T10929 | 20240322 | 1812 | 20240322 | 1927 | 2412288 | 75 | Transformer only | 3rd Party | Fire- house or bldg. | 20 | 1500 | 37.3766 | -121.8447 | No | Overcast-Drizzle;32-90 F | Transformer (UG) | Normal | 24-0045831 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927568 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | FUSE | 25893 | 20240322 | 2000 | 20240322 | 2200 | 2412358 | 120 | Distribution Circuit | Company Initiated | Operating error | 2195 | 210302 | 37.3107 | -121.939 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0045836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927573 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | SWITCH | 612460 | 20240323 | 51 | 20240323 | 1114 | 2412505 | 623 | Distribution Circuit | 3rd Party | Vehicle | 422 | 29386 | 37.4256 | -121.9738 | No | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken | 24-0045820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1927619 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20240323 | 111 | 20240323 | 308 | 2412511 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4240 | 249694 | 37.4156 | -121.8881 | No | Overcast-Drizzle;32-90 F |  |  | 24-0045888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1927623 | 0 | EPSS Ckt | N | 2024 | B & C
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 17501 | 20240323 | 452 | 20240323 | 800 | 2412580 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 752 | 37.0742 | -121.5572 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0045935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927669 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315919930345 | 20240324 | 825 | 20240324 | 1013 | 2413306 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 648 | 37.325 | -121.9043 | No | Overcast;32-90 F |  |  | 24-0046164 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | None | 0 | No | No | No | 1927880 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 46052 | 20240324 | 919 | 20240325 | 154 | 2413332 | 995 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 21893 | 37.2055 | -121.8264 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0046168 | UG | Sus | 46215804 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1927882 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | TRANSFORMER | T21185 | 20240325 | 1047 | 20240326 | 158 | 2414133 | 911 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 9166 | 37.3984 | -121.9089 | No | Overcast;32-90 F | Transformer (UG) | Deteriorated | 24-0046499 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928182 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1102 | 82261102 | INTERRUPTER | 45938 | 20240326 | 1215 | 20240326 | 1443 | 2415643 | 148 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 396 | 58608 | 37.3379 | -121.8875 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0047035 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928532 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | OCB | 1107/2 | 20240326 | 1928 | 20240327 | 39 | 2415980 | 311 | Distribution Circuit | 3rd Party | Vehicle | 4048 | 1258928 | 37.3662 | -121.8438 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0047155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928568 | 0 | EPSS Ckt | N | 2024 | 50 & GRD
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | OCB | 1111/2 | 20240326 | 1928 | 20240327 | 37 | s1928636 | 309 | Distribution Circuit | 3rd Party | Vehicle | 3541 | 812099 | 37.3662 | -121.8437 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0047155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1928636 | 0 | EPSS Ckt | N | 2024 | 50 & GRD
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | JUMPER | OPEN JUMPERS IRO 1203 CHERRY AVE | 20240327 | 1324 | 20240327 | 1544 | 2416485 | 140 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 2940 | 37.3039 | -121.9059 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0047500 | OH | Sus | 46216967 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1928846 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41761 | 20240329 | 1030 | 20240329 | 1755 | 2417511 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 11570 | 37.3027 | -121.961 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048326 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929385 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 315999833419 | 20240329 | 1207 | 20240330 | 649 | 2418085 | 1122 | Transformer only | Vegetation | Tree - grew into line | 3 | 3366 | 37.4096 | -121.8784 | No | Overcast;32-90 F | Transformer | Arcing | 24-0048470 | OH | Sus | 31689156 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929432 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | T750 | 20240329 | 1218 | 20240329 | 2219 | 2418092 | 601 | Transformer only | Equipment Failure/Involved | Underground | 3 | 1803 | 37.354 | -121.8906 | No | Overcast;32-90 F | Secondary | Normal | 24-0048457 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929428 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315963131387 | 20240329 | 1301 | 20240329 | 2217 | 2418084 | 556 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 4448 | 37.3538 | -121.8901 | No | Overcast;32-90 F | Secondary | Broken | 24-0048448 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929423 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11883 | 20240329 | 1507 | 20240330 | 440 | 2418284 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 16785 | 37.3825 | -121.8166 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0048537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | Yes | No | 1929451 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1106 | 82831106 | FUSE | 6057 | 20240329 | 1613 | 20240330 | 620 | 2418342 | 847 | Distribution Circuit | Equipment Failure/Involved | Underground | 210 | 38105 | 37.4184 | -121.8665 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0048551 | UG | Sus | 46218285 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929458 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | RECLOSER | XR060 | 20240329 | 1803 | 20240329 | 1814 | 2418428 | 11 | Distribution Circuit | 3rd Party | Metallic Balloon | 1374 | 15114 | 37.3288 | -121.8324 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0048573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1929466 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316116231224 | 20240329 | 1858 | 20240329 | 2051 | 2418498 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 2373 | 37.3498 | -121.8371 | No | Partly Cloudy-Rain;32-90 F | Fuse | Broken | 24-0048601 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929485 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OCB | 2107/2 | 20240330 | 1204 | 20240330 | 2109 | 2419031 | 545 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3943 | 324553 | 37.0071 | -121.5569 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0048766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1929607 | 0 | EPSS Ckt | N | 2024 | A & G TIME
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 28903 | 20240330 | 1547 | 20240330 | 1725 | 2419147 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 93 | 9114 | 37.3168 | -121.838 | No | Clear;32-90 F |  |  | 24-0048833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929648 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | INTERRUPTER | 1359 | 20240331 | 750 | 20240401 | 45 | 2419442 | 885 | Distribution Circuit | Equipment Failure/Involved | Underground | 1534 | 322872 | 37.2383 | -121.8396 | No | Partly Cloudy;32-90 F | Switch (UG) | Broken | 24-0048900 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929710 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | TRANSFORMER | 315929031854 | 20240331 | 911 | 20240331 | 1140 | 2419463 | 149 | Transformer only | Animal | Squirrel | 2 | 298 | 37.3664 | -121.902 | No | Overcast;32-90 F | Transformer (OH) |  | 24-0048913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929723 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20240331 | 1105 | 20240331 | 2322 | 2419501 | 737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 402 | 35644 | 37.1438 | -121.669 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0048911 | OH | Sus | 31689262 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1929721 | 0 | EPSS Ckt | N | 2024 | A PHASE GRD
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | SWITCH | 40220SW | 20240401 | 54 | 20240401 | 206 | 2419784 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 9720 | 37.3244 | -121.8064 | No | Partly Cloudy;32-90 F | Jumper | Normal | 24-0048967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929785 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 45222 | 20240401 | 638 | 20240402 | 153 | 2419818 | 924 | Distribution Circuit | Equipment Failure/Involved | Underground | 240 | 97275 | 37.2137 | -121.8489 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0049003 | UG | Sus | 46218729 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929822 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 26195 | 20240401 | 810 | 20240401 | 913 | 2419882 | 63 | Distribution Circuit | Animal | Squirrel | 78 | 4916 | 37.3182 | -121.92 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0049041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929885 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 20007 | 20240401 | 840 | 20240401 | 925 | 2419943 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 45 | 37.0384 | -121.5709 | No | Clear;32-90 F |  |  | 24-0049060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1929919 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | TRANSFORMER | 316904717718 | 20240401 | 952 | 20240401 | 1208 | 2420090 | 136 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 136 | 36.9818 | -121.5609 | No | Clear-Drizzle;32-90 F |  |  | 24-0049161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1929973 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 63366 | 20240401 | 1911 | 20240402 | 1325 | 2420486 | 513 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 28094 | 37.3934 | -121.902 | No | Clear;32-90 F | Bus | Burned/flashed | 24-0049450 | UG | Sus | 46218892 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930079 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 25447 | 20240401 | 1955 | 20240401 | 2122 | 2420508 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 783 | 37.1539 | -121.687 | No | Clear;32-90 F |  |  | 24-0049423 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930048 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317053618537 | 20240401 | 2210 | 20240401 | 2222 | 2420500 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 36 | 37.005 | -121.51 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0049447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930077 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1116 | 82261116 | OCB | 1116/2 | 20240402 | 1356 | 20240402 | 1406 | 2421104 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1087 | 10870 | 37.341 | -121.9017 | No | Clear;32-90 F | Capacitor | Arcing | 24-0049785 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930330 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315949628706 | 20240402 | 1454 | 20240402 | 1635 | 2421153 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 909 | 37.2802 | -121.8932 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0049854 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930340 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316184331223 | 20240402 | 2103 | 20240403 | 542 | 2421315 | 519 | Transformer only | 3rd Party | Vehicle | 15 | 7785 | 37.3504 | -121.814 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0049949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930372 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5241 | 20240403 | 140 | 20240403 | 1538 | 2421440 | 838 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 10056 | 37.1092 | -121.6815 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0049987 | UG | Sus | 46219660 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930415 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | TRANSFORMER | C3045 | 20240403 | 736 | 20240403 | 1043 | 2421713 | 179 | Distribution Circuit | Equipment Failure/Involved | Underground | 431 | 15679 | 37.3787 | -121.8551 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0050105 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1930586 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 4253 | 20240403 | 1009 | 20240403 | 1202 | 2421703 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 565 | 37.0457 | -121.7231 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 24-0050098 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930582 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 3053 | 20240403 | 1317 | 20240403 | 1457 | 2421886 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 300 | 36.9487 | -121.5156 | No | Clear;32-90 F |  |  | 24-0050314 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1930641 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | SWITCH | 35252SW | 20240403 | 1650 | 20240403 | 1906 | 2422019 | 136 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 1496 | 37.3839 | -121.9134 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0050007 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930667 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | SWITCH | 26997 | 20240403 | 2350 | 20240404 | 301 | 2422162 | 191 | Distribution Circuit | Equipment Failure/Involved | Underground | 158 | 30178 | 37.3946 | -121.8581 | No | Overcast;32-90 F | Elbow | Normal | 24-0050417 | UG | Sus | 46219325 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1930729 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2109 | 82462109 | SWITCH | X1624 | 20240404 | 1625 | 20240406 | 51 | 2423019 | 1946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 17826 | 37.4196 | -121.9515 | No | Overcast-Drizzle;32-90 F | Switch (OH) | Burned/flashed | 24-0050996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1930931 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315980928163 | 20240404 | 1627 | 20240404 | 1640 | 2422882 | 13 | Transformer only | Vegetation | Tree - grew into line | 12 | 156 | 37.2652 | -121.8822 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0050989 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930926 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316195428259 | 20240404 | 2120 | 20240405 | 158 | 2422976 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 7784 | 37.2685 | -121.8084 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Leaking | 24-0050995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1930930 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15541 | 20240404 | 2333 | 20240406 | 1940 | 2424594 | 2647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 41440 | 37.3922 | -121.4894 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1931333 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15555 | 20240405 | 11 | 20240406 | 600 | 2423305 | 1789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 8945 | 37.3556 | -121.4714 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0051537 | OH | Sus | 46221327 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931327 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 315999426608 | 20240405 | 1551 | 20240405 | 1852 | 2424578 | 181 | Transformer only | Vegetation | Tree - grew into line | 9 | 1629 | 37.2225 | -121.8752 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0051609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931374 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 75037 | 20240405 | 2044 | 20240405 | 2254 | 2424900 | 130 | Distribution Circuit | 3rd Party | Metallic Balloon | 40 | 5200 | 37.3513 | -121.8897 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0051668 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931433 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 28137 | 20240406 | 844 | 20240406 | 911 | 2425040 | 27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 135 | 37.1659 | -121.6474 | No | Clear;32-90 F |  |  | 24-0051696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931475 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20240406 | 2018 | 20240407 | 1346 | 2425469 | 1048 | Distribution Circuit | 3rd Party | Metallic Balloon | 2641 | 629783 | 37.4156 | -121.8881 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051830 | OH | Sus | 46221781 | SOUTH BAY AND CENTRAL COAST | APR | Three Phase Fault | 0 | No | Yes | Yes | 1931573 | 0 | EPSS Ckt | N | 2024 | TIME & INST OC
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 24227 | 20240407 | 756 | 20240407 | 851 | 2425613 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 287 | 15785 | 37.3456 | -121.8488 | No | Partly Cloudy;32-90 F |  |  | 24-0051869 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931613 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 18073 | 20240408 | 630 | 20240408 | 809 | 2425923 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 891 | 37.2201 | -121.7872 | No | Clear;32-90 F |  |  | 24-0051979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1931738 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | OTHER | J5452 TWD 27086 | 20240408 | 911 | 20240408 | 920 | 2426089 | 9 | Distribution Circuit | Company Initiated | Personnel- company | 209 | 1881 | 37.2053 | -121.8267 | No | Clear;32-90 F | Elbow | Normal | 24-0041757 | UG | Sus | 35364062 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931821 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315884927870 | 20240408 | 1009 | 20240408 | 1228 | 2426175 | 139 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 1251 | 37.2569 | -121.9151 | No | Clear;32-90 F |  |  | 24-0052115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1931884 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315724529328 | 20240408 | 1945 | 20240408 | 2243 | 2426597 | 178 | Transformer only | Vegetation | Tree - grew into line | 15 | 2670 | 37.2965 | -121.9708 | No | Clear;32-90 F | Secondary | Normal | 24-0052313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1931938 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS SUB | 8343 | OCB | 2100/2 | 20240409 | 1454 | 20240409 | 1519 | 2427262 | 25 | Distribution Circuit | 3rd Party | Thrown Object | 3671 | 91775 | 37.2332 | -121.9013 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052761 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932270 | 0 | Non-EPSS | N | 2024 | A & B PHASE OC
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 26571 | 20240409 | 2007 | 20240409 | 2236 | 2427440 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1937 | 37.3175 | -121.8719 | No | Clear;32-90 F |  |  | 24-0052879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932312 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5425 | 20240410 | 855 | 20240410 | 1158 | 2427553 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 730 | 37.0442 | -121.6005 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0052963 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932347 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28345 | 20240410 | 1155 | 20240410 | 1410 | 2427872 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2565 | 37.1263 | -121.7064 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0053139 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932537 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | FUSE | 75575 | 20240410 | 1157 | 20240410 | 1637 | 2427858 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 8400 | 37.2989 | -121.9368 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0053048 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932517 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316100827289 | 20240411 | 223 | 20240411 | 323 | 2428199 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 480 | 37.2416 | -121.8405 | No | Clear;32-90 F |  |  | 24-0053353 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1932610 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 3787 | 20240411 | 938 | 20240411 | 1345 | 2428413 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 31085 | 37.2742 | -121.8934 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0053409 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932736 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 13529 | 20240411 | 1530 | 20240412 | 212 | 2428783 | 642 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 642 | 37.424 | -121.9052 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0053754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932842 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1103 | 82831103 | OCB | 393382 | 20240411 | 1919 | 20240411 | 2149 | 2428941 | 150 | Distribution Circuit | Equipment Failure/Involved | Underground | 6515 | 545842 | 37.4294 | -121.914 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0053790 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1932861 | 0 | Non-EPSS | N | 2024 | A-B-&C PHASE OC
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | SWITCH | 15537 | 20240411 | 2122 | 20240411 | 2336 | 2429004 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 804 | 37.3884 | -121.4659 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0053807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932891 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 889 | 20240411 | 2211 | 20240412 | 1347 | 2429033 | 936 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 5328 | 36.9472 | -121.5098 | No | Clear;32-90 F |  |  | 24-0053835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1932918 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 1983 | 20240412 | 1450 | 20240412 | 1457 | 2429557 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 7 | 36.981 | -121.5278 | No | Partly Cloudy;32-90 F |  |  | 24-0054187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933153 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15539 | 20240412 | 1631 | 20240412 | 1833 | 2429618 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1342 | 37.3868 | -121.4664 | No | Overcast;32-90 F | Insulator | Broken | 24-0054195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933157 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315758229761 | 20240412 | 1755 | 20240413 | 437 | 2429890 | 642 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 7704 | 37.3084 | -121.9592 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0054261 | OH | Sus | 46228488 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933190 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | OCB | 1105/2 | 20240412 | 1804 | 20240413 | 354 | 2429880 | 590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2196 | 29500 | 37.2915 | -121.9358 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0054256 | OH | Sus | 31690489 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | Yes | 1933187 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315718429708 | 20240412 | 1904 | 20240413 | 504 | 2429882 | 600 | Transformer only | Equipment Failure/Involved | Overhead | 115 | 69000 | 37.307 | -121.9729 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 24-0054275 | OH | Sus | 31690581 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933199 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | SWITCH | 26142 | 20240413 | 717 | 20240413 | 726 | 2430208 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 63 | 37.4319 | -121.9009 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0053790 | UG | Sus | 35544110 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933284 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20240413 | 851 | 20240413 | 2305 | 2430201 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 510 | 65381 | 37.3557 | -121.83 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0054382 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933289 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20240413 | 925 | 20240413 | 1046 | 2430135 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 486 | 37.2181 | -121.7422 | No | Overcast;32-90 F |  |  | 24-0054381 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933288 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | TRANSFORMER | 316101033139 | 20240413 | 956 | 20240413 | 2139 | 2430235 | 703 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 5624 | 37.4025 | -121.8433 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0054427 | OH | Sus | 31690611 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933318 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | JUMPER | #2 PHASE BURNED OJ | 20240413 | 1246 | 20240413 | 1845 | 2430880 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3949 | 37.2835 | -121.8449 | No | Clear;32-90 F | Jumper | Broken | 24-0054548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Open Circuit | 0 | No | No | No | 1933414 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | C1953 | 20240413 | 1405 | 20240414 | 1354 | 2430487 | 1429 | Transformer only | Equipment Failure/Involved | Underground | 19 | 27151 | 37.3952 | -121.863 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0054513 | UG | Sus | 46228513 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933377 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5069 | 20240413 | 1603 | 20240413 | 2038 | 2430702 | 275 | Distribution Circuit | Animal | Squirrel | 7 | 1925 | 37.0893 | -121.6509 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0054574 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933437 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | OCB | 1110/2 | 20240414 | 750 | 20240414 | 903 | 2431106 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5819 | 383226 | 37.3662 | -121.8437 | No | Partly Cloudy;32-90 F |  |  | 24-0054638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1933504 | 0 | Non-EPSS | N | 2024 | A/C/51
SAN JOSE | SAN JOSE | HICKS-1109 | 83431109 | FUSE | 40433 | 20240414 | 854 | 20240414 | 2010 | 2431170 | 676 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 10140 | 37.2481 | -121.9066 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0054659 | OH | Sus | 31690742 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933527 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 17717 | 20240414 | 1034 | 20240414 | 1142 | 2431253 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 996 | 37.1153 | -121.6356 | No | Overcast;32-90 F |  |  | 24-0054673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933546 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | JUMPER | 15719 HIGH SIDE JUMPER | 20240414 | 1438 | 20240414 | 2245 | 2431332 | 487 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3631 | 115921 | 37.3268 | -121.8543 | No | Partly Cloudy;32-90 F | Jumper | Arcing | 24-0054712 | OH | Sus | 46228706 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933574 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315936328101 | 20240414 | 1619 | 20240414 | 2026 | 2431374 | 247 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 3952 | 37.2635 | -121.8975 | No | Partly Cloudy;32-90 F | Secondary | Arcing | 24-0054723 | OH | Sus | 46228763 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933583 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315890529765 | 20240414 | 1952 | 20240416 | 941 | 2431458 | 2269 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 13614 | 37.3089 | -121.9141 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0055352 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934104 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315936328101 | 20240415 | 1242 | 20240415 | 1943 | 2431951 | 421 | Transformer only | Vegetation | Tree - bark fell into line | 16 | 6736 | 37.2635 | -121.8975 | No | Partly Cloudy;32-90 F | Transformer | Contaminated | 24-0054988 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933820 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316816319473 | 20240416 | 1651 | 20240417 | 336 | 2432872 | 645 | Transformer only | Vegetation | Tree - bark fell into line | 10 | 6450 | 37.0299 | -121.5916 | No | Clear;32-90 F | Transformer | Broken | 24-0055601 | OH | Sus | 31690710 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934211 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | INTERRUPTER | 34046 | 20240416 | 1830 | 20240416 | 1936 | 2432999 | 66 | Distribution Circuit | Animal | Bird found | 323 | 18798 | 37.323 | -121.9268 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0055614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1934222 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | RECLOSER | XR088 | 20240416 | 2307 | 20240416 | 2314 | 2433077 | 7 | Distribution Circuit | 3rd Party | Metallic Balloon | 863 | 6041 | 37.3323 | -121.8264 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0055708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934308 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 17553 | 20240416 | 2319 | 20240417 | 216 | 2433082 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 177 | 37.1601 | -121.7494 | No | Clear;32-90 F | Jumper | Bent or Twisted | 24-0055711 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934311 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 40294 | 20240416 | 2336 | 20240417 | 1546 | 2433083 | 758 | Distribution Circuit | Equipment Failure/Involved | Underground | 1021 | 209166 | 37.2305 | -121.7839 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0055722 | UG | Sus | 46229660 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934314 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | TRANSFORMER | T25267 | 20240417 | 1117 | 20240418 | 455 | 2433467 | 1058 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 2116 | 37.1546 | -121.6569 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0055902 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934510 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | T2381 | 20240417 | 2026 | 20240418 | 610 | 2433835 | 584 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 5152 | 37.2957 | -121.7817 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0056135 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934595 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316088431139 | 20240418 | 1547 | 20240418 | 2233 | 2434308 | 406 | Transformer only | Equipment Failure/Involved | Fire- pole | 28 | 11368 | 37.3473 | -121.8463 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0056538 | OH | Sus | 31691116 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1934784 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 33844 | 20240418 | 1619 | 20240418 | 2255 | 2434329 | 225 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 15743 | 37.2345 | -121.823 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0056625 | UG | Sus | 46230909 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1934803 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 41073 | 20240419 | 1454 | 20240420 | 38 | 2435129 | 584 | Distribution Circuit | 3rd Party | Vehicle | 385 | 53320 | 37.2684 | -121.7364 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0057044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1935059 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 72723 | 20240419 | 1517 | 20240419 | 2129 | 2435292 | 372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 6942 | 37.0303 | -121.5774 | No | Clear;32-90 F |  |  | 24-0057081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935082 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315937329304 | 20240419 | 2100 | 20240420 | 407 | 2435289 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 5978 | 37.2965 | -121.8978 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0057078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935078 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 11881 | 20240419 | 2335 | 20240420 | 251 | 2435324 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4900 | 37.3882 | -121.8132 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0057103 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935110 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 96883 | 20240420 | 930 | 20240420 | 1345 | 2435406 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2805 | 37.2239 | -121.659 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0057125 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935150 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315903928574 | 20240421 | 1028 | 20240421 | 2148 | 2435831 | 680 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 8840 | 37.2763 | -121.9089 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935315 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | OCB | 1110/2 | 20240422 | 432 | 20240422 | 658 | 2436102 | 146 | Distribution Circuit | 3rd Party | Other | 4064 | 406446 | 37.341 | -121.902 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0057361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1935365 | 0 | Non-EPSS | N | 2024 | GRD OC
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | T14877 | 20240422 | 432 | 20240422 | 916 | 2436112 | 284 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 1420 | 37.299 | -121.8672 | No | Clear;32-90 F |  |  | 24-0057449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1935481 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | TRANSFORMER | 315936829674 | 20240422 | 443 | 20240422 | 852 | 2436106 | 249 | Transformer only | Unknown Cause | Patrol - not conducted | 14 | 3486 | 37.3064 | -121.8981 | No | Clear;32-90 F |  |  | 24-0057428 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935439 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | JUMPER | OJ SSD 847 ON MAIN LINE | 20240422 | 732 | 20240422 | 1638 | 2436411 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 48762 | 37.1212 | -121.6457 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0057467 | OH | Sus | 31691820 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935500 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 8105 | 20240422 | 1306 | 20240422 | 1437 | 2436668 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 6825 | 37.3295 | -121.8429 | No | Clear;32-90 F | Fuse | Normal | 24-0057683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1935583 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 8105 | 20240422 | 1907 | 20240422 | 2005 | 2436907 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 4350 | 37.3295 | -121.8429 | No | Clear;32-90 F |  |  | 24-0057766 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935620 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316845818725 | 20240423 | 1120 | 20240423 | 1243 | 2437427 | 83 | Transformer only | Vegetation | Other ground vegetation | 10 | 830 | 37.0092 | -121.5812 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0058040 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935834 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316180827418 | 20240423 | 1244 | 20240423 | 1348 | 2437492 | 64 | Transformer only | Vegetation | Tree - grew into line | 11 | 704 | 37.2455 | -121.8131 | No | Clear;32-90 F | Secondary | Arcing | 24-0058042 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935836 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41501 | 20240423 | 1550 | 20240423 | 1704 | 2437633 | 74 | Distribution Circuit | 3rd Party | Metallic Balloon | 38 | 2812 | 37.3263 | -121.8305 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0058222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1935885 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315964429267 | 20240423 | 2119 | 20240424 | 302 | 2437778 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 4802 | 37.2955 | -121.8886 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0058261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1935908 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316178431374 | 20240424 | 2224 | 20240425 | 228 | 2438524 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 9248 | 37.3542 | -121.8158 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0058713 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936220 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | FUSE | 5055 | 20240425 | 716 | 20240426 | 233 | 2438613 | 1157 | Distribution Circuit | Equipment Failure/Involved | Underground | 272 | 98041 | 37.2505 | -121.8173 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0058829 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936397 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315943528753 | 20240425 | 1301 | 20240425 | 1451 | 2439027 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1320 | 37.2814 | -121.8954 | No | Clear;32-90 F | Secondary | Broken | 24-0058956 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936450 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 315978034350 | 20240425 | 1441 | 20240425 | 1510 | 2439109 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 87 | 37.435 | -121.8864 | No | Partly Cloudy;32-90 F | Street Light Equipment | Normal | 24-0050240 | OH | Sus | 35128233 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936468 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | OCB | 2106/2 | 20240425 | 2056 | 20240426 | 1422 | 2439292 | 989 | Distribution Circuit | 3rd Party | Vehicle | 640 | 79319 | 37.0071 | -121.5569 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0059111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936507 | 0 | EPSS Ckt | N | 2024 | B & GRD (TIME 51)
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | TRANSFORMER | 316074229265 | 20240426 | 454 | 20240426 | 818 | 2439465 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1224 | 37.2961 | -121.8506 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0059200 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936614 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316208328066 | 20240426 | 933 | 20240426 | 1143 | 2439690 | 130 | Transformer only | Vegetation | Tree - grew into line | 12 | 1560 | 37.2633 | -121.804 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936728 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 12789 | 20240426 | 1125 | 20240426 | 1227 | 2439783 | 62 | Distribution Circuit | 3rd Party | Metallic Balloon | 49 | 3038 | 37.3602 | -121.8954 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Arcing | 24-0059322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1936733 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | TRANSFORMER | 316122432494 | 20240426 | 1241 | 20240426 | 1326 | 2439832 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 540 | 37.3847 | -121.8356 | No | Overcast;32-90 F | Transformer (OH) | Leaking | 24-0059325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936736 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 28501 | 20240426 | 1305 | 20240426 | 1430 | 2439864 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 850 | 36.9791 | -121.5092 | No | Partly Cloudy;32-90 F |  |  | 24-0059396 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | None | 0 | No | No | No | 1936756 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 70553 | 20240426 | 1515 | 20240426 | 1643 | 2439982 | 88 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 493 | 43384 | 37.3677 | -121.8052 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0059460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936788 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 70553 | 20240426 | 1755 | 20240427 | 426 | 2440124 | 631 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 493 | 311083 | 37.3677 | -121.8052 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0059514 | OH | Sus | 31692299 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | Yes | 1936825 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 3283 | 20240426 | 1801 | 20240427 | 1516 | 2440133 | 1275 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 33438 | 37.0146 | -121.5918 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0059520 | UG | Sus | 46235439 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936830 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 3625 | 20240427 | 1135 | 20240427 | 1256 | 2440550 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 108 | 37.4246 | -121.9697 | No | Clear;32-90 F |  |  | 24-0059635 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1936970 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 28841 | 20240427 | 1406 | 20240428 | 38 | 2440579 | 632 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 22120 | 37.3427 | -121.8063 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0059652 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936982 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315921928579 | 20240427 | 1425 | 20240427 | 1630 | 2440647 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1125 | 37.2765 | -121.9028 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0059658 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1936985 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 25151 | 20240427 | 2234 | 20240427 | 2255 | 2440756 | 21 | Distribution Circuit | Animal | Bird found | 2 | 42 | 37.2181 | -121.7422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059723 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937045 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 13885 | 20240428 | 900 | 20240428 | 919 | 2440946 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 76 | 37.1089 | -121.7476 | No | Clear;32-90 F |  |  | 24-0059755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937080 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 41719 | 20240428 | 1804 | 20240429 | 219 | 2441155 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 7425 | 37.3015 | -121.9135 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0059797 | OH | Sus | 31692462 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937119 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315971728070 | 20240429 | 1019 | 20240429 | 1842 | 2441570 | 503 | Transformer only | Animal | Squirrel | 15 | 7545 | 37.2628 | -121.8851 | No | Clear;32-90 F | Secondary | Broken | 24-0059948 | OH | Sus | 46235916 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937308 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316187532066 | 20240429 | 1554 | 20240430 | 42 | 2441921 | 528 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 6336 | 37.3732 | -121.8129 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0060127 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937394 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 28543 | 20240429 | 2030 | 20240429 | 2231 | 2442069 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 282 | 37.4333 | -121.9672 | No | Clear;32-90 F |  |  | 24-0060211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937457 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR320 | 20240429 | 2114 | 20240429 | 2218 | 2442080 | 64 | Distribution Circuit | 3rd Party | Metallic Balloon | 2076 | 132864 | 37.0019 | -121.5672 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0060179 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Line | 0 | No | No | No | 1937421 | 0 | EPSS Ckt | N | 2024 | A/B
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 28543 | 20240430 | 722 | 20240430 | 851 | 2442218 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 207 | 37.4333 | -121.9672 | No | Clear;32-90 F |  |  | 24-0060297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1937579 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41527 | 20240430 | 1206 | 20240430 | 1440 | 2442662 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 15092 | 37.3378 | -121.837 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0060442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1937712 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | FLYING BELLS IFO 1455 WEAVER DR | 20240501 | 945 | 20240502 | 606 | 2443284 | 1221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 25437 | 37.2996 | -121.9084 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0060790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1937972 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0403 | 82250403 | TRANSFORMER | 315876930389 | 20240501 | 1036 | 20240501 | 1059 | 2443387 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 161 | 37.3259 | -121.9192 | No | Clear;32-90 F | Secondary | Broken | 24-0060858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1938010 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | VASONA-1108 | 83771108 | TRANSFORMER | 315898927272 | 20240502 | 1535 | 20240503 | 120 | 2444293 | 585 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 5850 | 37.2405 | -121.9099 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0061448 | OH | Sus | 46237500 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938412 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4165 | 20240502 | 2011 | 20240502 | 2345 | 2444562 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3107 | 36.9884 | -121.4904 | No | Clear;32-90 F |  |  | 24-0061536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1938473 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 75363 | 20240503 | 859 | 20240503 | 1130 | 2444837 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 11627 | 37.3385 | -121.8275 | No | Clear;32-90 F |  |  | 24-0061702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1938676 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OCB | 1107/2 | 20240505 | 111 | 20240505 | 1505 | 2446243 | 746 | Distribution Circuit | Equipment Failure/Involved | Underground | 3579 | 170822 | 37.3043 | -121.8681 | No | Overcast-Drizzle;32-90 F | Switch (UG) | Burned/flashed | 24-0062286 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939055 | 0 | Non-EPSS | N | 2024 | B & GRD TARGET
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 11069 | 20240505 | 1041 | 20240505 | 1235 | 2446415 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 14364 | 37.2827 | -121.8237 | No | Clear;32-90 F |  |  | 24-0062369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939132 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4455 | 20240505 | 1444 | 20240505 | 1810 | 2446504 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 14474 | 36.9953 | -121.5633 | No | Clear;32-90 F |  |  | 24-0062406 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1939162 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | JUMPER | OJ @ N/O CGC# 316207225864 | 20240505 | 1503 | 20240506 | 110 | 2446494 | 607 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1214 | 37.2032 | -121.8039 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0062387 | OH | Sus | 35550803 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939146 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315902534199 | 20240505 | 1955 | 20240506 | 1125 | 2446601 | 930 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 9300 | 37.4307 | -121.9125 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062414 | OH | Sus | 35550804 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939169 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | TRANSFORMER | 316619823072 | 20240506 | 900 | 20240506 | 1548 | 2446845 | 408 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2448 | 37.1279 | -121.6605 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0062531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939336 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20240506 | 1421 | 20240506 | 1639 | 2447304 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 12144 | 37.2267 | -121.8632 | No | Clear;32-90 F |  |  | 24-0062764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939427 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | FUSE | 72451 | 20240506 | 2024 | 20240507 | 448 | 2447487 | 504 | Distribution Circuit | 3rd Party | Vehicle | 90 | 45360 | 37.2905 | -121.9029 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0062815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939454 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12453 | 20240507 | 839 | 20240508 | 147 | 2447702 | 1028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 256 | 164400 | 37.2508 | -121.8497 | No | Clear;32-90 F | Jumper | Burned Open | 24-0062966 | OH | Sus | 46239430 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939633 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315702630067 | 20240507 | 1800 | 20240508 | 411 | 2448182 | 611 | Transformer only | Vegetation | Tree - branch fell on line | 29 | 17719 | 37.3168 | -121.9784 | No | Clear;32-90 F | Secondary | Broken | 24-0063273 | OH | Sus | 46239645 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1939751 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | RECLOSER | XR058 | 20240508 | 122 | 20240508 | 1232 | 2448322 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1216 | 88708 | 37.3277 | -121.8313 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0063375 | OH | Sus | 31693450 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939852 | 0 | Non-EPSS | N | 2024 | A & GRD
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 18189 | 20240508 | 742 | 20240508 | 911 | 2448487 | 89 | Distribution Circuit | 3rd Party | Metallic Balloon | 71 | 6292 | 37.3084 | -121.9716 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1939936 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 72153 | 20240508 | 958 | 20240508 | 1523 | 2448648 | 325 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 37 | 12025 | 37.1053 | -121.6376 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0063557 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940029 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | RECLOSER | 42894 | 20240508 | 1031 | 20240508 | 1106 | 2448660 | 35 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 223 | 7805 | 37.3077 | -121.8775 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0063540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940023 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | RECLOSER | 71015 | 20240508 | 1046 | 20240508 | 1157 | 2448803 | 71 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 710 | 37.3274 | -121.7665 | No | Clear;32-90 F |  |  | 24-0063591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Multi-Fault | 0 | No | No | No | 1940041 | 0 | EPSS Ckt | N | 2024 | A C & GRD
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 93927 | 20240508 | 1152 | 20240508 | 1358 | 2448849 | 126 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 71 | 8946 | 37.3338 | -121.8506 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940078 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 1985 | 20240508 | 1315 | 20240508 | 1429 | 2448956 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 296 | 36.9585 | -121.551 | No | Clear;32-90 F |  |  | 24-0063770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940093 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | TRANSFORMER | T2329 | 20240508 | 1353 | 20240509 | 204 | 2448987 | 731 | Distribution Circuit | Equipment Failure/Involved | Underground | 219 | 13926 | 37.2711 | -121.7686 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0063813 | UG | Sus | 35551522 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940108 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | FUSE | 8083 | 20240509 | 830 | 20240509 | 1446 | 2449489 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 180 | 67680 | 37.4057 | -121.8849 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0064108 | OH | Sus | 46240386 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940355 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 11997 | 20240509 | 1322 | 20240509 | 1514 | 2449909 | 112 | Distribution Circuit | 3rd Party | Metallic Balloon | 49 | 5488 | 37.3487 | -121.8324 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0064341 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940446 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 8945 | 20240509 | 1503 | 20240509 | 1509 | 2449987 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 6 | 37.2942 | -121.994 | No | Clear;32-90 F | Other | Broken | 24-0064346 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1940450 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | TRANSFORMER | T8200 | 20240510 | 1730 | 20240511 | 1130 | 2451132 | 1080 | Transformer only | 3rd Party | Vehicle | 18 | 19440 | 37.2668 | -121.8268 | No | Clear;32-90 F | Transformer | Broken | 24-0064881 | OH | Sus | 35552340 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1940788 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1115 | 82261115 | FUSE | 26851 | 20240510 | 1832 | 20240510 | 2242 | 2451152 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 3338 | 37.3311 | -121.9074 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0064869 | OH | Sus | 35552318 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1940778 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316180827450 | 20240511 | 249 | 20240511 | 415 | 2451265 | 86 | Transformer only | Vegetation | Tree - grew into line | 10 | 860 | 37.2464 | -121.8132 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0064923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940840 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 40945 | 20240511 | 824 | 20240511 | 1948 | 2451599 | 684 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1368 | 37.1402 | -121.6324 | No | Clear;32-90 F |  |  | 24-0065083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1940951 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 19873 | 20240513 | 920 | 20240513 | 1013 | 2452518 | 53 | Distribution Circuit | Animal | Squirrel | 1 | 35 | 37.2809 | -121.8444 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0065356 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941266 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | SWITCH | X1846 | 20240513 | 1508 | 20240513 | 1522 | 2452903 | 14 | Distribution Circuit | Equipment Failure/Involved | Underground | 1379 | 19306 | 37.2187 | -121.8585 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0065522 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1941356 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 12779 | 20240513 | 1848 | 20240513 | 2049 | 2453051 | 121 | Distribution Circuit | 3rd Party | Other | 44 | 5324 | 37.3572 | -121.8416 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0065584 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941383 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 83427 | 20240513 | 2033 | 20240513 | 2209 | 2453102 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 183 | 17545 | 37.3687 | -121.8352 | No | Clear;32-90 F |  |  | 24-0065605 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941398 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | OTHER | WIRE DOWN 3 PHASES | 20240514 | 143 | 20240514 | 1027 | 2453153 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 159760 | 37.3208 | -121.8422 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0065636 | OH | Sus | 31693908 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | Yes | Yes | 1941423 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 19255 | 20240514 | 713 | 20240514 | 1033 | 2453499 | 200 | Distribution Circuit | Animal | Squirrel | 21 | 4200 | 37.3161 | -121.9733 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 24-0065767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941595 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 40841 | 20240514 | 928 | 20240514 | 1937 | 2453417 | 609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 445 | 189225 | 37.325 | -121.9321 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0065731 | OH | Sus | 31693910 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941567 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0404 | 82250404 | JUMPER | OJ 374 E JULIAN ST | 20240514 | 1124 | 20240514 | 1547 | 2453552 | 263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 895 | 108249 | 37.3441 | -121.8862 | No | Partly Cloudy;32-90 F | Jumper | Burned/flashed | 24-0065852 | OH | Sus | 46246906 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941624 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20240515 | 655 | 20240515 | 921 | 2454031 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 243 | 36.9852 | -121.4853 | No | Overcast-Fog;32-90 F |  |  | 24-0066185 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1941814 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | OCB | 2104/2 | 20240515 | 911 | 20240516 | 337 | 2454234 | 1106 | Distribution Circuit | 3rd Party | Vehicle | 333 | 78069 | 37.0072 | -121.557 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0066206 | OH | Sus | 31694197 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | Yes | No | 1941855 | 0 | EPSS Ckt | N | 2024 | PH OC TIME
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 70297 | 20240515 | 2035 | 20240516 | 306 | 2454700 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 42228 | 37.353 | -121.8119 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0066582 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1941990 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240516 | 1456 | 20240516 | 1702 | 2460805 | 126 | Distribution Circuit | Equipment Failure/Involved | Underground | 4291 | 177878 | 37.2814 | -121.8603 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0066916 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942126 | 0 | Non-EPSS | N | 2024 | B & GRD
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 3783 | 20240517 | 244 | 20240518 | 2258 | 2461179 | 2406 | Distribution Circuit | Equipment Failure/Involved | Underground | 559 | 467945 | 37.2611 | -121.8194 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0067051 | UG | Sus | 46248460 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942222 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | 316247830922 | 20240517 | 946 | 20240517 | 1103 | 2461523 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 616 | 37.3422 | -121.7912 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0067172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942371 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 14891 | 20240517 | 1355 | 20240517 | 1433 | 2461729 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 342 | 37.0537 | -121.5812 | No | Clear;32-90 F |  |  | 24-0067340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942434 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | SWITCH | 25868 | 20240517 | 1506 | 20240517 | 1520 | 2461769 | 14 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 106 | 37.3334 | -121.7827 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0057997 | UG | Sus | 45744737 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942441 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | TRANSFORMER | 315982330010 | 20240517 | 1914 | 20240518 | 126 | 2461910 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 5876 | 37.316 | -121.8827 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0067413 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942458 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 26551 | 20240517 | 2243 | 20240517 | 2351 | 2461971 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 680 | 37.0852 | -121.632 | No | Clear;32-90 F |  |  | 24-0067441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942487 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26095 | 20240518 | 1717 | 20240518 | 1957 | 2462345 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 960 | 37.0115 | -121.5165 | No | Partly Cloudy;32-90 F |  |  | 24-0067573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942603 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240518 | 1905 | 20240519 | 1035 | 2462397 | 930 | Distribution Circuit | Equipment Failure/Involved | Overhead | 776 | 207651 | 37.133 | -121.6122 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0067571 | OH | Sus | 35554200 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942602 | 0 | EPSS Ckt | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316199428172 | 20240519 | 1019 | 20240519 | 1307 | 2462519 | 168 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1848 | 37.2662 | -121.807 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0067615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942649 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | OCB | 2105/2 | 20240519 | 1551 | 20240520 | 156 | 2462694 | 605 | Distribution Circuit | 3rd Party | Vehicle | 4371 | 281823 | 37.1267 | -121.6595 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0067645 | OH | Sus | 35554185 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942680 | 0 | EPSS Ckt | N | 2024 | B C & GRD
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | SWITCH | 19357 | 20240520 | 1000 | 20240520 | 1236 | 2463179 | 156 | Distribution Circuit | 3rd Party | Vandalism | 1 | 156 | 37.3671 | -121.8811 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0067836 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1942888 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | RECLOSER | XR184 | 20240520 | 1505 | 20240521 | 1354 | 2463428 | 1369 | Distribution Circuit | Equipment Failure/Involved | Underground | 1447 | 478529 | 37.2513 | -121.8228 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0068012 | UG | Sus | 46249254 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1942947 | 0 | Non-EPSS | N | 2024 | C- GRD
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | SWITCH | 63256 | 20240520 | 1522 | 20240520 | 1630 | 2463450 | 68 | Distribution Circuit | Company Initiated | Personnel- company | 477 | 32436 | 37.275 | -121.8332 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0068046 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Open Circuit | 0 | No | No | No | 1942957 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240521 | 541 | 20240521 | 1055 | 2463928 | 314 | Distribution Circuit | Animal | Bird found | 2 | 628 | 37.2814 | -121.8603 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0068128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943029 | 0 | Non-EPSS | N | 2024 | B- GRD
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 26315 | 20240521 | 1311 | 20240521 | 1420 | 2464382 | 69 | Distribution Circuit | 3rd Party | Metallic Balloon | 144 | 9936 | 37.3235 | -121.8323 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0068421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943240 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | FUSE | 44420 | 20240521 | 1501 | 20240522 | 532 | 2464469 | 871 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 2052 | 37.398 | -121.9103 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0068516 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943268 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20240521 | 1515 | 20240522 | 207 | 2464477 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 11715 | 37.2267 | -121.8632 | No | Clear;32-90 F | Secondary | Broken | 24-0068488 | OH | Sus | 46249799 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943254 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 26795 | 20240521 | 1900 | 20240522 | 131 | 2464598 | 391 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 9384 | 37.3012 | -121.9694 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0068517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943269 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | OTHER | T14774 TWD J5237 | 20240521 | 2005 | 20240522 | 129 | 2464633 | 324 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 5832 | 37.3282 | -121.8579 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0068485 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943279 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 42864 | 20240521 | 2035 | 20240522 | 2004 | 2464643 | 812 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 202195 | 37.2786 | -121.7569 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0068546 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943300 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | OCB | 2111/2 | 20240521 | 2040 | 20240522 | 1429 | 2464667 | 1069 | Distribution Circuit | Equipment Failure/Involved | Underground | 2692 | 217455 | 37.1267 | -121.6597 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0068530 | UG | Sus | 46249921 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943284 | 0 | EPSS Ckt | N | 2024 | B- GRD
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 33862 | 20240522 | 420 | 20240523 | 202 | 2464764 | 1302 | Distribution Circuit | Equipment Failure/Involved | Underground | 219 | 57357 | 37.2517 | -121.8129 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0068581 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943322 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316843720330 | 20240522 | 733 | 20240522 | 1602 | 2464808 | 509 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1018 | 37.0533 | -121.5824 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0068686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943476 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 8937 | 20240522 | 1550 | 20240522 | 1600 | 2465296 | 10 | Distribution Circuit | 3rd Party | Vandalism | 1 | 10 | 37.352 | -121.8664 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0068933 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943551 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1167 | 20240522 | 1740 | 20240522 | 2225 | 2465363 | 285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1425 | 37.0582 | -121.5506 | No | Clear;32-90 F |  |  | 24-0069015 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943605 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 3799 | 20240522 | 1803 | 20240522 | 1958 | 2465378 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 5285 | 37.0765 | -121.5715 | No | Clear;32-90 F |  |  | 24-0068984 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943573 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 21395 | 20240522 | 1807 | 20240522 | 1920 | 2465380 | 73 | Distribution Circuit | Animal | Squirrel | 7 | 536 | 37.4464 | -121.8888 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0068979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943569 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315665929274 | 20240523 | 135 | 20240523 | 1610 | 2465522 | 875 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 7875 | 37.295 | -121.9909 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0069039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1943625 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | JUMPER | FB'S E/O 182531 | 20240523 | 1324 | 20240523 | 1600 | 2466019 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2808 | 37.2943 | -121.991 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0069208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943830 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | TRANSFORMER | T22608 | 20240523 | 1915 | 20240523 | 2127 | 2466184 | 132 | Transformer only | Equipment Failure/Involved | Underground | 1 | 132 | 37.2447 | -121.8567 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0069448 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943879 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1101 | 83801101 | SWITCH | 27404 | 20240523 | 1955 | 20240523 | 2302 | 2466195 | 187 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 939 | 37.3958 | -121.9237 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0069275 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943870 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41537 | 20240523 | 2035 | 20240524 | 127 | 2465891 | 292 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 8176 | 37.3387 | -121.8355 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0069444 | OH | Sus | 46250836 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1943876 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317079516870 | 20240524 | 1055 | 20240524 | 1256 | 2466589 | 121 | Transformer only | Animal | Squirrel | 1 | 121 | 36.9586 | -121.5003 | No | Clear;32-90 F | Transformer (OH) |  | 24-0069802 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944066 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 63187 | 20240524 | 1256 | 20240524 | 1646 | 2466687 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 9890 | 37.3534 | -121.8906 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0069820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944072 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316228932150 | 20240524 | 1720 | 20240525 | 557 | 2466793 | 757 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1514 | 37.3756 | -121.799 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0069899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944104 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 40417 | 20240525 | 1006 | 20240525 | 1113 | 2467414 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 5896 | 37.2267 | -121.8632 | No | Overcast;32-90 F |  |  | 24-0069986 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944197 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 28181 | 20240525 | 1118 | 20240526 | 157 | 2467451 | 879 | Distribution Circuit | 3rd Party | Vehicle | 355 | 206281 | 37.3204 | -121.8773 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0069994 | OH | Sus | 35555965 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944202 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | OCB | 1101/2 | 20240525 | 1120 | 20240525 | 1154 | 2467460 | 34 | Distribution Circuit | 3rd Party | Metallic Balloon | 1747 | 59398 | 37.3043 | -121.8683 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0069991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944201 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 2153 | 20240525 | 1618 | 20240526 | 1302 | 2467573 | 1244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 5376 | 37.0882 | -121.7564 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070033 | OH | Sus | 46251725 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944232 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 70023 | 20240526 | 1007 | 20240526 | 1102 | 2467791 | 55 | Distribution Circuit | Animal | Bird found | 134 | 7370 | 37.2293 | -121.8726 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0070095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944289 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 28161 | 20240526 | 1233 | 20240526 | 1418 | 2467839 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2343 | 37.0757 | -121.5771 | No | Clear;32-90 F |  |  | 24-0070116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944296 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2107 | 83892107 | OCB | 2107/2 | 20240526 | 1809 | 20240526 | 1950 | 2467985 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 4661 | 37.403 | -121.9056 | No | Clear;32-90 F |  |  | 24-0070133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944310 | 0 | Non-EPSS | N | 2024 | PHASE OC- at X1692 A PH
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15911 | 20240527 | 235 | 20240527 | 916 | 2468051 | 401 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 5713 | 37.1925 | -121.8011 | No | Clear;32-90 F |  |  | 24-0070165 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944340 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | TRANSFORMER | 316116933099 | 20240527 | 953 | 20240527 | 1004 | 2468139 | 11 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 55 | 37.4014 | -121.8377 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0070193 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944366 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 100000103880 | 20240527 | 2120 | 20240527 | 2254 | 2468429 | 94 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2 | 180 | 37.221 | -121.845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944444 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | RECLOSER | 49970 | 20240528 | 949 | 20240529 | 1330 | 2468749 | 1125 | Distribution Circuit | Equipment Failure/Involved | Underground | 1757 | 924422 | 37.2698 | -121.8677 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0070434 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944602 | 0 | Non-EPSS | N | 2024 | C & GRD TARGET
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 17777 | 20240528 | 1046 | 20240528 | 1242 | 2468817 | 116 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 238 | 27608 | 37.3991 | -121.8483 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0070504 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944634 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316203027992 | 20240528 | 1347 | 20240528 | 1449 | 2469066 | 62 | Transformer only | 3rd Party | Metallic Balloon | 20 | 1240 | 37.2612 | -121.8057 | No | Clear;32-90 F | Transformer (OH) |  | 24-0070622 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944675 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T12180 | 20240528 | 1742 | 20240529 | 103 | 2469288 | 441 | Transformer only | 3rd Party | Vehicle | 24 | 10584 | 37.3275 | -121.7696 | No | Clear;32-90 F | Secondary | Broken | 24-0070719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944713 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | JUMPER | FLYING BELLS 1 S/NW/O 19397 | 20240529 | 1015 | 20240529 | 1139 | 2469742 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 5292 | 37.2891 | -121.914 | No | Clear;32-90 F | Jumper | Arcing | 24-0070865 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944920 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20240529 | 1158 | 20240529 | 2033 | 2469853 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 65920 | 37.1083 | -121.7324 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070929 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944943 | 0 | EPSS Ckt | Y | 2024 | B & C TARGET
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | OCB | 1103/2 | 20240529 | 1628 | 20240529 | 2358 | 2470207 | 450 | Distribution Circuit | 3rd Party | Metallic Balloon | 91 | 40950 | 37.3662 | -121.8439 | No | Clear;32-90 F | Insulator | Broken | 24-0071103 | OH | Sus | 31695393 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945007 | 0 | EPSS Ckt | N | 2024 | B & C PH- TIME
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | RECLOSER | 906172 | 20240529 | 1629 | 20240529 | 2334 | 2470240 | 425 | Distribution Circuit | 3rd Party | Kite | 157 | 66725 | 37.2772 | -121.809 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1945012 | 0 | Non-EPSS | N | 2024 | B PH- 50 INST
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | FUSE | 28707 | 20240529 | 1640 | 20240529 | 2124 | 2469797 | 284 | Distribution Circuit | Vegetation | Tree - grew into line | 316 | 89744 | 37.2509 | -121.8167 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071084 | OH | Sus | 46252648 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1944998 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1103 | 83801103 | JUMPER | HSJ & 6433 | 20240529 | 1702 | 20240529 | 1810 | 2470213 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 68 | 37.3748 | -121.9053 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0071104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1945008 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | RIVER OAKS-2106 | 82342106 | OCB | 2106/2 | 20240529 | 2220 | 20240530 | 29 | 2470478 | 129 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 1419 | 37.4112 | -121.927 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0071171 | UG | Sus | 46252921 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945067 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20240530 | 1505 | 20240530 | 1951 | 2471091 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 214 | 52472 | 37.4483 | -121.8461 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0071540 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945317 | 0 | EPSS Ckt | Y | 2024 | A- GRD- 50
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 316278333680 | 20240530 | 2052 | 20240531 | 446 | 2471333 | 474 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 948 | 37.4178 | -121.7826 | No | Clear;32-90 F | Transformer | Broken | 24-0071634 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1945369 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | TRANSFORMER | 315873327449 | 20240531 | 1719 | 20240531 | 1906 | 2472097 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1284 | 37.2454 | -121.9189 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0072083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1945654 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13091 | 20240531 | 2249 | 20240601 | 644 | 2472270 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5700 | 37.374 | -121.8091 | No | Clear;32-90 F | Pole - Tower- steel | Broken | 24-0072110 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | None | 0 | No | No | No | 1945681 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | JUMPER | OPEN JUMPERS 2 SPANS E/O CGC 315690029684 | 20240531 | 2257 | 20240601 | 142 | 2472271 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 7260 | 37.3062 | -121.982 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0072111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1945682 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | RECLOSER | XR072 | 20240601 | 1732 | 20240601 | 1925 | 2472703 | 113 | Distribution Circuit | Animal | Bird found | 604 | 68252 | 37.2975 | -121.8379 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072227 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945793 | 0 | Non-EPSS | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 1157 | 20240602 | 525 | 20240602 | 713 | 2473052 | 108 | Distribution Circuit | Animal | Bird found | 66 | 7128 | 37.2148 | -121.8609 | No | Clear;32-90 F | Fuse | Normal | 24-0072300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945866 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | OCB | 1111/2 | 20240602 | 1747 | 20240602 | 1759 | 2473310 | 12 | Distribution Circuit | 3rd Party | Metallic Balloon | 3540 | 42480 | 37.3662 | -121.8437 | No | Partly Cloudy;32-90 F | Jumper | Normal | 24-0072350 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1945911 | 0 | EPSS Ckt | N | 2024 | AB (AT 69100)
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | T8974 | 20240602 | 2316 | 20240603 | 1254 | 2473511 | 818 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 8764 | 36.9786 | -121.5731 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0072400 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1945957 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4165 | 20240603 | 142 | 20240603 | 311 | 2473559 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2314 | 36.9884 | -121.4904 | No | Partly Cloudy;32-90 F |  |  | 24-0072417 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1945975 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | TRANSFORMER | T21420 | 20240603 | 1039 | 20240603 | 1053 | 2474004 | 14 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 14 | 37.3748 | -121.8903 | No | Overcast;32-90 F |  |  | 24-0072538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1946137 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | SWITCH | 25852 | 20240603 | 1319 | 20240603 | 1329 | 2474221 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 22 | 220 | 36.9783 | -121.5712 | No | Overcast;32-90 F | Switch (UG) | Normal | 24-0072400 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1946179 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 14291 | 20240603 | 1547 | 20240603 | 1807 | 2474444 | 140 | Distribution Circuit | Animal | Other | 1 | 140 | 37.2518 | -121.8285 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0072748 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946212 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | SWITCH | 39158 | 20240603 | 1731 | 20240605 | 434 | 2474428 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 768 | 37.4034 | -121.8961 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0072608 | OH | Sus | 35556573 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946208 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | FUSE | 15227 | 20240604 | 919 | 20240604 | 1424 | 2474817 | 305 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 8540 | 37.3995 | -121.8658 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946500 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | C2272 | 20240604 | 1155 | 20240605 | 1750 | 2475062 | 1795 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 6630 | 37.2193 | -121.8241 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073159 | UG | Sus | 35558207 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946503 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 1673 | 20240604 | 1609 | 20240604 | 1848 | 2475102 | 159 | Distribution Circuit | Vegetation | Tree - grew into line | 307 | 48813 | 37.329 | -121.95 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073222 | OH | Sus | 46254953 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946523 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315996030631 | 20240604 | 1649 | 20240605 | 322 | 2475368 | 633 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 17091 | 37.3331 | -121.8783 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946583 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 3221 | 20240604 | 1700 | 20240604 | 1812 | 2475377 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 72 | 37.2436 | -121.857 | No | Clear;32-90 F |  |  | 24-0073277 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946547 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1104 | 83701104 | FUSE | 359445 | 20240605 | 809 | 20240605 | 816 | 2475794 | 7 | Distribution Circuit | 3rd Party | Vehicle | 68 | 476 | 37.3175 | -121.8811 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946681 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 70351 | 20240605 | 813 | 20240605 | 1002 | 2475877 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 8277 | 37.3235 | -121.8449 | No | Clear;32-90 F |  |  | 24-0073470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946772 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 4283 | 20240605 | 1155 | 20240605 | 2155 | 2476205 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3198 | 37.2108 | -121.7329 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073721 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946885 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315964129213 | 20240605 | 1246 | 20240605 | 1436 | 2476262 | 110 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 1650 | 37.294 | -121.8886 | No | Partly Cloudy;Above 90 |  |  | 24-0073677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946875 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | INTERRUPTER | 272564 | 20240605 | 1309 | 20240605 | 2134 | 2476285 | 442 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 33830 | 37.353 | -121.8232 | No | Clear;Above 90 | Conductor- Underground | Normal | 24-0073672 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946874 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 954008 | 20240605 | 1339 | 20240605 | 1346 | 2476266 | 7 | Distribution Circuit | Company Initiated | Operating error | 142 | 994 | 37.2176 | -121.8342 | No | Clear;32-90 F | Recloser | Normal | 24-0073486 | OH | Sus | 35558207 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946844 | 0 | EPSS Ckt | Y | 2024 | GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20240605 | 1634 | 20240605 | 2016 | 2476476 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 386 | 85692 | 37.1503 | -121.6194 | No | Clear;Above 90 |  |  | 24-0073765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946905 | 0 | EPSS Ckt | Y | 2024 | A PHSE & GRD
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 13273 | 20240605 | 1752 | 20240606 | 146 | 2476611 | 474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 11376 | 37.0223 | -121.5868 | No | Clear;32-90 F |  |  | 24-0073927 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947038 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | INTERRUPTER | 392398 | 20240605 | 1806 | 20240605 | 2104 | 2476634 | 168 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 23058 | 37.2281 | -121.8859 | No | Clear;32-90 F | Interrupter | Malfunctioning | 24-0073810 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1946936 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 26601 | 20240605 | 1840 | 20240605 | 2330 | 2476728 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3190 | 37.3407 | -121.7877 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0073795 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1946925 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T9038 | 20240605 | 1920 | 20240606 | 422 | 2476856 | 542 | Distribution Circuit | Equipment Failure/Involved | Underground | 103 | 14032 | 37.3264 | -121.7775 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073859 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1946980 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1111 | 82251111 | TRANSFORMER | 315934130320 | 20240605 | 1949 | 20240606 | 248 | 2476891 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 6704 | 37.3245 | -121.899 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0073868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946987 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | RECLOSER | 53992 | 20240605 | 2122 | 20240606 | 1040 | 2477097 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 628 | 129116 | 37.1206 | -121.6207 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1946983 | 0 | EPSS Ckt | Y | 2024 | A PH & GRD
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | INTERRUPTER | 272564 | 20240605 | 2215 | 20240606 | 4 | 2477151 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 8938 | 37.353 | -121.8232 | No | Clear;32-90 F |  |  | 24-0073914 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947024 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 432197 | 20240606 | 725 | 20240606 | 737 | 2477030 | 12 | Distribution Circuit | Animal | Squirrel | 2 | 24 | 36.9813 | -121.5043 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073979 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947073 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | INTERRUPTER | 272564 | 20240606 | 1008 | 20240606 | 1203 | 2477701 | 115 | Distribution Circuit | Equipment Failure/Involved | Underground | 82 | 9430 | 37.353 | -121.8232 | No | Clear;32-90 F | Interrupter | Malfunctioning | 24-0074136 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1947226 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | RECLOSER | XR026 | 20240606 | 1255 | 20240606 | 1304 | 2477702 | 9 | Distribution Circuit | 3rd Party | Metallic Balloon | 1531 | 13779 | 37.3407 | -121.8608 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0074175 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947244 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 2533 | 20240606 | 1542 | 20240607 | 117 | 2477573 | 575 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 10925 | 37.3102 | -121.7907 | No | Clear;32-90 F | Secondary | Contaminated | 24-0074315 | OH | Sus | 46256414 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947282 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1109 | 83531109 | OCB | 1109/2 | 20240606 | 1712 | 20240607 | 300 | 2478281 | 588 | Distribution Circuit | 3rd Party | Metallic Balloon | 1959 | 135353 | 37.3662 | -121.8438 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0074375 | OH | Sus | 31696332 | SOUTH BAY AND CENTRAL COAST | JUN | Multi-Fault | 0 | No | Yes | No | 1947308 | 0 | Non-EPSS | N | 2024 | A C & GRD
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | OCB | 1116/2 | 20240606 | 2002 | 20240607 | 240 | 2478536 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3432 | 104472 | 37.2332 | -121.9011 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074411 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947331 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 5681 | 20240606 | 2124 | 20240607 | 1156 | 2478657 | 777 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1818 | 102565 | 37.3159 | -121.9667 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0074386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947345 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2115 | 82832115 | OCB | 2115/2 | 20240607 | 132 | 20240607 | 1326 | 2478773 | 714 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 9701 | 37.4156 | -121.8882 | No | Clear;32-90 F | Connector or Splice (UG) | Broken | 24-0074477 | UG | Sus | 46256727 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947387 | 0 | Non-EPSS | N | 2024 | B PAHSE- GRD & 51
SAN JOSE | SAN JOSE | EL PATIO-1102 | 82921102 | TRANSFORMER | 315795730289 | 20240607 | 933 | 20240608 | 1413 | 2479067 | 1720 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 8600 | 37.3229 | -121.9468 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947535 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316601021726 | 20240607 | 946 | 20240607 | 1441 | 2479085 | 295 | Transformer only | Vegetation | Tree - fell into line | 1 | 295 | 37.0908 | -121.6664 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0074659 | OH | Sus | 31696460 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | No | 1947543 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1102 | 82921102 | SWITCH | 63446SW | 20240607 | 1030 | 20240607 | 1128 | 2479182 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 2262 | 37.3213 | -121.9454 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947540 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | JUMPER | OJ 1/W OF 25197 | 20240607 | 1512 | 20240607 | 1640 | 2479471 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1056 | 37.127 | -121.6664 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0074801 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947576 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315926228260 | 20240607 | 2259 | 20240608 | 1916 | 2479812 | 1217 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 13387 | 37.2678 | -121.901 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0074908 | OH | Sus | 46257579 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947661 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 25019 | 20240608 | 902 | 20240609 | 230 | 2479982 | 1048 | Distribution Circuit | Equipment Failure/Involved | Underground | 116 | 51368 | 37.2508 | -121.8471 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0074954 | UG | Sus | 46257638 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947723 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316801520641 | 20240608 | 1158 | 20240608 | 1248 | 2480076 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 100 | 37.0617 | -121.5971 | No | Clear;32-90 F | Secondary | Burned/flashed | 24-0074962 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1947727 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | RECLOSER | XR054 | 20240609 | 750 | 20240609 | 832 | 2480465 | 42 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2599 | 109158 | 37.3089 | -121.9622 | No | Overcast;32-90 F |  |  | 24-0075072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947826 | 0 | Non-EPSS | N | 2024 | A- B & C
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | SWITCH | 65216SW | 20240609 | 1017 | 20240609 | 1408 | 2480533 | 231 | Distribution Circuit | Animal | Squirrel | 10 | 2310 | 37.3201 | -121.9734 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0075104 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947857 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 64686 | 20240609 | 2145 | 20240611 | 210 | 2480720 | 1510 | Distribution Circuit | Equipment Failure/Involved | Underground | 152 | 126065 | 37.442 | -121.9052 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0075178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1947920 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20240610 | 417 | 20240610 | 924 | 2480776 | 307 | Distribution Circuit | Animal | Bird found | 3515 | 484116 | 37.1066 | -121.6618 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1947931 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 28117 | 20240610 | 1014 | 20240610 | 1042 | 2481180 | 28 | Distribution Circuit | 3rd Party | Other | 50 | 1400 | 37.0422 | -121.5246 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0075282 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948081 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | FUSE | 19713 | 20240610 | 1045 | 20240611 | 115 | 2481312 | 870 | Distribution Circuit | 3rd Party | Vehicle | 115 | 28899 | 37.3276 | -121.8582 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0075398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948139 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 8707 | 20240610 | 1213 | 20240610 | 1401 | 2481424 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 5832 | 37.2604 | -121.8034 | No | Clear;32-90 F |  |  | 24-0075373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948128 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | OCB | 2113/2 | 20240611 | 1843 | 20240612 | 58 | 2482722 | 211 | Distribution Circuit | Equipment Failure/Involved | Underground | 4789 | 1290740 | 37.2448 | -121.7951 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0075989 | UG | Sus | 46262465 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1948524 | 0 | EPSS Ckt | N | 2024 | GRD TIME & PH TIME
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 17643 | 20240613 | 4 | 20240613 | 332 | 2484104 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 624 | 37.4344 | -121.8651 | No | Clear;32-90 F |  |  | 24-0076503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1948893 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11939 | 20240613 | 932 | 20240613 | 1104 | 2484424 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 9752 | 37.2222 | -121.8624 | No | Clear;32-90 F |  |  | 24-0076667 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949084 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 100000009191 | 20240613 | 1105 | 20240613 | 1227 | 2484547 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 492 | 37.2682 | -121.8816 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0076671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949085 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 3921 | 20240613 | 2032 | 20240614 | 700 | 2485023 | 628 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 5024 | 36.9504 | -121.5229 | No | Clear;32-90 F |  |  | 24-0076948 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949197 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 3645 | 20240614 | 544 | 20240614 | 903 | 2485185 | 199 | Distribution Circuit | Animal | Bird found | 7 | 1393 | 37.3117 | -121.7902 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0077024 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949321 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 3921 | 20240614 | 1101 | 20240614 | 1119 | 2485575 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 162 | 36.9504 | -121.5229 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0077093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949377 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316152030497 | 20240614 | 2353 | 20240615 | 1002 | 2486180 | 609 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 4872 | 37.3299 | -121.8245 | No | Clear;32-90 F | Transformer (OH) | Arcing | 24-0077318 | OH | Sus | 46264074 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949485 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | SWITCH | 46584 | 20240615 | 52 | 20240615 | 141 | 2486204 | 49 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 49 | 37.4135 | -121.8516 | No | Clear;32-90 F | Other | Broken | 24-0077273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949487 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 17643 | 20240615 | 352 | 20240615 | 542 | 2486229 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 330 | 37.4344 | -121.8651 | No | Clear;32-90 F |  |  | 24-0077325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1949492 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | OTHER | WIRE DOWN SSD 14375 | 20240615 | 1407 | 20240615 | 2045 | 2486536 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6315 | 54100 | 36.9996 | -121.5713 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077393 | OH | Sus | 31697383 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | Yes | Yes | 1949558 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315981129007 | 20240615 | 1808 | 20240615 | 2332 | 2486643 | 324 | Transformer only | Vegetation | Tree - grew into line | 12 | 3888 | 37.2885 | -121.8827 | No | Clear;32-90 F | Secondary | Normal | 24-0077410 | OH | Sus | 46264167 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949572 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 26309 | 20240616 | 925 | 20240617 | 500 | 2486920 | 1175 | Distribution Circuit | Animal | Squirrel | 6 | 1664 | 37.1649 | -121.6455 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949631 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2101 | 83892101 | OCB | 2101/2 | 20240616 | 1108 | 20240616 | 1950 | 2486946 | 522 | Distribution Circuit | Equipment Failure/Involved | Underground | 1148 | 112031 | 37.403 | -121.9058 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0077470 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949627 | 0 | Non-EPSS | N | 2024 | B & GRD TARGET- 50 INST TARGET
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | OCB | 2104/2 | 20240616 | 1313 | 20240617 | 1756 | 2487020 | 1707 | Distribution Circuit | Equipment Failure/Involved | Underground | 2714 | 69695 | 37.403 | -121.9057 | No | Partly Cloudy;32-90 F | Other | Failed/Faulted | 24-0077488 | UG | Sus | 46264304 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949643 | 0 | Non-EPSS | N | 2024 | 51 TIME TARGET
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 8505 | 20240616 | 1815 | 20240616 | 2034 | 2487156 | 139 | Distribution Circuit | 3rd Party | Metallic Balloon | 224 | 31136 | 37.2662 | -121.8082 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949675 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | TRANSFORMER | 315816729478 | 20240617 | 919 | 20240617 | 1211 | 2487617 | 172 | Transformer only | Vegetation | Tree - grew into line | 35 | 6020 | 37.3006 | -121.9394 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0077619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1949817 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 71540 | 20240617 | 1217 | 20240617 | 1800 | 2487835 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1029 | 37.2917 | -121.8067 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949913 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 4155 | 20240617 | 1459 | 20240618 | 701 | 2488041 | 962 | Distribution Circuit | 3rd Party | Vehicle | 56 | 19749 | 37.1219 | -121.6862 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0077826 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1949940 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | OJ AT 1081 | 20240617 | 2007 | 20240618 | 333 | 2488608 | 446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 16948 | 36.9983 | -121.5245 | No | Clear;32-90 F | Jumper | Burned Open | 24-0077923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Open Circuit | 0 | No | No | No | 1950030 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 12811 | 20240617 | 2024 | 20240617 | 2229 | s1950024 | 125 | Distribution Circuit | Animal | Squirrel | 10 | 1250 | 37.248 | -121.8879 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077918 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950024 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | SWITCH | 11915 | 20240617 | 2212 | 20240618 | 1155 | 2488667 | 823 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1646 | 37.2452 | -121.8749 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0077919 | OH | Sus | 46264685 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950026 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | SWITCH | 35144 | 20240617 | 2229 | 20240618 | 347 | 2488686 | 318 | Distribution Circuit | 3rd Party | Vehicle | 75 | 1724 | 37.3054 | -121.9209 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0077722 | OH | Sus | 35561038 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950016 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 6897 | 20240618 | 707 | 20240618 | 932 | 2488902 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 171 | 24795 | 37.4432 | -121.88 | No | Clear;32-90 F |  |  | 24-0078034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950184 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20240618 | 1336 | 20240618 | 1939 | 2489460 | 363 | Distribution Circuit | Company Initiated | Personnel- company | 18 | 6534 | 37.1127 | -121.7585 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0078288 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1950288 | 0 | EPSS Ckt | Y | 2024 | N/A
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315750329923 | 20240618 | 1349 | 20240618 | 1540 | 2489406 | 111 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 2220 | 37.3127 | -121.9621 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0078216 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950264 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 25385 | 20240619 | 228 | 20240620 | 305 | 2489736 | 1477 | Distribution Circuit | Equipment Failure/Involved | Underground | 776 | 15172 | 37.1011 | -121.585 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0078396 | UG | Sus | 46265607 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950384 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 83283 | 20240619 | 630 | 20240619 | 700 | 2489750 | 30 | Distribution Circuit | 3rd Party | Metallic Balloon | 32 | 960 | 37.053 | -121.5835 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950368 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 27935 | 20240619 | 704 | 20240619 | 840 | 2489776 | 96 | Distribution Circuit | Animal | Bird found | 37 | 3552 | 37.2246 | -121.8587 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0078397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950385 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1114 | 82921114 | SWITCH | 12280 | 20240619 | 1822 | 20240619 | 1850 | 2490227 | 28 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 476 | 37.2985 | -121.9319 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0078498 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1950484 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | RECLOSER | XR188 | 20240619 | 2102 | 20240619 | 2255 | 2490290 | 113 | Distribution Circuit | Animal | Bird found | 640 | 69301 | 37.0127 | -121.6026 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078531 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950493 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 1451 | 20240620 | 1116 | 20240620 | 1324 | 2490793 | 128 | Distribution Circuit | 3rd Party | Metallic Balloon | 97 | 12416 | 37.0061 | -121.5108 | No | Clear;32-90 F | Fuse | Normal | 24-0078724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950620 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 15467 | 20240620 | 1855 | 20240620 | 2024 | 2491097 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 376 | 33464 | 37.4358 | -121.9142 | No | Clear;32-90 F |  |  | 24-0078842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950674 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1103 | 82261103 | OCB | 1103/2 | 20240621 | 757 | 20240621 | 806 | 2491348 | 9 | Distribution Circuit | Animal | Squirrel | 551 | 4959 | 37.341 | -121.9018 | No | Clear;32-90 F | Bushing | Broken | 24-0078944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950764 | 0 | Non-EPSS | N | 2024 | PH T OC
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 28111 | 20240621 | 944 | 20240621 | 1121 | 2491625 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 5044 | 37.0675 | -121.556 | No | Partly Cloudy;32-90 F |  |  | 24-0079084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950898 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26637 | 20240621 | 1126 | 20240621 | 1231 | 2491799 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 5974 | 37.1078 | -121.6009 | No | Clear;32-90 F |  |  | 24-0079134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950916 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20240621 | 2116 | 20240622 | 909 | 2492194 | 713 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3565 | 36.9852 | -121.4853 | No | Clear;32-90 F | Jumper | Burned Open | 24-0079348 | OH | Sus | 31698006 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950996 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | SWITCH | 60656 | 20240622 | 1050 | 20240622 | 1616 | 2492481 | 326 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 4238 | 37.3334 | -121.8578 | No | Clear;32-90 F | Stepdown | Leaking | 24-0079356 | UG | Sus | 35562084 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951049 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20240623 | 135 | 20240623 | 1047 | 2492830 | 552 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2760 | 36.9852 | -121.4853 | No | Partly Cloudy;32-90 F |  |  | 24-0079516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951143 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | RECLOSER | XR116 | 20240623 | 548 | 20240623 | 1903 | 2492854 | 795 | Distribution Circuit | 3rd Party | Vehicle | 2463 | 294178 | 37.3459 | -121.8611 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0079500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | Yes | No | 1951117 | 0 | Non-EPSS | N | 2024 | none
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | SWITCH | 28690 | 20240623 | 942 | 20240623 | 1646 | 2492944 | 424 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 4664 | 37.3135 | -121.8516 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0074429 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951146 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 28814 | 20240623 | 1718 | 20240623 | 1859 | 2493071 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 408 | 37536 | 37.2419 | -121.8304 | No | Clear;32-90 F |  |  | 24-0079563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951183 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | XR160 | 20240623 | 1933 | 20240623 | 2151 | 2493159 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3004 | 316078 | 37.2262 | -121.8309 | No | Clear;32-90 F |  |  | 24-0079566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951188 | 0 | EPSS Ckt | N | 2024 | A- C- GRD
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315861930336 | 20240623 | 2232 | 20240624 | 1112 | 2493233 | 760 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 8360 | 37.3245 | -121.9244 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951215 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315911729398 | 20240624 | 51 | 20240624 | 1225 | 2493245 | 694 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4858 | 37.2989 | -121.9067 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0079783 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951426 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | TRANSFORMER | T8331 | 20240624 | 811 | 20240624 | 905 | 2493432 | 54 | Transformer only | Company Initiated | Coordination failure | 10 | 540 | 37.22 | -121.7628 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0079707 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951370 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | JUMPER | JUMPERS 3 POLES SOURCE SIDE CGC 316405725537 | 20240624 | 930 | 20240624 | 936 | 2493687 | 6 | Distribution Circuit | 3rd Party | Vehicle | 2 | 12 | 37.1936 | -121.7336 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0079720 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951381 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 72567 | 20240624 | 939 | 20240624 | 1103 | 2493612 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 7194 | 37.2942 | -121.9027 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0079716 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951378 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315879729959 | 20240624 | 1543 | 20240624 | 2134 | 2494413 | 351 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 5616 | 37.3141 | -121.9178 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0079910 | OH | Sus | 46268253 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951500 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 28814 | 20240624 | 1831 | 20240624 | 2024 | 2494639 | 113 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 408 | 46104 | 37.2419 | -121.8304 | No | Clear;32-90 F | Fuse | Normal | 24-0079989 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951556 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 71131 | 20240625 | 1056 | 20240625 | 1555 | 2495345 | 299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 61594 | 37.3428 | -121.8456 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0080290 | OH | Sus | 46268486 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951869 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR144 | 20240625 | 1205 | 20240625 | 1229 | 2495422 | 24 | Distribution Circuit | 3rd Party | Vehicle | 2610 | 62640 | 37.0009 | -121.5659 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0080313 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951882 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 28455 | 20240625 | 1409 | 20240625 | 1525 | 2495574 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 734 | 37.428 | -121.9121 | No | Partly Cloudy;32-90 F |  |  | 24-0080449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951932 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 33592 | 20240625 | 1445 | 20240625 | 2058 | 2495599 | 337 | Distribution Circuit | Equipment Failure/Involved | Underground | 82 | 15272 | 37.0198 | -121.5755 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0080466 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1951937 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20240625 | 1534 | 20240625 | 1711 | 2495653 | 97 | Distribution Circuit | 3rd Party | Metallic Balloon | 402 | 38994 | 37.1438 | -121.669 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080461 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1951935 | 0 | EPSS Ckt | Y | 2024 | A AND C
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | SWITCH | 19733 | 20240625 | 1753 | 20240626 | 134 | 2495798 | 461 | Distribution Circuit | Vegetation | Tree - grew into line | 2027 | 123416 | 37.3096 | -121.9517 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1951960 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 28751 | 20240626 | 144 | 20240626 | 1743 | 2496046 | 959 | Distribution Circuit | 3rd Party | Vehicle | 117 | 42317 | 37.2908 | -121.8299 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0080638 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952024 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 40391 | 20240626 | 151 | 20240626 | 721 | 2496047 | 330 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 990 | 36.9836 | -121.5294 | No | Partly Cloudy;32-90 F | Customer Equipment | Failed/Faulted | 24-0080693 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952057 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 40381 | 20240626 | 1357 | 20240626 | 1415 | 2496906 | 18 | Distribution Circuit | Animal | Squirrel | 1 | 18 | 37.1616 | -121.6846 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0080931 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952240 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | OTHER | J5199 TWD T21002 | 20240626 | 1830 | 20240626 | 2127 | 2497120 | 177 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 3363 | 37.3531 | -121.8415 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0080802 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952276 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 14763 | 20240626 | 2127 | 20240627 | 59 | 2497215 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 29280 | 37.3901 | -121.8141 | No | Clear;32-90 F |  |  | 24-0081087 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952303 | 1 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 11304 | 20240627 | 140 | 20240627 | 655 | 2497307 | 290 | Distribution Circuit | Equipment Failure/Involved | Underground | 1025 | 18808 | 37.3516 | -121.8495 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0081070 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952330 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRIP-SAVER | 28421 | 20240627 | 949 | 20240627 | 1314 | 2497574 | 205 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 2 | 410 | 36.9304 | -121.5251 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0081232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952468 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | SWITCH | 43817 | 20240627 | 1218 | 20240627 | 1330 | 2497671 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 72 | 37.0986 | -121.546 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952499 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240627 | 1654 | 20240628 | 422 | 2497913 | 620 | Distribution Circuit | Equipment Failure/Involved | Underground | 4291 | 259164 | 37.2814 | -121.8603 | No | Clear;32-90 F | Elbow | Burned/flashed | 24-0081499 | UG | Sus | 46269514 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952550 | 0 | Non-EPSS | N | 2024 | C PHASE & GRD OC RLY
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240627 | 1722 | 20240627 | 1951 | 2497929 | 149 | Distribution Circuit | Animal | Bird found | 400 | 59600 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952558 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE OC
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316800322135 | 20240627 | 1915 | 20240628 | 1145 | 2497989 | 990 | Transformer only | 3rd Party | Other | 2 | 1980 | 37.1029 | -121.5983 | No | Clear;32-90 F | Fuse | Normal | 24-0081549 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952594 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315908028182 | 20240627 | 2040 | 20240628 | 239 | 2498007 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 2872 | 37.2656 | -121.9073 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0081542 | OH | Sus | 46269515 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952585 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | OCB | XR208 | 20240628 | 1058 | 20240628 | 1253 | 2498552 | 96 | Distribution Circuit | 3rd Party | Kite | 4122 | 263051 | 37.4386 | -121.873 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081762 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1952813 | 0 | EPSS Ckt | Y | 2024 | GRD (50) A & C - SET A ALARM
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4303 | 20240628 | 2233 | 20240629 | 2145 | 2499034 | 1392 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 18096 | 37.0617 | -121.5581 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0082067 | UG | Sus | 46270366 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952998 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 35204 | 20240628 | 2247 | 20240629 | 1507 | 2499026 | 880 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 4785 | 37.3873 | -121.9172 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 24-0081990 | UG | Sus | 35563707 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952927 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | RECLOSER | XR376 | 20240628 | 2353 | 20240629 | 1415 | 2499066 | 862 | Distribution Circuit | Vegetation | Tree - grew into line | 956 | 143936 | 37.2692 | -121.809 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0081994 | OH | Sus | 46270254 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952931 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20240629 | 616 | 20240629 | 1141 | 2499114 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3515 | 726525 | 37.1066 | -121.6618 | No | Clear;32-90 F |  |  | 24-0082010 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952950 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 14181 | 20240629 | 823 | 20240629 | 1446 | 2499249 | 383 | Distribution Circuit | Animal | Squirrel | 2 | 766 | 37.0536 | -121.5331 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082086 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953010 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 25269 | 20240629 | 924 | 20240629 | 2255 | 2499238 | 811 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 16919 | 37.3267 | -121.8544 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0082051 | UG | Sus | 31698861 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952986 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 56253 | 20240629 | 1147 | 20240629 | 1600 | 2499273 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 32890 | 37.3382 | -121.9292 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0082049 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1952993 | 0 | Non-EPSS | Y | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 17359 | 20240629 | 1605 | 20240630 | 47 | 2499447 | 518 | Distribution Circuit | 3rd Party | Vehicle | 17 | 7364 | 37.1058 | -121.6768 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0082108 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953028 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | FUSE | 19865 | 20240630 | 603 | 20240630 | 803 | 2499642 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 120 | 37.3508 | -121.8958 | No | Clear;32-90 F |  |  | 24-0082169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953086 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316124532239 | 20240630 | 1242 | 20240630 | 2255 | 2499762 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8194 | 37.3778 | -121.8347 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0082207 | OH | Sus | 31698902 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953118 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN RAMON-2113 | 14232113 | OCB | 2113/2 | 20240630 | 1430 | 20240701 | 842 | 2499857 | 630 | Distribution Circuit | Equipment Failure/Involved | Underground | 7769 | 1381474 | 37.8002 | -121.9078 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0082215 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1953129 | 0 | Non-EPSS | N | 2024 | A & GRD
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | SWITCH | 35276SW | 20240630 | 1517 | 20240630 | 2337 | 2499876 | 500 | Distribution Circuit | Equipment Failure/Involved | Underground | 85 | 13142 | 37.3753 | -121.8478 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0082182 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1953133 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316616422452 | 20240701 | 1000 | 20240701 | 1110 | 2500661 | 70 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 280 | 37.1109 | -121.6613 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0082380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953305 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | 315914830373 | 20240701 | 1125 | 20240701 | 1223 | 2500761 | 58 | Transformer only | Equipment Failure/Involved | Electrical Overload | 12 | 696 | 37.3256 | -121.9061 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0082460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953332 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 100000023525 | 20240701 | 1128 | 20240701 | 1732 | 2500767 | 364 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 3 | 1092 | 37.2842 | -121.8848 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0082474 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | Yes | No | 1953334 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 526266 | 20240701 | 1402 | 20240701 | 1721 | 2500901 | 199 | Distribution Circuit | Equipment Failure/Involved | Underground | 4394 | 98120 | 37.3586 | -121.8431 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0082361 | UG | Sus | 35563725 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953356 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | JUMPER | JUMPERS 1 SPAN SOUTH OF 15377 | 20240701 | 1649 | 20240701 | 2220 | 2501058 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2648 | 37.3091 | -121.9624 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0082662 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953379 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315889430090 | 20240701 | 1810 | 20240701 | 2049 | 2501146 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 477 | 37.3179 | -121.9146 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0082694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953387 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 100000058341 | 20240701 | 1908 | 20240701 | 2044 | 2501184 | 96 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 192 | 37.0141 | -121.5727 | No | Clear;32-90 F | Sectionalizer | Broken | 24-0082707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953395 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | TRANSFORMER | T26130 | 20240701 | 2124 | 20240702 | 540 | 2501327 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3968 | 37.308 | -121.858 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0082752 | OH | Sus | 35563969 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953432 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 40274 | 20240701 | 2215 | 20240702 | 2050 | 2501406 | 254 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 54594 | 37.2302 | -121.8037 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0082761 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953437 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20240702 | 39 | 20240702 | 344 | 2501448 | 185 | Distribution Circuit | 3rd Party | Metallic Balloon | 849 | 157065 | 37.0163 | -121.5446 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082763 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953441 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE OC
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26095 | 20240702 | 401 | 20240702 | 934 | 2501576 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3663 | 37.0115 | -121.5165 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0082848 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953512 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRIP-SAVER | 28421 | 20240702 | 1014 | 20240702 | 1037 | 2501791 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 15 | 36.9304 | -121.5251 | No | Clear-Heat Wave;32-90 F |  |  | 24-0082910 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953570 | 1 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 455625 | 20240702 | 1043 | 20240702 | 1127 | 2501746 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 396 | 37.3554 | -121.798 | No | Clear-Heat Wave;32-90 F | Insulator | Broken | 24-0082888 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953554 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 73381 | 20240702 | 1258 | 20240702 | 1536 | 2501966 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1738 | 37.1781 | -121.8176 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 24-0083026 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953610 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 18177 | 20240702 | 1340 | 20240703 | 221 | 2501996 | 761 | Distribution Circuit | 3rd Party | Vehicle | 41 | 31201 | 37.3678 | -121.8288 | No | Clear-Heat Wave;Above 90 | Anchor or Guy | Broken | 24-0083083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953622 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | TRIP-SAVER | 28421 | 20240702 | 1346 | 20240702 | 1409 | 2501999 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 46 | 36.9304 | -121.5251 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083068 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953619 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | OCB | 2105/2 | 20240702 | 1440 | 20240702 | 1619 | 2502149 | 99 | Distribution Circuit | 3rd Party | Vehicle | 2610 | 258390 | 37.0071 | -121.5569 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Together | 24-0083128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953629 | 0 | EPSS Ckt | N | 2024 | A-B-C INST
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OCB | 2107/2 | 20240702 | 1440 | 20240702 | 1613 | 2502095 | 93 | Distribution Circuit | 3rd Party | Vehicle | 4026 | 374418 | 37.0071 | -121.5569 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Together | 24-0083121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953627 | 0 | EPSS Ckt | Y | 2024 | A & C GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | 316852521058 | 20240702 | 1608 | 20240702 | 2324 | 2502390 | 436 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 1744 | 37.0734 | -121.5798 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0083193 | OH | Sus | 35563968 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953664 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 31936 | 20240702 | 1613 | 20240702 | 1936 | 2502403 | 203 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 567 | 71609 | 37.3245 | -121.8189 | No | Clear-Heat Wave;Above 90 | Fuse | Failed/Faulted | 24-0083232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953687 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | RECLOSER | XR478 | 20240702 | 1731 | 20240702 | 1810 | 2502582 | 39 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3281 | 125998 | 37.2968 | -121.8799 | No | Clear-Heat Wave;Above 90 | Other | Normal | 24-0083005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953669 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315817330611 | 20240702 | 1750 | 20240702 | 1806 | 2502655 | 16 | Transformer only | Vegetation | Tree - fell into line | 4 | 64 | 37.3324 | -121.9395 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken | 24-0083208 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953675 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 1359 | 20240702 | 1801 | 20240702 | 1909 | 2502697 | 68 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 4817 | 91303 | 37.2383 | -121.8396 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1953701 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2107 | 82462107 | FUSE | 45682 | 20240702 | 1811 | 20240702 | 2141 | 2502724 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 122 | 14658 | 37.4128 | -121.96 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953736 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 11797 | 20240702 | 1822 | 20240702 | 1913 | 2502815 | 51 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 340 | 17349 | 37.2274 | -121.7933 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953698 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | 316753622518 | 20240702 | 1840 | 20240703 | 315 | 2502843 | 515 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 515 | 37.1132 | -121.6143 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0083280 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953719 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1108 | 83871108 | FUSE | 124029 | 20240702 | 1909 | 20240702 | 2031 | 2502896 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1312 | 37.3608 | -121.9115 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083296 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953731 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | RECLOSER | XR064 | 20240702 | 1913 | 20240702 | 1919 | s1967474 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 346 | 2076 | 37.2239 | -121.7797 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1967474 | 0 | EPSS Ckt | Y | 2024 | NOT LOGGED
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 1359 | 20240702 | 1931 | 20240702 | 2011 | 2502943 | 40 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 315 | 12587 | 37.2383 | -121.8396 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953712 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 11797 | 20240702 | 1934 | 20240702 | 2050 | 2502950 | 76 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 510 | 26520 | 37.2274 | -121.7933 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953713 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | C28 | 20240702 | 1946 | 20240702 | 2145 | 2503020 | 119 | Transformer only | Equipment Failure/Involved | Underground | 16 | 1904 | 37.21 | -121.8711 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083346 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | FUSE | 17141 | 20240702 | 1947 | 20240702 | 2142 | 2503037 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 14744 | 37.4565 | -121.898 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083311 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953744 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315891028340 | 20240702 | 2017 | 20240703 | 1434 | 2503358 | 1083 | Transformer only | Equipment Failure/Involved | Electrical Overload | 24 | 22450 | 37.2698 | -121.9132 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0083379 | OH | Sus | 35563968 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1953808 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 31936 | 20240702 | 2047 | 20240702 | 2303 | 2503134 | 136 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 567 | 75691 | 37.3245 | -121.8189 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953773 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 12089 | 20240702 | 2147 | 20240703 | 1218 | 2503210 | 871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 69680 | 37.3432 | -121.8297 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953894 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2107 | 82462107 | TRANSFORMER | T20593 | 20240702 | 2200 | 20240703 | 548 | s1953786 | 468 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 122 | 13796 | 37.4137 | -121.9593 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083369 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953786 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 2571 | 20240702 | 2204 | 20240703 | 709 | 2503221 | 545 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 25305 | 37.4472 | -121.8858 | No | Clear;32-90 F | Relay | Failed/Faulted | 24-0083365 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953783 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | TRANSFORMER | T10183 | 20240703 | 130 | 20240703 | 550 | 2502698 | 260 | Transformer only | Equipment Failure/Involved | Underground | 14 | 3640 | 37.3295 | -121.7771 | No | Clear;32-90 F | Secondary | Broken | 24-0083383 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1953823 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | 316852521058 | 20240703 | 739 | 20240703 | 825 | 2503516 | 46 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 184 | 37.0734 | -121.5798 | No | Clear;32-90 F |  |  | 24-0083435 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953879 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 14027 | 20240703 | 1102 | 20240703 | 1108 | 2503707 | 6 | Distribution Circuit | Animal | Squirrel | 3 | 18 | 37.3085 | -121.9945 | No | Clear-Heat Wave;32-90 F | Fuse | Normal | 24-0083518 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953906 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315791730549 | 20240703 | 1208 | 20240703 | 1317 | 2503755 | 69 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 345 | 37.3307 | -121.9479 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Deteriorated | 24-0083602 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953921 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315749329631 | 20240703 | 1413 | 20240703 | 1857 | 2503872 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3190 | 37.3048 | -121.9623 | No | Clear-Heat Wave;Above 90 | Cutout- fuse holder | Broken | 24-0083712 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953946 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | TRANSFORMER | 315997231466 | 20240703 | 1424 | 20240703 | 1539 | 2503885 | 75 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 1125 | 37.3561 | -121.8783 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1953945 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | C28 | 20240703 | 1514 | 20240704 | 210 | 2503934 | 656 | Distribution Circuit | Equipment Failure/Involved | Underground | 312 | 25516 | 37.21 | -121.8711 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0083776 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953983 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316128032010 | 20240703 | 1602 | 20240704 | 250 | 2503980 | 648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 15102 | 37.3715 | -121.8334 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083825 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954016 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | JUMPER | BROKEN JUMPER | 20240703 | 1605 | 20240703 | 1915 | 2504087 | 190 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3 | 570 | 37.3085 | -121.9944 | No | Clear-Heat Wave;Above 90 | Jumper | Broken | 24-0083753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1953964 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316145730627 | 20240703 | 1632 | 20240703 | 2112 | 2504050 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 9895 | 37.3336 | -121.8267 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954023 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 35276 | 20240703 | 1637 | 20240704 | 256 | 2504373 | 619 | Distribution Circuit | Equipment Failure/Involved | Underground | 85 | 33274 | 37.3753 | -121.8478 | No | Clear-Heat Wave;Above 90 | Elbow | Burned/flashed | 24-0083835 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954021 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 469810 | 20240703 | 1650 | 20240703 | 2200 | 2504084 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 1158 | 37.2003 | -121.7222 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953963 | 0 | EPSS Ckt | Y | 2024 | C PH & GRD
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | TRANSFORMER | C1558 | 20240703 | 1816 | 20240704 | 305 | 2504212 | 529 | Distribution Circuit | Equipment Failure/Involved | Underground | 418 | 31253 | 37.2309 | -121.8075 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0083828 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954018 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 40086 | 20240703 | 1827 | 20240703 | 2023 | 2504238 | 116 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 283 | 32828 | 37.2344 | -121.8405 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0083838 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954025 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315875429954 | 20240703 | 1828 | 20240703 | 2344 | 2504236 | 316 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 4740 | 37.3139 | -121.9193 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083833 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954020 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315875430003 | 20240703 | 1828 | 20240704 | 109 | 2504235 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5213 | 37.3152 | -121.9193 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083842 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954028 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | TRANSFORMER | T6081 | 20240703 | 1916 | 20240704 | 320 | 2504332 | 484 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 13068 | 37.2857 | -121.7552 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083847 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954031 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 70299 | 20240703 | 1922 | 20240704 | 1327 | 2504333 | 1085 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 32378 | 37.3524 | -121.8118 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083864 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1954045 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | FUSE | 40294 | 20240703 | 1937 | 20240703 | 2047 | 2504346 | 70 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 271 | 18970 | 37.2305 | -121.7839 | No | Clear;32-90 F | Fuse | Burned Open | 24-0083853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1954034 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | TRANSFORMER | 316034133617 | 20240703 | 2000 | 20240703 | 2031 | 2504371 | 31 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 279 | 37.4153 | -121.8668 | No | Clear-Heat Wave;32-90 F |  |  | 24-0083858 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1954039 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 18359 | 20240703 | 2008 | 20240703 | 2048 | 2504372 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 640 | 37.3006 | -121.9057 | No | Clear;32-90 F |  |  | 24-0083856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954036 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 17419 | 20240703 | 2029 | 20240704 | 1308 | 2504413 | 999 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 24528 | 37.2444 | -121.8422 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1954064 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20240703 | 2029 | 20240704 | 531 | 2504412 | 542 | Distribution Circuit | 3rd Party | Vehicle | 1006 | 230126 | 37.0163 | -121.5446 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0083857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954038 | 0 | EPSS Ckt | Y | 2024 | APHASE & GRD
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | TRANSFORMER | C1906 | 20240703 | 2044 | 20240704 | 557 | 2504428 | 553 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 15770 | 37.2959 | -121.8179 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083878 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954057 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13931 | 20240703 | 2048 | 20240704 | 1424 | 2504441 | 1056 | Distribution Circuit | Equipment Failure/Involved | Underground | 54 | 16551 | 37.331 | -121.8514 | No | Clear-Heat Wave;32-90 F | Conductor- Underground | Burned/flashed | 24-0083882 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954061 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | TRANSFORMER | C3412 | 20240703 | 2133 | 20240704 | 1810 | 2504480 | 1088 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 170 | 29702 | 37.2676 | -121.841 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0083914 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954086 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316193531645 | 20240704 | 10 | 20240704 | 441 | 2504516 | 271 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 542 | 37.3617 | -121.8107 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0083909 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954084 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 2473 | 20240704 | 226 | 20240704 | 424 | 2504667 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1534 | 37.0479 | -121.5622 | No | Overcast;32-90 F |  |  | 24-0083922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954092 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1103 | 82951103 | TRANSFORMER | C1247 | 20240704 | 323 | 20240704 | 1429 | 2504685 | 666 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 132 | 23445 | 37.2323 | -121.8076 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0083921 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954091 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316003431110 | 20240704 | 1107 | 20240704 | 1205 | 2504971 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 1044 | 37.3462 | -121.876 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084000 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954139 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | JUMPER | 4 SPANS E/O CGC# 315952029048 | 20240704 | 1617 | 20240704 | 2314 | 2505214 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 5421 | 37.29 | -121.8915 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0084113 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954196 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4239 | 20240704 | 1653 | 20240704 | 2313 | 2505167 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1140 | 36.9629 | -121.4932 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0084084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954174 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 30334 | 20240705 | 58 | 20240705 | 259 | 2505603 | 121 | Distribution Circuit | Equipment Failure/Involved | Underground | 83 | 8884 | 37.385 | -121.8429 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0084178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1954263 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | 2105/2 | 20240705 | 509 | 20240705 | 716 | 2505682 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6312 | 628704 | 37.0071 | -121.5569 | No | Clear;32-90 F |  |  | 24-0084187 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1954272 | 0 | EPSS Ckt | N | 2024 | A/B/C
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316871521570 | 20240705 | 823 | 20240705 | 1530 | 2505793 | 427 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1281 | 37.0875 | -121.5738 | No | Heat Wave-Clear;32-90 F | Transformer | Broken | 24-0084265 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954311 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | TRANSFORMER | 315823330673 | 20240705 | 934 | 20240705 | 947 | 2505803 | 13 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 78 | 37.3341 | -121.9373 | No | Clear;32-90 F | Secondary | Contaminated | 24-0084256 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1954305 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 8651 | 20240705 | 1001 | 20240705 | 1507 | 2505891 | 306 | Distribution Circuit | 3rd Party | Vehicle | 68 | 20808 | 37.0907 | -121.5915 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0084223 | OH | Sus | 35564554 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954316 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | SWITCH | 11998 | 20240705 | 1244 | 20240706 | 211 | 2506032 | 807 | Distribution Circuit | Equipment Failure/Involved | Underground | 20 | 16140 | 37.3879 | -121.8414 | No | Clear-Heat Wave;Above 90 | Elbow | Broken | 24-0084178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954344 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | C1187 | 20240705 | 1459 | 20240705 | 2057 | 2506138 | 358 | Transformer only | Equipment Failure/Involved | Electrical Overload | 21 | 7518 | 37.229 | -121.8892 | No | Heat Wave-Clear;Above 90 | Transformer | Burned Open | 24-0084367 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954365 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1111 | 83871111 | FUSE | 8277 | 20240705 | 2208 | 20240705 | 2344 | 2507179 | 96 | Distribution Circuit | Vegetation | Tree - grew into line | 309 | 29664 | 37.3359 | -121.9434 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954456 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4455 | 20240705 | 2336 | 20240706 | 841 | 2507229 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 14387 | 36.9953 | -121.5633 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084501 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954476 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 27863 | 20240706 | 1116 | 20240706 | 1723 | 2507527 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 712 | 37.2145 | -121.7374 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084591 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954520 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316174632374 | 20240706 | 1610 | 20240706 | 1920 | 2507732 | 190 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 1330 | 37.3815 | -121.8175 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0084655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954554 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | FUSE | 11441 | 20240707 | 13 | 20240707 | 1409 | 2508583 | 836 | Distribution Circuit | 3rd Party | Vehicle | 126 | 35400 | 37.4208 | -121.8817 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0084794 | OH | Sus | 35564967 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954692 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR578 | 20240707 | 557 | 20240707 | 1610 | 2508721 | 613 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 19983 | 37.1273 | -121.6629 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0084809 | UG | Sus | 35563969 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954708 | 0 | EPSS Ckt | Y | 2024 | B AND GRD
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 6487 | 20240707 | 910 | 20240707 | 1359 | 2508800 | 289 | Distribution Circuit | Animal | Other | 1 | 289 | 37.2872 | -121.8756 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0084873 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954749 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | RECLOSER | XR328 | 20240707 | 922 | 20240707 | 1034 | 2508813 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 476 | 34272 | 37.1531 | -121.6743 | No | Clear-Heat Wave;32-90 F |  |  | 24-0084834 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | Yes | No | No | 1954725 | 0 | EPSS Ckt | Y | 2024 | B AND GRD
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 44410 | 20240707 | 1825 | 20240708 | 1110 | 2509332 | 1005 | Distribution Circuit | Equipment Failure/Involved | Underground | 197 | 73063 | 37.2564 | -121.8214 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0085024 | UG | Sus | 35563969 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954874 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | JUMPER | OJ NORTH OF CGC 316346623883 | 20240707 | 1826 | 20240708 | 1613 | 2509338 | 1307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3921 | 37.1504 | -121.755 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken | 24-0084959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954816 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | OTHER | MTR#SO-ND267440 | 20240708 | 303 | 20240708 | 512 | 2509673 | 107 | Distribution Circuit | Company Initiated | Return Circuit Normal | 83 | 3521 | 37.3869 | -121.8412 | No | Overcast;32-90 F | Elbow | Normal | 24-0084178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1954901 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 5285 | 20240708 | 1004 | 20240708 | 1230 | 2510082 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1802 | 180983 | 37.1092 | -121.5955 | No | Clear;32-90 F |  |  | 24-0085154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955018 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR144 | 20240708 | 1012 | 20240708 | 1117 | 2510133 | 65 | Distribution Circuit | 3rd Party | Vehicle | 2610 | 169650 | 37.0009 | -121.5659 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0085155 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955019 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | JUMPER | OJ SS OF CGC# 315876219898 | 20240708 | 1458 | 20240708 | 1712 | 2510514 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2010 | 37.3132 | -121.919 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0085284 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955078 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 17117 | 20240708 | 1622 | 20240708 | 1628 | 2510592 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 234 | 37.2782 | -121.9164 | No | Clear;32-90 F | Pothead(Riser Termination) | Deteriorated | 24-0085286 | OH | Sus | 46273171 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955087 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | TRANSFORMER | 316900318139 | 20240708 | 1745 | 20240709 | 122 | 2510669 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4615 | 36.9932 | -121.5623 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085344 | OH | Sus | 35565039 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955096 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316193028861 | 20240709 | 1004 | 20240710 | 327 | 2511432 | 1043 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2086 | 37.2851 | -121.8098 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955308 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28675 | 20240709 | 1020 | 20240709 | 1541 | 2511459 | 321 | Distribution Circuit | Vegetation | Tree - grew into line | 30 | 9630 | 37.3043 | -121.9921 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0085580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1955303 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | RECLOSER | XR020 | 20240709 | 1317 | 20240710 | 257 | 2511600 | 820 | Distribution Circuit | Equipment Failure/Involved | Underground | 2841 | 193257 | 37.3412 | -121.8815 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0085679 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955337 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | FUSE | 298879 | 20240709 | 1632 | 20240709 | 1950 | 2511746 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 4158 | 37.2989 | -121.9921 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0085777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955365 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | FUSE | 43170 | 20240709 | 1746 | 20240709 | 1829 | 2511820 | 43 | Distribution Circuit | Equipment Failure/Involved | Underground | 776 | 8550 | 37.1219 | -121.6334 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0080753 | UG | Sus | 35329574 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1955374 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 180327 | 20240709 | 2050 | 20240710 | 307 | 2511938 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 8671 | 37.2841 | -121.8123 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955394 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 2215 | 20240709 | 2235 | 20240710 | 133 | 2511982 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 4984 | 37.2811 | -121.8875 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0085866 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955420 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR176 | 20240710 | 846 | 20240710 | 1043 | 2512241 | 117 | Distribution Circuit | 3rd Party | Kite | 1101 | 61767 | 37.0929 | -121.6472 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0085971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955557 | 0 | EPSS Ckt | Y | 2024 | C GRD
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | FUSE | 34046 | 20240710 | 934 | 20240710 | 1052 | 2512393 | 78 | Distribution Circuit | Animal | Bird found | 322 | 20556 | 37.323 | -121.9268 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0086060 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955606 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20240710 | 1120 | 20240710 | 1252 | 2512437 | 92 | Distribution Circuit | Animal | Bird found | 402 | 36984 | 37.1438 | -121.669 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0086089 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955614 | 0 | EPSS Ckt | Y | 2024 | A GRD
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 11819 | 20240710 | 1158 | 20240710 | 1404 | 2512466 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 20034 | 37.2809 | -121.8885 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0086114 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1955623 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 28751 | 20240710 | 1259 | 20240710 | 2048 | 2512528 | 469 | Distribution Circuit | Vegetation | Tree - grew into line | 117 | 54873 | 37.2908 | -121.8299 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0086383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955674 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315967927583 | 20240710 | 1849 | 20240711 | 313 | 2512845 | 504 | Transformer only | Equipment Failure/Involved | Electrical Overload | 12 | 6048 | 37.2494 | -121.8864 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0086425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955698 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75157 | 20240710 | 1856 | 20240710 | 2016 | 2512733 | 80 | Distribution Circuit | Vegetation | Tree - grew into line | 65 | 5200 | 37.3012 | -121.9669 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0086387 | OH | Sus | 46278108 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955677 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR176 | 20240710 | 2140 | 20240711 | 836 | 2512991 | 656 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1101 | 205946 | 37.0929 | -121.6472 | No | Clear;32-90 F |  |  | 24-0086420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955695 | 0 | EPSS Ckt | Y | 2024 | C PHASE & OC GRD
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11919 | 20240711 | 118 | 20240711 | 655 | 2513053 | 337 | Distribution Circuit | Vegetation | Tree - grew into line | 40 | 13480 | 37.2275 | -121.876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086478 | OH | Sus | 46278223 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1955737 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2111 | 82462111 | OCB | 2111/2/NORM | 20240711 | 542 | 20240711 | 1729 | 2513143 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 665 | 155215 | 37.4209 | -121.9603 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0086485 | OH | Sus | 31699358 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1955745 | 0 | Non-EPSS | N | 2024 | GRD & TIME
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20240711 | 803 | 20240711 | 1226 | 2513346 | 263 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 386 | 101518 | 37.1503 | -121.6194 | No | Clear-Heat Wave;32-90 F |  |  | 24-0086555 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955801 | 0 | EPSS Ckt | Y | 2024 | A GRD
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 2007 | 20240711 | 851 | 20240711 | 917 | 2513204 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 1586 | 37.4359 | -121.8839 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 24-0086580 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1955847 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316640020130 | 20240711 | 1108 | 20240711 | 2241 | 2513684 | 693 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 2079 | 37.0472 | -121.6525 | No | Clear;32-90 F | Transformer | Malfunctioning | 24-0086812 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1955974 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1111 | 83871111 | JUMPER | FLYING BELLS 1 SPAN E/O CGC 315803330686 | 20240711 | 1345 | 20240711 | 1631 | 2513860 | 166 | Distribution Circuit | Vegetation | Tree - grew into line | 33 | 5478 | 37.3345 | -121.944 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Contaminated | 24-0086784 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1955969 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | TRANSFORMER | 316723023025 | 20240711 | 1702 | 20240712 | 48 | 2514127 | 466 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 932 | 37.1272 | -121.6248 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0086913 | OH | Sus | 35565646 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956012 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | TRANSFORMER | T10785 | 20240711 | 1727 | 20240712 | 1332 | 2514339 | 1205 | Distribution Circuit | Equipment Failure/Involved | Underground | 32 | 32544 | 37.3079 | -121.9399 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Broken | 24-0086947 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956034 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 42433 | 20240711 | 1748 | 20240712 | 1334 | 2514192 | 1186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 55742 | 37.3958 | -121.8553 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Normal | 24-0087204 | OH | Sus | 35565646 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956260 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | TRANSFORMER | 316074833270 | 20240711 | 1823 | 20240712 | 1512 | 2514239 | 1236 | Distribution Circuit | Environmental/External | Ice or snow | 84 | 38682 | 37.4059 | -121.8525 | No | Heat Wave-Clear;Above 90 | Transformer | Deteriorated | 24-0086994 | OH | Sus | 35565646 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956065 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | OCB | 2104/2 | 20240711 | 1941 | 20240712 | 1441 | 2514368 | 727 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 7185 | 1460300 | 37.1267 | -121.6594 | No | Clear-Heat Wave;32-90 F | Switch (UG) | Burned/flashed | 24-0086973 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956049 | 0 | EPSS Ckt | N | 2024 | GRD
SAN JOSE | SAN JOSE | DIXON LANDING-2101 | 14722101 | TRANSFORMER | 315919835189 | 20240711 | 2039 | 20240712 | 1104 | 2514450 | 865 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 9515 | 37.458 | -121.907 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0087052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956120 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315886828493 | 20240711 | 2229 | 20240712 | 246 | 2514512 | 257 | Transformer only | Vegetation | Tree - branch fell on line | 19 | 4883 | 37.274 | -121.9149 | No | Clear;32-90 F | Transformer | Arcing | 24-0087041 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956110 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240711 | 2354 | 20240712 | 1547 | 2514546 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 401 | 55753 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0087043 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | Yes | No | 1956112 | 0 | EPSS Ckt | Y | 2024 | SGF - DCD EVENT DETECTED
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315934929256 | 20240712 | 223 | 20240712 | 1458 | 2514618 | 755 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 3775 | 37.2951 | -121.8987 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956124 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 12469 | 20240712 | 310 | 20240713 | 833 | 2514663 | 1763 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 45765 | 37.3781 | -121.8311 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0087063 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956131 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315921928579 | 20240712 | 334 | 20240712 | 1655 | 2514735 | 801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 17640 | 37.2765 | -121.9028 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956145 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240712 | 1844 | 20240712 | 2146 | 2515524 | 142 | Distribution Circuit | Equipment Failure/Involved | Underground | 6647 | 510298 | 37.2814 | -121.8603 | No | Clear-Heat Wave;32-90 F | Elbow | Failed/Faulted | 24-0087411 | UG | Sus | 46277999 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956341 | 0 | Non-EPSS | N | 2024 | C- PHASE & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316461724462 | 20240712 | 2053 | 20240712 | 2100 | 2515614 | 7 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 7 | 37.1656 | -121.715 | No | Partly Cloudy;32-90 F |  |  | 24-0087439 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1956366 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 11135 | 20240713 | 947 | 20240713 | 1118 | 2515899 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 121 | 37.3784 | -121.8364 | No | Partly Cloudy;32-90 F |  |  | 24-0087523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956463 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | FUSE | 14935 | 20240713 | 957 | 20240713 | 1511 | 2515884 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8478 | 37.2624 | -121.9162 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0087510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956451 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | RECLOSER | 654924 | 20240713 | 1050 | 20240713 | 1237 | 2515937 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 312 | 33384 | 37.0924 | -121.6152 | No | Clear;32-90 F |  |  | 24-0087520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956460 | 0 | EPSS Ckt | Y | 2024 | A & GRD
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315694029813 | 20240713 | 1149 | 20240713 | 1331 | 2515981 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1428 | 37.3099 | -121.9814 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0087537 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956469 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 5335 | 20240713 | 1253 | 20240714 | 438 | 2516025 | 945 | Distribution Circuit | Equipment Failure/Involved | Underground | 200 | 39456 | 37.0906 | -121.6288 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0087571 | UG | Sus | 46279496 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956490 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 3069 | 20240713 | 1900 | 20240713 | 1910 | 2516241 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 380 | 37.1606 | -121.6814 | No | Clear;32-90 F |  |  | 24-0087606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956513 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 25011 | 20240713 | 1936 | 20240714 | 1638 | 2516266 | 1262 | Distribution Circuit | Equipment Failure/Involved | Underground | 85 | 65889 | 37.2236 | -121.8652 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0087615 | UG | Sus | 46279760 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956522 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11867 | 20240713 | 2043 | 20240713 | 2050 | 2516287 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 154 | 37.2242 | -121.8653 | No | Partly Cloudy;32-90 F |  |  | 24-0087618 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956530 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR292 | 20240714 | 121 | 20240714 | 912 | 2516386 | 471 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 770 | 269087 | 37.1334 | -121.6754 | No | Partly Cloudy;32-90 F |  |  | 24-0087655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956566 | 0 | EPSS Ckt | Y | 2024 | B & C
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | C2903 | 20240714 | 2229 | 20240715 | 1418 | 2516885 | 932 | Distribution Circuit | Equipment Failure/Involved | Underground | 181 | 26967 | 37.3278 | -121.8422 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0087790 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956714 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 31924 | 20240715 | 720 | 20240715 | 1112 | 2516927 | 232 | Distribution Circuit | Equipment Failure/Involved | Underground | 142 | 29218 | 37.2584 | -121.8528 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0087909 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1956854 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | OJ 1/P/E/O CGC 316897721393 | 20240715 | 1619 | 20240716 | 230 | 2517616 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1833 | 37.0827 | -121.5644 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0088211 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1956961 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 1477 | 20240715 | 1627 | 20240715 | 1817 | 2517624 | 110 | Distribution Circuit | 3rd Party | Other | 14 | 1540 | 37.0521 | -121.5914 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088205 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956956 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4165 | 20240715 | 2035 | 20240715 | 2339 | 2517745 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 33 | 3972 | 36.9884 | -121.4904 | No | Clear;32-90 F |  |  | 24-0088240 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1956992 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 13747 | 20240716 | 1232 | 20240716 | 1433 | 2518275 | 121 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 11374 | 37.2838 | -121.9094 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088486 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957216 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 3797 | 20240716 | 2014 | 20240717 | 616 | 2518925 | 602 | Distribution Circuit | 3rd Party | Vehicle | 40 | 24080 | 37.0728 | -121.588 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0088672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957287 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2108 | 83892108 | FUSE | 34940SW | 20240717 | 1257 | 20240717 | 1946 | 2519578 | 409 | Distribution Circuit | Equipment Failure/Involved | Underground | 325 | 64949 | 37.4259 | -121.9133 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0089025 | UG | Sus | 46281192 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957535 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4877 | 20240718 | 1103 | 20240718 | 1740 | 2520198 | 397 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 3176 | 36.9734 | -121.5477 | No | Clear;32-90 F |  |  | 24-0089517 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1957751 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | TRANSFORMER | C1924 | 20240718 | 1642 | 20240719 | 152 | 2520415 | 524 | Distribution Circuit | Equipment Failure/Involved | Underground | 579 | 17306 | 37.2441 | -121.862 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0089494 | UG | Sus | 35567281 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957737 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR152 | 20240718 | 2247 | 20240719 | 905 | 2520688 | 618 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 89516 | 37.1047 | -121.6625 | No | Clear;32-90 F |  |  | 24-0089547 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957779 | 0 | EPSS Ckt | Y | 2024 | C PH- GRD- 50
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316898419591 | 20240719 | 820 | 20240719 | 1930 | 2520948 | 670 | Transformer only | 3rd Party | Vehicle | 1 | 670 | 37.0332 | -121.5635 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0089754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957950 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | T8727 | 20240719 | 906 | 20240719 | 926 | 2520850 | 20 | Transformer only | 3rd Party | Customer Equipment | 19 | 380 | 37.334 | -121.8479 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0089637 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957883 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28667 | 20240719 | 1030 | 20240719 | 1628 | 2521028 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 13962 | 37.3079 | -121.9887 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0089689 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1957927 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | T21571 | 20240719 | 1346 | 20240719 | 2040 | 2521110 | 414 | Transformer only | Equipment Failure/Involved | Underground | 4 | 1656 | 37.0133 | -121.5858 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0089798 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957975 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316163324953 | 20240719 | 1703 | 20240719 | 2015 | 2521326 | 192 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 3264 | 37.178 | -121.818 | No | Clear;32-90 F | Jumper | Burned/flashed | 24-0089921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958023 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | SWITCH | 11500 | 20240719 | 2331 | 20240720 | 700 | 2521533 | 449 | Distribution Circuit | Company Initiated | Return Circuit Normal | 18 | 1900 | 37.4263 | -121.9092 | No | Clear;32-90 F | Connector or Splice (UG) | Normal | 24-0089025 | UG | Sus | 46281192 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958041 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 40554 | 20240720 | 1233 | 20240720 | 2113 | 2521791 | 520 | Distribution Circuit | Equipment Failure/Involved | Underground | 273 | 126664 | 37.2954 | -121.8155 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0090064 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958145 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | JUMPER | BURNT OPEN SS JUMPER (B PHASE) | 20240720 | 2043 | 20240720 | 2230 | 2522129 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 12412 | 37.0199 | -121.5727 | No | Clear;32-90 F | Jumper | Burned Open | 24-0090112 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958191 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | SWITCH | 10252 | 20240720 | 2224 | 20240720 | 2243 | 2522191 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 99 | 1657 | 37.2625 | -121.8491 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0090069 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958193 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316097830179 | 20240721 | 608 | 20240721 | 1304 | 2522265 | 416 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 7072 | 37.3211 | -121.8429 | No | Clear;32-90 F |  |  | 24-0090146 | OH | Sus | 46282642 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1958222 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | INTERRUPTER | 34046 | 20240721 | 814 | 20240721 | 1033 | 2522325 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 322 | 44758 | 37.323 | -121.9268 | No | Partly Cloudy;32-90 F |  |  | 24-0090155 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958230 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 954008 | 20240721 | 1110 | 20240721 | 1334 | 2522421 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 145 | 19152 | 37.2176 | -121.8342 | No | Clear;32-90 F |  |  | 24-0090166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958237 | 0 | EPSS Ckt | Y | 2024 | A GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316568022190 | 20240721 | 1451 | 20240721 | 1724 | 2522499 | 153 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 765 | 37.1035 | -121.678 | No | Clear;32-90 F |  |  | 24-0090203 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1958271 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315958231504 | 20240721 | 1644 | 20240722 | 519 | 2522610 | 755 | Transformer only | Vegetation | Tree - branch fell on line | 35 | 26425 | 37.357 | -121.8919 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0090206 | OH | Sus | 31701527 | SOUTH BAY AND CENTRAL COAST | JUL | Open Circuit | 0 | No | No | No | 1958274 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 15039 | 20240722 | 612 | 20240722 | 639 | 2522803 | 27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 27 | 37.0041 | -121.5349 | No | Partly Cloudy;32-90 F |  |  | 24-0090266 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958323 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 25341 | 20240722 | 700 | 20240722 | 820 | 2522810 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1812 | 37.0618 | -121.5875 | No | Clear;32-90 F |  |  | 24-0090300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958371 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316163324953 | 20240722 | 1826 | 20240722 | 1952 | 2523626 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1462 | 37.178 | -121.818 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090655 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958547 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316029826152 | 20240722 | 1955 | 20240722 | 2038 | 2523670 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 387 | 37.2102 | -121.8641 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0090660 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958553 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 17237 | 20240723 | 439 | 20240723 | 625 | 2523857 | 106 | Distribution Circuit | 3rd Party | Metallic Balloon | 240 | 25453 | 37.3548 | -121.8176 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0090726 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958619 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20240723 | 840 | 20240723 | 1109 | 2524085 | 149 | Distribution Circuit | Animal | Bird found | 214 | 31886 | 37.4483 | -121.8461 | No | Clear-Heat Wave;32-90 F | Insulator | Normal | 24-0090807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1958716 | 0 | EPSS Ckt | Y | 2024 | A & C INST
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | JUMPER | 1/S/N/OF 15472 LONE HILL RD | 20240723 | 945 | 20240723 | 1151 | 2524169 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 882 | 37.2445 | -121.9211 | No | Clear-Heat Wave;32-90 F | Crossarm- Wood | Broken | 24-0090826 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958759 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 316985218572 | 20240723 | 1552 | 20240724 | 233 | 2524443 | 641 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 641 | 37.0055 | -121.5335 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0091082 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958848 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 18359 | 20240723 | 1734 | 20240723 | 1835 | 2524674 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 976 | 37.3006 | -121.9057 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 24-0091134 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958864 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1102 | 82951102 | FUSE | 6176 | 20240723 | 1847 | 20240723 | 2200 | 2524733 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 227 | 43769 | 37.2252 | -121.7782 | No | Clear;32-90 F |  |  | 24-0091198 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958904 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75513 | 20240723 | 1859 | 20240724 | 345 | 2524744 | 526 | Distribution Circuit | Vegetation | Tree - grew into line | 120 | 63120 | 37.308 | -121.9878 | No | Clear-Heat Wave;32-90 F | Conductor- Overhead | Contaminated | 24-0091217 | OH | Sus | 46283338 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1958922 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316132632229 | 20240723 | 2031 | 20240724 | 402 | 2524956 | 451 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 2706 | 37.3778 | -121.8314 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0091218 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958924 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 2145 | 20240724 | 146 | 20240724 | 2119 | 2525067 | 1173 | Distribution Circuit | Equipment Failure/Involved | Underground | 146 | 50956 | 37.236 | -121.8734 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0091235 | UG | Sus | 46283701 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1958947 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 40136 | 20240724 | 932 | 20240725 | 159 | 2525479 | 987 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 24493 | 37.1263 | -121.6512 | No | Clear-Heat Wave;32-90 F | Transformer (UG) | Broken | 24-0091387 | UG | Sus | 35568338 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959129 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 17265 | 20240724 | 1044 | 20240724 | 1253 | 2525609 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 129 | 37.3051 | -121.845 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0091405 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959139 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | FUSE | 2549 | 20240724 | 1241 | 20240724 | 1349 | 2525758 | 68 | Distribution Circuit | Animal | Squirrel | 39 | 2652 | 37.3064 | -121.7809 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0091525 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959178 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 42279 | 20240724 | 1557 | 20240724 | 1700 | 2525943 | 63 | Distribution Circuit | Animal | Bird found | 59 | 3717 | 37.3937 | -121.8393 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Normal | 24-0091646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959209 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | T13735 | 20240724 | 1722 | 20240724 | 2002 | 2526023 | 160 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 2720 | 37.3022 | -121.9527 | No | Partly Cloudy-Heat Wave;32-90 F |  |  | 24-0091696 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1959234 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1104 | 82831104 | OCB | 1104/2 | 20240724 | 1738 | 20240725 | 1244 | 2526032 | 820 | Distribution Circuit | Equipment Failure/Involved | Underground | 2689 | 625015 | 37.4156 | -121.888 | No | Partly Cloudy-Heat Wave;Above 90 | Connector or Splice (UG) | Failed/Faulted | 24-0091656 | UG | Sus | 31702342 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959214 | 0 | Non-EPSS | N | 2024 | C & G SET A RLY
SAN JOSE | SAN JOSE | PIERCY-2111 | 83912111 | OCB | 2111/2/NORM | 20240724 | 1934 | 20240725 | 237 | 2526096 | 205 | Distribution Circuit | Equipment Failure/Involved | Underground | 1650 | 80558 | 37.2702 | -121.7873 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0091695 | UG | Sus | 31702343 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959233 | 0 | EPSS Ckt | N | 2024 | PH GRD TIME
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | SWITCH | 12558 | 20240724 | 2232 | 20240725 | 653 | 2526182 | 333 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 2656 | 37.3361 | -121.9147 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0091664 | UG | Sus | 35568412 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959288 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | TRANSFORMER | T20602 | 20240724 | 2244 | 20240725 | 1237 | 2526191 | 833 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 55 | 10161 | 37.1337 | -121.6478 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0091765 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959313 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | SWITCH | 30300 | 20240725 | 144 | 20240725 | 1541 | 2526261 | 837 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 25789 | 37.444 | -121.9024 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0091677 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959301 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | T20034 | 20240725 | 712 | 20240726 | 151 | 2526324 | 1119 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 9442 | 37.125 | -121.6505 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0091810 | UG | Sus | 35568697 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959370 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 12003 | 20240725 | 2224 | 20240726 | 946 | 2527072 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 13706 | 37.3353 | -121.8293 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0092224 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959609 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315718429708 | 20240727 | 100 | 20240727 | 330 | 2528090 | 150 | Transformer only | Equipment Failure/Involved | Overhead | 115 | 17250 | 37.307 | -121.9729 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0092688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959904 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1104 | 82261104 | OCB | 1104/2 | 20240727 | 208 | 20240727 | 447 | 2528097 | 155 | Distribution Circuit | 3rd Party | Vandalism | 378 | 17085 | 37.341 | -121.9019 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Broken | 24-0092700 | UG | Sus | 46285322 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959909 | 0 | Non-EPSS | N | 2024 | GRD TIME OC
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 14481 | 20240727 | 634 | 20240727 | 824 | 2528124 | 110 | Distribution Circuit | Animal | Squirrel | 21 | 2274 | 37.3452 | -121.8396 | No | Overcast;32-90 F | Fuse | Normal | 24-0092730 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959942 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 72299 | 20240727 | 1242 | 20240727 | 2022 | 2528241 | 460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2300 | 37.0433 | -121.5376 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0092758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1959989 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2119 | 83802119 | OCB | 2119/2 | 20240727 | 1530 | 20240727 | 1745 | 2528389 | 130 | Distribution Circuit | 3rd Party | Vandalism | 61 | 7655 | 37.3828 | -121.9262 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0092789 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960009 | 0 | Non-EPSS | N | 2024 | GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 34134 | 20240727 | 2051 | 20240727 | 2346 | 2528482 | 175 | Distribution Circuit | Animal | Bird found | 39 | 2585 | 37.1442 | -121.6269 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0092835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960058 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | SWITCH | 33384 | 20240727 | 2151 | 20240728 | 944 | 2528487 | 713 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 6417 | 37.3011 | -121.8584 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0092799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960028 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR246 | 20240728 | 252 | 20240728 | 1432 | 2528508 | 700 | Distribution Circuit | 3rd Party | Vehicle | 4121 | 366032 | 37.1236 | -121.641 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0092838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960061 | 0 | EPSS Ckt | Y | 2024 | C GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 34134 | 20240728 | 620 | 20240728 | 1758 | 2528768 | 698 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 9507 | 37.1442 | -121.6269 | No | Overcast;32-90 F |  |  | 24-0092913 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960115 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | 739448 | 20240728 | 1009 | 20240729 | 302 | 2528643 | 1013 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4138 | 37.2265 | -121.7506 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0092865 | OH | Sus | 46285622 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960093 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4877 | 20240728 | 1129 | 20240728 | 1330 | 2528687 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 968 | 36.9734 | -121.5477 | No | Partly Cloudy;32-90 F |  |  | 24-0092891 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1960101 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315858230149 | 20240729 | 1135 | 20240730 | 245 | 2529134 | 910 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 10010 | 37.3192 | -121.9258 | No | Clear;32-90 F | Secondary | Broken | 24-0093177 | OH | Sus | 46285955 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960345 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20240729 | 1432 | 20240729 | 1722 | 2529395 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1007 | 147836 | 37.0163 | -121.5446 | No | Clear;32-90 F |  |  | 24-0093338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1960381 | 0 | EPSS Ckt | Y | 2024 | B & C
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | INTERRUPTER | 30016 | 20240729 | 2208 | 20240730 | 1336 | 2529846 | 928 | Distribution Circuit | Equipment Failure/Involved | Underground | 209 | 104696 | 37.3958 | -121.8736 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0093468 | UG | Sus | 46286094 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960449 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 15127 | 20240730 | 1702 | 20240730 | 2023 | 2530556 | 201 | Distribution Circuit | Animal | Other | 2 | 402 | 37.3824 | -121.8874 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093946 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960771 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 13081 | 20240730 | 1710 | 20240731 | 950 | 2530560 | 1000 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 7139 | 37.3769 | -121.815 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0093922 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960756 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315932528906 | 20240730 | 1821 | 20240731 | 140 | 2530531 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 19006 | 37.2856 | -121.8996 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0093885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1960744 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 3051 | 20240730 | 1958 | 20240731 | 310 | 2530650 | 432 | Distribution Circuit | 3rd Party | Vehicle | 19 | 8208 | 36.9688 | -121.5529 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0093945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | SWITCH | 67462 | 20240730 | 2008 | 20240731 | 56 | 2530664 | 288 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 3538 | 37.325 | -121.9165 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0093850 | UG | Sus | 35569561 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1960775 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | SWITCH | 46704 | 20240730 | 2331 | 20240731 | 243 | 2530727 | 192 | Distribution Circuit | Equipment Failure/Involved | Underground | 64 | 1384 | 37.3321 | -121.9132 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0093932 | UG | Sus | 35569786 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1960802 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR246 | 20240731 | 821 | 20240731 | 1645 | 2530915 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3977 | 751508 | 37.1236 | -121.641 | No | Partly Cloudy;32-90 F |  |  | 24-0094045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1960902 | 0 | EPSS Ckt | Y | 2024 | A PH- GRD
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 13977 | 20240731 | 947 | 20240731 | 1114 | 2531103 | 87 | Distribution Circuit | Animal | Squirrel | 194 | 16878 | 37.3839 | -121.8282 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0094172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1961015 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 2497 | 20240731 | 1341 | 20240731 | 1631 | 2531338 | 170 | Distribution Circuit | Animal | Squirrel | 5 | 850 | 37.0209 | -121.5689 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0094425 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1961087 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | 507074 | 20240731 | 1751 | 20240801 | 927 | 2531517 | 936 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 61776 | 37.0326 | -121.6843 | No | Clear;32-90 F |  |  | 24-0094446 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Line | 0 | No | No | No | 1961102 | 0 | EPSS Ckt | Y | 2024 | C INST
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | T6323 | 20240731 | 2139 | 20240801 | 1050 | 2531589 | 791 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 90 | 19084 | 37.264 | -121.8666 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0094484 | OH | Sus | 35570082 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1961132 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316882318705 | 20240801 | 1622 | 20240802 | 111 | 2532224 | 529 | Transformer only | 3rd Party | Vehicle | 11 | 5819 | 37.0088 | -121.5687 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0094852 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961356 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 41601 | 20240801 | 1748 | 20240801 | 2257 | 2532330 | 309 | Distribution Circuit | Vegetation | Tree - grew into line | 86 | 14166 | 37.2978 | -121.8324 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 24-0094827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961365 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75149 | 20240802 | 907 | 20240802 | 1124 | 2532810 | 137 | Distribution Circuit | Vegetation | Tree - grew into line | 44 | 6028 | 37.2946 | -121.9536 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961534 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | TRANSFORMER | 317095617442 | 20240802 | 1054 | 20240802 | 2221 | 2532975 | 687 | Transformer only | Animal | Bird found | 2 | 1374 | 36.9745 | -121.4956 | No | Clear;32-90 F | Jumper | Burned Open | 24-0095173 | OH | Sus | 46288603 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961603 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | INTERRUPTER | 32116 | 20240802 | 1144 | 20240802 | 2059 | 2533014 | 555 | Distribution Circuit | Equipment Failure/Involved | Underground | 1832 | 234063 | 37.0276 | -121.5994 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0095153 | UG | Sus | 46288613 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961597 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2106 | 82462106 | TRANSFORMER | T20939 | 20240802 | 1307 | 20240803 | 515 | 2533081 | 966 | Distribution Circuit | Equipment Failure/Involved | Underground | 200 | 113148 | 37.4083 | -121.9407 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0095301 | UG | Sus | 35570511 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961651 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 7801 | 20240802 | 1732 | 20240802 | 2033 | 2533224 | 181 | Distribution Circuit | Vegetation | Tree - grew into line | 108 | 19548 | 37.3057 | -121.9069 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 24-0095297 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961649 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | INTERRUPTER | 32116 | 20240803 | 1218 | 20240804 | 19 | 2533648 | 721 | Distribution Circuit | Equipment Failure/Involved | Underground | 1832 | 264977 | 37.0276 | -121.5994 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0095425 | UG | Sus | 46288981 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1961751 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | JUMPER | FB @ 1002 PASCOE | 20240803 | 1225 | 20240803 | 1431 | 2533652 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2646 | 37.29 | -121.8848 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0095418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961746 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | JUMPER | FLYING BELLS 2 POLES SS OF CGC 316123731362 | 20240803 | 1550 | 20240804 | 1704 | 2533740 | 1514 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 22 | 33308 | 37.3542 | -121.8344 | No | Partly Cloudy;Above 90 | Transformer (OH) | Burned/flashed | 24-0095442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961763 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | TRANSFORMER | 315812529940 | 20240804 | 2220 | 20240804 | 2244 | 2534367 | 24 | Transformer only | Vegetation | Tree - grew into line | 13 | 312 | 37.3133 | -121.941 | No | Clear;32-90 F | Secondary | Contaminated | 24-0095594 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1961893 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 11681 | 20240805 | 705 | 20240805 | 803 | 2534619 | 58 | Distribution Circuit | Animal | Squirrel | 201 | 11658 | 37.2635 | -121.8123 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961959 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316591520628 | 20240805 | 1300 | 20240805 | 1716 | 2535047 | 256 | Transformer only | 3rd Party | Customer Equipment | 2 | 512 | 37.0606 | -121.6693 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0096059 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962141 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 40908 | 20240805 | 1413 | 20240805 | 2137 | 2535109 | 444 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 111 | 49284 | 37.2932 | -121.7833 | No | Clear;32-90 F |  |  | 24-0096105 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962171 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | INTERRUPTER | 32864 | 20240805 | 1452 | 20240806 | 537 | 2535140 | 885 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 19066 | 37.3861 | -121.9159 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0096091 | UG | Sus | 46289656 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962161 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | JUMPER | FLYING BELLS 1/S/SS/OF CGC 315948128662 | 20240805 | 2056 | 20240806 | 240 | 2535345 | 344 | Distribution Circuit | Vegetation | Tree - grew into line | 25 | 8600 | 37.2791 | -121.8933 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0096095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962163 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | SWITCH | 40908SW | 20240805 | 2311 | 20240806 | 710 | 2535385 | 479 | Distribution Circuit | Equipment Failure/Involved | Underground | 111 | 15377 | 37.2931 | -121.7834 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0096135 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962203 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 26809 | 20240805 | 2340 | 20240806 | 248 | 2535407 | 188 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 198 | 37224 | 37.2953 | -121.9703 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0096137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962205 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316867019105 | 20240806 | 1157 | 20240807 | 245 | 2535844 | 888 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2664 | 37.0197 | -121.574 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096421 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962449 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1112 | 83371112 | SWITCH | 12443 | 20240806 | 2149 | 20240807 | 213 | 2536250 | 264 | Distribution Circuit | Vegetation | Tree - grew into line | 1010 | 111625 | 37.2959 | -121.987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0096563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962516 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316143630736 | 20240806 | 2211 | 20240807 | 1202 | 2536150 | 831 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 14127 | 37.3366 | -121.8274 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0096576 | OH | Sus | 35571352 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962521 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | FB EAST OF CGC 315948728408 | 20240806 | 2302 | 20240807 | 142 | 2536280 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 4160 | 37.2721 | -121.8927 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0096579 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1962524 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | FB SE OF LINE & BUCK ON CORTE DEL ARBOL | 20240806 | 2315 | 20240807 | 400 | 2536274 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 10260 | 37.2703 | -121.8975 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0096575 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1962520 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | TRANSFORMER | 316194228222 | 20240807 | 937 | 20240807 | 1338 | 2536619 | 241 | Transformer only | Vegetation | Tree - grew into line | 9 | 2169 | 37.2674 | -121.8089 | No | Clear;32-90 F | Secondary | Normal | 24-0096698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1962691 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | SWITCH | 7807 | 20240807 | 1639 | 20240807 | 2243 | 2536997 | 364 | Distribution Circuit | Vegetation | Tree - grew into line | 463 | 65464 | 37.3012 | -121.959 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 24-0096852 | OH | Sus | 2017265 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1962781 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1112 | 83371112 | TRANSFORMER | C1941 | 20240807 | 1859 | 20240807 | 2123 | 2537070 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 80 | 11520 | 37.2938 | -121.9856 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0097002 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962810 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1112 | 83371112 | TRANSFORMER | 315678729259 | 20240807 | 1903 | 20240808 | 314 | 2537069 | 491 | Transformer only | Equipment Failure/Involved | Electrical Overload | 26 | 12766 | 37.2946 | -121.9866 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0096992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962803 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20240808 | 230 | 20240808 | 951 | 2537264 | 441 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1008 | 209669 | 37.0163 | -121.5446 | No | Clear;32-90 F |  |  | 24-0097046 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1962841 | 0 | EPSS Ckt | Y | 2024 | B- GRD
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | JUMPER | JUMPERS @ 3480 MARGATE AVE | 20240808 | 1652 | 20240808 | 1927 | 2538167 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 4495 | 37.3145 | -121.9612 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0097422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963070 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | FUSE | 14257 | 20240808 | 2039 | 20240808 | 2138 | 2538330 | 59 | Distribution Circuit | Animal | Bird found | 72 | 4248 | 37.3785 | -121.8857 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0097475 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963114 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 2527 | 20240809 | 656 | 20240809 | 1000 | 2538450 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 736 | 37.1975 | -121.816 | No | Clear;32-90 F |  |  | 24-0097625 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963278 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 5119 | 20240809 | 722 | 20240810 | 1910 | 2538458 | 2148 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 17882 | 37.0168 | -121.498 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0097605 | UG | Sus | 46293286 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963262 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315755529916 | 20240809 | 1003 | 20240809 | 1107 | 2538656 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 832 | 37.3125 | -121.9603 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0097641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963282 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 32020 | 20240809 | 1226 | 20240809 | 1405 | 2538760 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 11202 | 37.386 | -121.8886 | No | Clear;32-90 F |  |  | 24-0097775 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963323 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | SWITCH | 70423 | 20240809 | 1933 | 20240809 | 2138 | 2539038 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 386 | 20453 | 37.2914 | -121.896 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0097897 | OH | Sus | 31703893 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963362 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 4239 | 20240809 | 2034 | 20240809 | 2140 | 2539064 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 198 | 36.9629 | -121.4932 | No | Clear;32-90 F |  |  | 24-0097915 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963370 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315975529132 | 20240809 | 2225 | 20240810 | 858 | 2539100 | 633 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 4431 | 37.2919 | -121.8847 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0097937 | OH | Sus | 35572560 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963387 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | OCB | 2104/2 | 20240810 | 402 | 20240810 | 2056 | 2539142 | 989 | Distribution Circuit | 3rd Party | Vehicle | 1781 | 171994 | 37.1267 | -121.6594 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0097942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963391 | 0 | EPSS Ckt | N | 2024 | OVERCURRENT
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 9957 | 20240810 | 907 | 20240811 | 530 | 2539238 | 1223 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 53812 | 37.3098 | -121.913 | No | Partly Cloudy;32-90 F | Conductor- Underground | Deteriorated | 24-0097981 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1963440 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4877 | 20240810 | 1229 | 20240810 | 1326 | 2539347 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 456 | 36.9734 | -121.5477 | No | Clear;32-90 F |  |  | 24-0098005 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963460 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 7801 | 20240810 | 1411 | 20240810 | 1806 | 2539273 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 25380 | 37.3057 | -121.9069 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0097974 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963433 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | OCB | 1109/2 | 20240811 | 649 | 20240811 | 805 | 2539700 | 76 | Distribution Circuit | Animal | Squirrel | 65 | 4940 | 37.3043 | -121.868 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0098055 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1963520 | 0 | Non-EPSS | N | 2024 | A PHASE
SAN JOSE | SAN JOSE | SARATOGA-1112 | 83371112 | JUMPER | OJ SS OF CGC 315680829273 | 20240812 | 858 | 20240812 | 1148 | 2540215 | 170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 21760 | 37.2952 | -121.986 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0098197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963684 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | FUSE | 38848 | 20240812 | 952 | 20240812 | 1057 | 2540312 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 3965 | 37.4299 | -121.9123 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0098166 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963744 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | SWITCH | 531 | 20240812 | 956 | 20240812 | 1221 | 2540303 | 145 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 145 | 37.1555 | -121.6721 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0098232 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963739 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12849 | 20240812 | 1439 | 20240812 | 1810 | 2540526 | 211 | Distribution Circuit | 3rd Party | Other | 60 | 12660 | 37.247 | -121.848 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0098539 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963825 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 31176 | 20240812 | 1519 | 20240812 | 1720 | 2540544 | 121 | Distribution Circuit | Vegetation | Tree - grew into line | 177 | 21417 | 37.3159 | -121.9616 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Contaminated | 24-0098469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1963809 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 18841 | 20240812 | 2014 | 20240812 | 2315 | 2540762 | 181 | Distribution Circuit | Equipment Failure/Involved | Underground | 148 | 24852 | 37.314 | -121.8179 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0098569 | UG | Sus | 46298432 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1963850 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 70613 | 20240813 | 245 | 20240814 | 216 | 2541180 | 1411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1411 | 36.9543 | -121.525 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0098756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964056 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 11829 | 20240813 | 1628 | 20240813 | 2017 | 2541070 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 27938 | 37.2944 | -121.8867 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0099025 | OH | Sus | 31704956 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964132 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 44606 | 20240813 | 2200 | 20240813 | 2314 | 2541650 | 74 | Distribution Circuit | Equipment Failure/Involved | Underground | 217 | 16058 | 37.3062 | -121.8281 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0080258 | UG | Sus | 35507285 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1964166 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | FUSE | 42497 | 20240814 | 1230 | 20240814 | 1911 | 2542132 | 401 | Distribution Circuit | Vegetation | Tree - grew into line | 108 | 43308 | 37.3314 | -121.9439 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099316 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964393 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 40027 | 20240814 | 1851 | 20240815 | 246 | 2542448 | 475 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 155 | 12033 | 37.2882 | -121.8809 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099397 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964446 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2103 | 83892103 | INTERRUPTER | 199514 | 20240815 | 1515 | 20240815 | 2024 | 2543090 | 309 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 309 | 37.4192 | -121.9151 | No | Clear;32-90 F | Other | Malfunctioning | 24-0099837 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964599 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316797922191 | 20240815 | 1933 | 20240816 | 722 | 2543290 | 709 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 709 | 37.1044 | -121.5991 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099860 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964633 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 27863 | 20240815 | 1945 | 20240815 | 2346 | 2543241 | 241 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 6 | 1446 | 37.2145 | -121.7374 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099835 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964598 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 28291 | 20240815 | 2009 | 20240816 | 219 | 2543263 | 370 | Distribution Circuit | Vegetation | Tree - grew into line | 70 | 25900 | 37.3121 | -121.9592 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099839 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964601 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1116 | 82921116 | SWITCH | 10773 | 20240816 | 1740 | 20240816 | 2102 | 2543951 | 202 | Distribution Circuit | Vegetation | Tree - grew into line | 139 | 28078 | 37.2974 | -121.9698 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100081 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964863 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | JUMPER | OJ @1434 SHORERIDGE | 20240816 | 2116 | 20240817 | 316 | 2544057 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6840 | 37.3485 | -121.8622 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100196 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964885 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | JUMPER | OJ W/O 12657 | 20240816 | 2256 | 20240817 | 251 | 2544081 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 13865 | 37.3049 | -121.9682 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0100204 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964895 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316862619159 | 20240817 | 712 | 20240817 | 834 | 2544160 | 82 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 574 | 37.0212 | -121.5756 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0100221 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964914 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315961928860 | 20240817 | 830 | 20240817 | 1053 | 2544202 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 2002 | 37.2844 | -121.8892 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0100244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964955 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315947728612 | 20240817 | 1040 | 20240817 | 1140 | 2544289 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 720 | 37.2775 | -121.8938 | No | Clear;32-90 F | Secondary | Broken | 24-0100250 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964962 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 70063 | 20240817 | 1150 | 20240817 | 1800 | 2544323 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 11470 | 37.2946 | -121.8949 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0100261 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1964973 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 18931 | 20240817 | 1501 | 20240818 | 818 | 2544422 | 1037 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 246637 | 37.3815 | -121.822 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1964996 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | OCB | 1109/2 | 20240817 | 1933 | 20240817 | 1952 | 2544524 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4002 | 65013 | 37.4156 | -121.8881 | No | Partly Cloudy;32-90 F | Switch (OH) | Arcing | 24-0100325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965017 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315974528063 | 20240818 | 927 | 20240818 | 1928 | 2544731 | 601 | Transformer only | Animal | Squirrel | 2 | 1202 | 37.2625 | -121.8842 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 24-0100368 | OH | Sus | 31705562 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965069 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 43323 | 20240818 | 1853 | 20240818 | 2010 | 2544886 | 77 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 154 | 37.3918 | -121.9115 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965120 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | RECLOSER | XR170 | 20240819 | 103 | 20240819 | 808 | 2544974 | 343 | Distribution Circuit | Equipment Failure/Involved | Underground | 6648 | 1318331 | 37.2814 | -121.8603 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0100443 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965133 | 0 | Non-EPSS | N | 2024 | B PH- GRD
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | OCB | 1105/2 | 20240819 | 255 | 20240819 | 1056 | 2544996 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 92535 | 37.2915 | -121.9358 | No | Clear;32-90 F | Jumper | Burned Open | 24-0100447 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1965138 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315947129009 | 20240819 | 837 | 20240819 | 1204 | 2545165 | 207 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 1863 | 37.2884 | -121.8942 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100617 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965320 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 109808 | 20240819 | 920 | 20240819 | 947 | 2545537 | 27 | Distribution Circuit | Company Initiated | Improper Construction | 1653 | 44631 | 37.1063 | -121.6366 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0100633 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965328 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 14793 | 20240819 | 1450 | 20240819 | 1741 | 2545687 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 5985 | 37.2877 | -121.8932 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0100703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965345 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240819 | 1802 | 20240820 | 310 | 2545873 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 400 | 29496 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100790 | OH | Sus | 46302440 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | Yes | No | 1965367 | 0 | EPSS Ckt | Y | 2024 | B- C- 50
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 14795 | 20240819 | 1830 | 20240820 | 126 | 2545805 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 11232 | 37.288 | -121.8923 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0100774 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965362 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | RECLOSER | XR360 | 20240819 | 2306 | 20240820 | 447 | 2545973 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 34581 | 37.3768 | -121.8983 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0100822 | OH | Sus | 31705646 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1965404 | 0 | Non-EPSS | N | 2024 | C PHASE
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 25865 | 20240819 | 2332 | 20240821 | 35 | 2545976 | 1268 | Distribution Circuit | Equipment Failure/Involved | Underground | 1533 | 77267 | 37.3133 | -121.835 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0100830 | UG | Sus | 31705647 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965416 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2115 | 82832115 | OCB | 2115/2 | 20240820 | 1324 | 20240820 | 1358 | 2546525 | 34 | Distribution Circuit | Equipment Failure/Involved | Underground | 147 | 4998 | 37.4156 | -121.8882 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0101112 | UG | Sus | 46302981 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965639 | 0 | Non-EPSS | N | 2024 | B PHASE- GRD & INST
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OTHER | X1906 | 20240820 | 1401 | 20240821 | 148 | 2546549 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 439 | 225893 | 37.0831 | -121.6092 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0101125 | OH | Sus | 46302947 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | Yes | 1965647 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 72191 | 20240820 | 2021 | 20240821 | 452 | 2546797 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 15905 | 37.3656 | -121.8955 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101227 | OH | Sus | 35575687 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965690 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 70197 | 20240821 | 516 | 20240821 | 525 | 2546880 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 121 | 1089 | 37.4284 | -121.973 | No | Clear;32-90 F | Jumper | Arcing | 24-0101254 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965722 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 26805 | 20240821 | 1008 | 20240821 | 1419 | 2547190 | 251 | Distribution Circuit | Vegetation | Tree - grew into line | 157 | 39407 | 37.3009 | -121.9715 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101377 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965906 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 42789 | 20240821 | 1032 | 20240821 | 1916 | 2547141 | 524 | Distribution Circuit | Vegetation | Tree - grew into line | 33 | 17292 | 37.2854 | -121.9001 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101394 | OH | Sus | 46303239 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1965916 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | SWITCH | 27458 | 20240821 | 1459 | 20240822 | 128 | 2547422 | 629 | Distribution Circuit | Equipment Failure/Involved | Underground | 68 | 26834 | 37.2695 | -121.8327 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0100443 | UG | Sus | 46302057 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1965960 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | JUMPER | #3 JUMPER AT THE BOTTOM OF 42121 | 20240821 | 2039 | 20240821 | 2222 | 2547683 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 21630 | 37.3197 | -121.9185 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0101704 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Open Circuit | 0 | No | No | No | 1966002 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | SWITCH | 63290 | 20240822 | 156 | 20240822 | 205 | 2547730 | 9 | Distribution Circuit | Equipment Failure/Involved | Underground | 242 | 2178 | 37.274 | -121.8321 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0100443 | UG | Sus | 46302057 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966021 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | FUSE | 6740 | 20240822 | 1237 | 20240823 | 145 | 2548171 | 788 | Distribution Circuit | Equipment Failure/Involved | Underground | 265 | 49787 | 37.3824 | -121.8653 | No | Overcast;32-90 F | Transformer (UG) | Broken | 24-0101981 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966234 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | TRANSFORMER | 315937528035 | 20240822 | 1654 | 20240822 | 1734 | 2548519 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 640 | 37.2617 | -121.897 | No | Clear;32-90 F | Secondary | Broken | 24-0102124 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966270 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | JUMPER | OJ @1318 BURKETTE | 20240822 | 2045 | 20240823 | 332 | 2548644 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 38258 | 37.3008 | -121.9834 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0102188 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966302 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316517824611 | 20240822 | 2310 | 20240823 | 12 | 2548726 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 372 | 37.1697 | -121.6962 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0102214 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966331 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 40307 | 20240823 | 713 | 20240823 | 1020 | 2548850 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 374 | 36.9885 | -121.4906 | No | Overcast;32-90 F |  |  | 24-0102370 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966500 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 3625 | 20240823 | 1739 | 20240823 | 1855 | 2549537 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 101 | 37.4246 | -121.9697 | No | Clear;32-90 F |  |  | 24-0102653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966596 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | FUSE | 75319 | 20240823 | 1905 | 20240823 | 2132 | 2549532 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 5733 | 37.2912 | -121.8544 | No | Partly Cloudy;32-90 F |  |  | 24-0102646 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966595 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 75159 | 20240823 | 1939 | 20240824 | 53 | 2549506 | 314 | Distribution Circuit | Vegetation | Tree - grew into line | 131 | 41134 | 37.3017 | -121.976 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0102632 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966589 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315686629611 | 20240823 | 2100 | 20240823 | 2310 | 2549552 | 130 | Transformer only | Vegetation | Tree - grew into line | 10 | 1300 | 37.3043 | -121.9839 | No | Partly Cloudy;32-90 F | Secondary | Normal | 24-0102665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966601 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | OCB | 1109/2 | 20240824 | 838 | 20240824 | 1406 | 2549988 | 328 | Distribution Circuit | 3rd Party | Vehicle | 731 | 118410 | 37.4156 | -121.8881 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0102722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966668 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | FUSE | 63217 | 20240824 | 1401 | 20240824 | 1408 | 2550244 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 15 | 105 | 37.4445 | -121.8745 | No | Clear;32-90 F | Fuse | Normal | 24-0102722 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966730 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | TRANSFORMER | 315935927453 | 20240824 | 1815 | 20240825 | 637 | 2550513 | 742 | Transformer only | Vegetation | Tree - grew into line | 14 | 10388 | 37.2457 | -121.8974 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0102860 | OH | Sus | 46304820 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1966791 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315974528063 | 20240825 | 808 | 20240825 | 1015 | 2550751 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 254 | 37.2625 | -121.8842 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0102884 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | Yes | No | 1966827 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 3867 | 20240825 | 812 | 20240825 | 929 | 2550769 | 77 | Distribution Circuit | Animal | Squirrel | 147 | 11319 | 37.3187 | -121.9659 | No | Clear;32-90 F | Fuse | Burned Open | 24-0102893 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966850 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | C2942 | 20240825 | 1104 | 20240826 | 109 | 2550819 | 845 | Distribution Circuit | Equipment Failure/Involved | Underground | 1097 | 56989 | 37.2528 | -121.8283 | No | Clear;32-90 F | Secondary | Broken | 24-0102957 | UG | Sus | 46304920 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966903 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1108 | 82831108 | OCB | 1108/2 | 20240825 | 1544 | 20240825 | 1714 | 2550902 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4145 | 373050 | 37.4156 | -121.8881 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102925 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1966877 | 0 | EPSS Ckt | N | 2024 | A- B- C (ON X1586)
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12001 | 20240825 | 1800 | 20240826 | 228 | 2550978 | 508 | Distribution Circuit | Vegetation | Tree - grew into line | 94 | 47752 | 37.3351 | -121.8282 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1966891 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1109 | 83801109 | INTERRUPTER | 56788 | 20240826 | 1102 | 20240827 | 431 | 2551479 | 1049 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 137 | 11864 | 37.3847 | -121.9201 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0103158 | UG | Sus | 31706484 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967152 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | RECLOSER | XR336 | 20240826 | 1320 | 20240826 | 2153 | 2551639 | 513 | Distribution Circuit | 3rd Party | Vandalism | 576 | 32152 | 37.2316 | -121.7616 | No | Clear;32-90 F | Secondary | Broken | 24-0103194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967167 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26091 | 20240826 | 1519 | 20240826 | 1621 | 2551779 | 62 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 3906 | 37.0279 | -121.5264 | No | Clear-Rain;Above 90 |  |  | 24-0103328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967210 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | INTERRUPTER | 948228 | 20240827 | 702 | 20240827 | 1132 | 2552169 | 270 | Distribution Circuit | Animal | Bird found | 183 | 49410 | 37.3912 | -121.843 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0103500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967461 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 33352 | 20240827 | 1013 | 20240827 | 1521 | 2552534 | 180 | Distribution Circuit | Equipment Failure/Involved | Underground | 109 | 30420 | 37.2931 | -121.8268 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0103561 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967491 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | TRANSFORMER | 316008929850 | 20240827 | 1423 | 20240827 | 2323 | 2552801 | 540 | Transformer only | Vegetation | Tree - branch fell on line | 6 | 3240 | 37.3117 | -121.8734 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0103707 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967553 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240827 | 1611 | 20240828 | 149 | 2552872 | 578 | Distribution Circuit | Equipment Failure/Involved | Underground | 833 | 43010 | 37.133 | -121.6122 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0103745 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967561 | 0 | EPSS Ckt | Y | 2024 | A & B
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | FUSE | 8195 | 20240827 | 2139 | 20240827 | 2347 | 2553143 | 128 | Distribution Circuit | Animal | Bird found | 16 | 2048 | 37.3426 | -121.7952 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0103821 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967610 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 71413 | 20240828 | 824 | 20240828 | 952 | 2553678 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 264 | 37.3228 | -121.9 | No | Clear;32-90 F |  |  | 24-0103992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1967829 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | JUMPER | FUCO 1965 | 20240828 | 1005 | 20240828 | 1041 | 2553760 | 36 | Distribution Circuit | Company Initiated | Improper Construction | 111 | 3996 | 37.3369 | -121.9436 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095745 | OH | Sus | 35510424 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1967855 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 41807 | 20240828 | 1239 | 20240828 | 1819 | 2553843 | 340 | Distribution Circuit | Vegetation | Tree - grew into line | 25 | 8500 | 37.3105 | -121.9598 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 24-0104140 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1967877 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13951 | 20240828 | 1920 | 20240828 | 2243 | 2554285 | 203 | Distribution Circuit | Vegetation | Tree - grew into line | 34 | 6902 | 37.3227 | -121.8432 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104416 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1967955 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20240828 | 2030 | 20240828 | 2221 | 2554332 | 111 | Distribution Circuit | Animal | Bird found | 3645 | 187559 | 37.1066 | -121.6618 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0104433 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967967 | 0 | EPSS Ckt | Y | 2024 | B&G
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 2145 | 20240828 | 2334 | 20240829 | 1825 | 2554400 | 1131 | Distribution Circuit | Equipment Failure/Involved | Underground | 146 | 69411 | 37.236 | -121.8734 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0104460 | UG | Sus | 31706813 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1967982 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315833330285 | 20240829 | 555 | 20240829 | 1716 | 2554455 | 681 | Transformer only | 3rd Party | Vandalism | 12 | 8172 | 37.3229 | -121.9339 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0104494 | OH | Sus | 31706815 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968003 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | JUMPER | JUMPERS IFO 1808 VALLA DR | 20240829 | 1009 | 20240829 | 1439 | 2554915 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 11880 | 37.2685 | -121.9175 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0104688 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968223 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | JUMPER | OJ SOUTH OF CGC# 315786629619 | 20240829 | 1227 | 20240829 | 1921 | 2555027 | 414 | Distribution Circuit | Vegetation | Tree - grew into line | 19 | 7866 | 37.3043 | -121.9494 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104943 | OH | Sus | 46306713 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968278 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 25261 | 20240829 | 1508 | 20240830 | 138 | 2555189 | 630 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 1890 | 37.0596 | -121.5934 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0104970 | UG | Sus | 46306801 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968282 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 13017 | 20240830 | 738 | 20240830 | 907 | 2555625 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 5340 | 37.3197 | -121.8965 | No | Overcast;32-90 F |  |  | 24-0105183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968470 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | OCB | 2106/2 | 20240830 | 1659 | 20240831 | 315 | 2556208 | 616 | Distribution Circuit | Company Initiated | Operating error | 6444 | 134470 | 37.3226 | -121.7971 | No | Clear;32-90 F | Transformer (UG) | Burned/flashed | 24-0092911 | UG | Sus | 35473081 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968576 | 0 | Non-EPSS | N | 2024 | C GRD & TIME OC
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 75117 | 20240830 | 1726 | 20240830 | 1830 | 2556177 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 5120 | 37.3492 | -121.818 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0105472 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968573 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | T13366 | 20240830 | 1828 | 20240830 | 2035 | 2556219 | 70 | Distribution Circuit | 3rd Party | Other | 31 | 1457 | 37.3606 | -121.8312 | No | Clear;32-90 F | Secondary | Broken | 24-0105497 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968580 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 911035 | 20240830 | 1908 | 20240830 | 2032 | 2556236 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 420 | 37.3085 | -121.9961 | No | Clear;32-90 F |  |  | 24-0105503 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1968583 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR152 | 20240830 | 2319 | 20240831 | 1438 | 2556305 | 919 | Distribution Circuit | Vegetation | Tree - branch fell on line | 332 | 62668 | 37.1047 | -121.6625 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0105522 | OH | Sus | 35578084 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | Yes | No | 1968596 | 0 | EPSS Ckt | Y | 2024 | C-GRD
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | JUMPER | OJ SS CGC 315795630636 | 20240830 | 2326 | 20240831 | 59 | 2556301 | 93 | Distribution Circuit | Vegetation | Tree - grew into line | 31 | 2883 | 37.3331 | -121.9471 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105521 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968595 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | SWITCH | 6962 | 20240831 | 402 | 20240831 | 411 | 2556335 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 314 | 2826 | 37.3185 | -121.8005 | No | Partly Cloudy;32-90 F | Switch (UG) | Normal | 24-0092911 | UG | Sus | 35473081 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968603 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 5179 | 20240831 | 1926 | 20240901 | 1036 | 2556679 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1820 | 37.0715 | -121.7134 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0105690 | OH | Sus | 31707140 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1968730 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | TRANSFORMER | T13323 | 20240831 | 1938 | 20240831 | 2122 | 2556669 | 104 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 1456 | 37.2363 | -121.8838 | No | Clear;32-90 F | Secondary | Broken | 24-0105637 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1968681 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | OCB | 1101/2 | 20240901 | 722 | 20240901 | 745 | 2557023 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2819 | 64837 | 37.2448 | -121.7956 | No | Clear;32-90 F |  |  | 24-0105661 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1968704 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 954008 | 20240901 | 749 | 20240902 | 300 | 2557057 | 1151 | Distribution Circuit | Animal | Squirrel | 145 | 29126 | 37.2176 | -121.8342 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0105665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968708 | 1 | EPSS Ckt | Y | 2024 | C PHASE & GRD & 50
SAN JOSE | SAN JOSE | FMC SUB | 8387 | FUSE | 8277 | 20240902 | 1403 | 20240902 | 1805 | 2557643 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 310 | 46033 | 37.3359 | -121.9434 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0105831 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1968836 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240902 | 1834 | 20240902 | 2056 | 2557731 | 142 | Distribution Circuit | 3rd Party | Vehicle | 833 | 118286 | 37.133 | -121.6122 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1968850 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | FUSE | 3937 | 20240903 | 1046 | 20240903 | 1248 | 2558217 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 122 | 37.316 | -121.9479 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0106036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969059 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | TRANSFORMER | T149249 | 20240903 | 1246 | 20240903 | 2101 | 2558677 | 495 | Transformer only | Equipment Failure/Involved | Underground | 1 | 495 | 37.3735 | -121.9148 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0106391 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969162 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | OTHER | T20982 TWD J5071 | 20240903 | 1300 | 20240903 | 1332 | 2558453 | 32 | Distribution Circuit | Company Initiated | Return Circuit Normal | 30 | 496 | 37.2906 | -121.825 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0103561 | UG | Sus | 46305846 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969113 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | TRANSFORMER | 316117432209 | 20240903 | 1551 | 20240903 | 2305 | 2558611 | 434 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 2170 | 37.3769 | -121.8371 | No | Clear;Above 90 | Transformer | Leaking | 24-0106386 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969161 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 15127 | 20240904 | 1306 | 20240904 | 1312 | 2559416 | 6 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 12 | 37.3824 | -121.8874 | No | Clear;Above 90 |  |  | 24-0106765 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969447 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | SWITCH | 181 | 20240904 | 1350 | 20240904 | 1537 | 2559440 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 26322 | 37.329 | -121.9494 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0106778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969458 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316138431661 | 20240904 | 1648 | 20240904 | 1757 | 2559607 | 69 | Transformer only | Equipment Failure/Involved | Overhead | 45 | 3105 | 37.3619 | -121.8297 | No | Clear;Above 90 | Fuse | Broken | 24-0106976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | None | 0 | No | No | No | 1969514 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 13987 | 20240904 | 1845 | 20240905 | 139 | 2559695 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 18630 | 37.2752 | -121.8978 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106978 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969515 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 911035 | 20240904 | 1852 | 20240904 | 1954 | 2559719 | 62 | Distribution Circuit | Animal | Squirrel | 5 | 310 | 37.3085 | -121.9961 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106998 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1969527 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20240905 | 627 | 20240905 | 1305 | 2559827 | 398 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 53853 | 37.3339 | -121.7556 | No | Clear;32-90 F |  |  | 24-0107038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969558 | 0 | EPSS Ckt | Y | 2024 | B- C & OC
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316302331965 | 20240905 | 856 | 20240905 | 951 | 2560069 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 37.3707 | -121.7742 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0107111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969662 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | SWITCH | 12894 | 20240905 | 928 | 20240905 | 1111 | 2560142 | 103 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 4532 | 37.3122 | -121.8214 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0100119 | UG | Sus | 35573624 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969709 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | FUSE | 44051 | 20240905 | 2243 | 20240906 | 254 | 2560694 | 251 | Distribution Circuit | Vegetation | Tree - grew into line | 38 | 9538 | 37.2463 | -121.8855 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107619 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1969843 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 49883 | 20240906 | 734 | 20240906 | 1508 | 2560791 | 236 | Distribution Circuit | Equipment Failure/Involved | Underground | 404 | 119701 | 37.2662 | -121.847 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0107752 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1969974 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316035830910 | 20240906 | 1336 | 20240907 | 604 | 2561300 | 988 | Transformer only | Equipment Failure/Involved | Electrical Overload | 20 | 19760 | 37.341 | -121.8647 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0108095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970133 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | OTHER | J5499 TWD T25346 | 20240906 | 1821 | 20240906 | 2135 | 2561560 | 194 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 2134 | 37.3162 | -121.7669 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0108022 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1970143 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 25313 | 20240908 | 1313 | 20240909 | 830 | 2562566 | 1157 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 3471 | 37.1277 | -121.683 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0108389 | UG | Sus | 46310903 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970391 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | OCB | 2104/2 | 20240908 | 1414 | 20240910 | 100 | 2562630 | 801 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 4289 | 670150 | 37.1267 | -121.6594 | No | Clear;Above 90 | Pothead(Riser Termination) | Burned/flashed | 24-0108386 | OH | Sus | 31708189 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970389 | 0 | EPSS Ckt | N | 2024 | TIME OC & TIME GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR494 | 20240908 | 1414 | 20240908 | 1814 | 2562621 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3497 | 839280 | 37.1066 | -121.6618 | No | Clear;32-90 F |  |  | 24-0108388 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970390 | 0 | EPSS Ckt | Y | 2024 | A-C- GRD
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 17229 | 20240909 | 652 | 20240909 | 909 | 2562959 | 137 | Distribution Circuit | Animal | Squirrel | 32 | 4425 | 37.2039 | -121.8409 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0108516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970563 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | T8170 | 20240909 | 1142 | 20240909 | 1344 | 2563354 | 122 | Transformer only | 3rd Party | Dig in- 3rd party | 18 | 2196 | 37.2044 | -121.832 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0108848 | UG | Sus | 31708104 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970697 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1109 | 82251109 | TRANSFORMER | 315934630400 | 20240909 | 1635 | 20240909 | 1641 | 2563642 | 6 | Transformer only | Company Initiated | Improper Construction | 18 | 108 | 37.3265 | -121.8992 | No | Clear;32-90 F | Secondary | Normal | 24-0108895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1970707 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | RECLOSER | 976553 | 20240909 | 1956 | 20240910 | 641 | 2563892 | 645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 6141 | 37.4042 | -121.8374 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0108941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970732 | 0 | EPSS Ckt | Y | 2024 | C PH
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20240910 | 630 | 20240910 | 1209 | 2564044 | 339 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 57291 | 37.3339 | -121.7556 | No | Partly Cloudy;32-90 F |  |  | 24-0108983 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1970763 | 0 | EPSS Ckt | Y | 2024 | B & C OC
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | TRANSFORMER | 316247929838 | 20240910 | 1506 | 20240911 | 254 | 2564644 | 708 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 4956 | 37.3122 | -121.7913 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0109294 | OH | Sus | 31708446 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971043 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 12453 | 20240910 | 1703 | 20240910 | 1816 | 2564770 | 73 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 256 | 18688 | 37.2508 | -121.8497 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109380 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1971060 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 12003 | 20240910 | 2120 | 20240911 | 148 | 2564883 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 8844 | 37.3353 | -121.8293 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0109415 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971075 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316093730750 | 20240911 | 1243 | 20240911 | 1336 | 2565507 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 742 | 37.3367 | -121.8446 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0109737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971336 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | SWITCH | 95024 | 20240911 | 1628 | 20240911 | 1634 | 2565840 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 144 | 37.3048 | -121.8987 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109452 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971402 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20240911 | 1708 | 20240911 | 2234 | 2565865 | 326 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 18908 | 37.053 | -121.5276 | No | Clear;32-90 F |  |  | 24-0109932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971409 | 0 | EPSS Ckt | Y | 2024 | B PHASE PROT TRIP
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | TRANSFORMER | 316008431275 | 20240911 | 2037 | 20240912 | 218 | 2566011 | 341 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 6820 | 37.3507 | -121.8744 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0109934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971435 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR092 | 20240912 | 411 | 20240912 | 2142 | 2566130 | 759 | Distribution Circuit | Equipment Failure/Involved | Underground | 1919 | 520481 | 37.3237 | -121.7968 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0110004 | UG | Sus | 46320864 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971469 | 0 | EPSS Ckt | N | 2024 | A & GRD TARGET
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | FUSE | 34252 | 20240912 | 558 | 20240912 | 1916 | 2566160 | 798 | Distribution Circuit | Equipment Failure/Involved | Underground | 368 | 62050 | 37.2192 | -121.763 | No | Partly Cloudy-Fog;32-90 F | Conductor- Underground | Deteriorated | 24-0110216 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971673 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | SWITCH | 333750 | 20240912 | 601 | 20240912 | 1147 | 2566163 | 346 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 22646 | 37.3916 | -121.8112 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0110036 | UG | Sus | 46320817 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971481 | 0 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 30927 | 20240912 | 708 | 20240912 | 2246 | 2566197 | 938 | Distribution Circuit | Vegetation | Tree - grew into line | 53 | 49714 | 37.2899 | -121.9228 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0110460 | OH | Sus | 46320678 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971715 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | SWITCH | 62804SW | 20240913 | 29 | 20240913 | 202 | -2566130 | 93 | Distribution Circuit | Equipment Failure/Involved | Underground | 243 | 15735 | 37.338 | -121.8168 | No | Partly Cloudy;32-90 F | Conductor- Underground | Burned/flashed | 24-0110004 | UG | Sus | 46320864 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 40365 | 20240913 | 1156 | 20240913 | 1359 | 2567475 | 123 | Distribution Circuit | Vegetation | Tree - grew into line | 69 | 8113 | 37.2778 | -121.9161 | No | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0110805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971958 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1105 | 83801105 | TRANSFORMER | T5610 | 20240913 | 1230 | 20240913 | 1320 | 2567513 | 50 | Transformer only | Animal | Other | 11 | 550 | 37.3842 | -121.9116 | No | Clear;32-90 F | Transformer | Arcing | 24-0110836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1971974 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315758629365 | 20240913 | 1322 | 20240913 | 1622 | 2567554 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2340 | 37.2976 | -121.959 | No | Clear;32-90 F | Secondary | Broken | 24-0110844 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1971979 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | JUMPER | OJ'S @ 1401 WILLOW ST | 20240913 | 2130 | 20240914 | 148 | 2567864 | 258 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 3354 | 37.3006 | -121.9183 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972028 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | SWITCH | 40204SW | 20240914 | 5 | 20240914 | 344 | 2567914 | 219 | Distribution Circuit | 3rd Party | Vehicle | 303 | 9647 | 37.2876 | -121.7426 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0110948 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972040 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 28273 | 20240914 | 729 | 20240914 | 846 | 2568001 | 77 | Distribution Circuit | Animal | Squirrel | 4 | 308 | 37.0965 | -121.6334 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0110985 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972093 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | FUSE | 18343 | 20240915 | 1122 | 20240915 | 1315 | 2568728 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 2825 | 37.3002 | -121.9193 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0111169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972251 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | JUMPER | JUMPERS 1/S/SS/ OF CGC 315872329439 | 20240915 | 1325 | 20240915 | 1616 | 2568823 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4275 | 37.3002 | -121.9203 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0111183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972264 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 2615 | 20240915 | 2152 | 20240916 | 0 | 2569134 | 128 | Distribution Circuit | Animal | Other | 254 | 32512 | 37.345 | -121.8153 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111267 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972340 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3747 | 20240916 | 809 | 20240916 | 850 | 2569313 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 105 | 4305 | 37.087 | -121.655 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111358 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972460 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | FUSE | 42227 | 20240916 | 1031 | 20240916 | 1237 | 2569586 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 252 | 37.2933 | -121.8503 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0111444 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972540 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | RECLOSER | XR188 | 20240916 | 1927 | 20240916 | 2150 | 2570066 | 143 | Distribution Circuit | Animal | Bird found | 666 | 95238 | 37.0127 | -121.6026 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111767 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972659 | 0 | EPSS Ckt | Y | 2024 | B PHASE & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20240916 | 2205 | 20240917 | 2 | 2570156 | 117 | Distribution Circuit | Vegetation | Tree - branch fell on line | 400 | 24496 | 37.1083 | -121.7324 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972678 | 0 | EPSS Ckt | Y | 2024 | A- B & 50
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 10831 | 20240917 | 1138 | 20240917 | 1253 | 2570697 | 75 | Distribution Circuit | Animal | Squirrel | 26 | 1950 | 37.0142 | -121.574 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0112017 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1972939 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315908028182 | 20240917 | 1834 | 20240918 | 133 | 2571006 | 419 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3352 | 37.2656 | -121.9073 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0112184 | OH | Sus | 31708899 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1972991 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315979027825 | 20240918 | 1051 | 20240918 | 2259 | 2571498 | 728 | Transformer only | Vegetation | Tree - grew into line | 8 | 5824 | 37.2562 | -121.8827 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0112414 | OH | Sus | 46323261 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1973272 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0405 | 82250405 | JUMPER | OJ 1 SP SE/O CGC# 315998930899 | 20240918 | 1221 | 20240918 | 1455 | 2571697 | 154 | Distribution Circuit | Vegetation | Tree - grew into line | 57 | 8778 | 37.3401 | -121.8772 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0112470 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973292 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 814616 | 20240918 | 1551 | 20240918 | 1657 | 2571863 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2310 | 37.0688 | -121.6174 | No | Clear;32-90 F |  |  | 24-0112698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973347 | 0 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 72381 | 20240918 | 1707 | 20240919 | 333 | 2571936 | 626 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 23773 | 37.0701 | -121.6161 | No | Clear;32-90 F | Jumper | Burned Open | 24-0112746 | OH | Sus | 46323375 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973360 | 0 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315979027825 | 20240919 | 907 | 20240919 | 2240 | 2572360 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 10032 | 37.2562 | -121.8827 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0113139 | OH | Sus | 31709164 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973585 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 28035 | 20240919 | 1040 | 20240919 | 1223 | 2572472 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 618 | 37.0137 | -121.6429 | No | Clear;32-90 F |  |  | 24-0113064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1973558 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 587857 | 20240919 | 1852 | 20240919 | 2008 | 2572879 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 4028 | 37.0314 | -121.5298 | No | Clear;32-90 F |  |  | 24-0113301 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1973631 | 0 | EPSS Ckt | Y | 2024 | B
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 72543 | 20240919 | 2210 | 20240920 | 102 | 2572933 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 7912 | 37.3205 | -121.8191 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0113323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973649 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 27989 | 20240920 | 1930 | 20240921 | 136 | 2573742 | 366 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 10248 | 37.2227 | -121.8739 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0113886 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973953 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1109 | 83871109 | TRANSFORMER | 315895531616 | 20240920 | 2105 | 20240921 | 315 | 2573780 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 11340 | 37.3596 | -121.9136 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0113892 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973958 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | JUMPER | FB EAST OF 71915 | 20240921 | 240 | 20240921 | 647 | 2573819 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 10374 | 37.3262 | -121.841 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0113899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1973970 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315971728070 | 20240921 | 712 | 20240921 | 1645 | 2573845 | 573 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 8595 | 37.2628 | -121.8851 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0113921 | OH | Sus | 46324807 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974037 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315872328042 | 20240921 | 1036 | 20240921 | 1243 | 2574000 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 254 | 37.2616 | -121.9195 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0114004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974094 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | 316134930358 | 20240921 | 1841 | 20240922 | 1242 | 2574222 | 1081 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 14053 | 37.3261 | -121.8303 | No | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 24-0114083 | OH | Sus | 46325041 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974145 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315702029585 | 20240922 | 415 | 20240922 | 628 | 2574343 | 133 | Transformer only | 3rd Party | Vehicle | 8 | 1064 | 37.3035 | -121.9785 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0114096 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974163 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | OJ 1.5 SPANS W/OF CGC 316216931021 | 20240922 | 1016 | 20240922 | 1513 | 2574499 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4455 | 37.3444 | -121.803 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974222 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1110 | 83371110 | TRANSFORMER | 315702029585 | 20240922 | 1914 | 20240923 | 200 | 2574701 | 406 | Transformer only | 3rd Party | Vehicle | 8 | 3248 | 37.3035 | -121.9785 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114158 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974271 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 25119 | 20240922 | 2231 | 20240923 | 1854 | 2574821 | 1223 | Distribution Circuit | Equipment Failure/Involved | Underground | 99 | 67177 | 37.2507 | -121.8439 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0114174 | UG | Sus | 46325052 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974285 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 247498 | 20240922 | 2311 | 20240923 | 1317 | 2574824 | 846 | Distribution Circuit | 3rd Party | Vehicle | 145 | 33826 | 37.354 | -121.7871 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0114172 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974283 | 0 | EPSS Ckt | Y | 2024 | A- B & INST OC
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10345 | 20240923 | 659 | 20240923 | 723 | 2574898 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 144 | 37.101 | -121.621 | No | Clear;32-90 F |  |  | 24-0114202 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974317 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316724822206 | 20240923 | 757 | 20240923 | 2230 | 2574955 | 873 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 873 | 37.1045 | -121.6241 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0114274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974493 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | JUMPER | FB'S IFO 1016 S GENEVIEVE LN | 20240923 | 1648 | 20240923 | 1729 | 2575626 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 5863 | 37.3091 | -121.9425 | No | Partly Cloudy;Above 90 | Crossarm- Wood | Broken | 24-0114493 | OH | Sus | 31709780 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974584 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315806729798 | 20240923 | 2030 | 20240923 | 2311 | 2575772 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 5076 | 37.3095 | -121.9429 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0114493 | OH | Sus | 31709780 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974611 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | JUMPER | FLYING BELLS 1 S/S/O K716 | 20240923 | 2154 | 20240924 | 57 | 2575792 | 183 | Distribution Circuit | Vegetation | Tree - grew into line | 38 | 6954 | 37.2771 | -121.9095 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974619 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 65210 | 20240924 | 227 | 20240925 | 319 | 2575873 | 1341 | Distribution Circuit | Equipment Failure/Involved | Underground | 2600 | 100523 | 37.32 | -121.9749 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0114644 | UG | Sus | 46325770 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974644 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20240924 | 648 | 20240924 | 824 | 2575933 | 96 | Distribution Circuit | Animal | Bird found | 397 | 38112 | 37.1263 | -121.7284 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114671 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974657 | 0 | EPSS Ckt | Y | 2024 | A- B & INST OC
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 11823 | 20240924 | 938 | 20240924 | 1258 | 2576254 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 24800 | 37.2803 | -121.8845 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0114805 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1974842 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72957 | 20240924 | 1652 | 20240924 | 1841 | s1974986 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 646 | 70449 | 37.3536 | -121.8295 | No | Clear;32-90 F | Fuse | Burned Open | 24-0071988 | OH | Sus | 35358715 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974986 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | FUSE | 3085 | 20240924 | 1700 | 20240924 | 1725 | 2576628 | 25 | Distribution Circuit | Animal | Bird found | 10 | 250 | 37.1626 | -121.6837 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0115117 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1974977 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20240924 | 1814 | 20240924 | 1952 | 2576773 | 98 | Distribution Circuit | Animal | Bird found | 856 | 83888 | 37.133 | -121.6122 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1974985 | 0 | EPSS Ckt | Y | 2024 | C & GRD
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315781229869 | 20240925 | 1509 | 20240926 | 250 | 2577631 | 701 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 25 | 17525 | 37.3113 | -121.9514 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0115681 | OH | Sus | 46327148 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1975352 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | JUMPER | JUMPERS IFO 1218 GLENN AVE | 20240925 | 1720 | 20240925 | 2130 | 2577716 | 250 | Distribution Circuit | Vegetation | Tree - grew into line | 18 | 4500 | 37.3064 | -121.9054 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975349 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | JUMPER | OPEN JUMPERS IRO 4966 CAPISTRANO AVE | 20240926 | 1247 | 20240926 | 1736 | 2578399 | 289 | Distribution Circuit | Vegetation | Tree - grew into line | 26 | 7514 | 37.3202 | -121.9896 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116008 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975618 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 28849 | 20240926 | 1736 | 20240926 | 1910 | 2578626 | 94 | Distribution Circuit | Vegetation | Tree - grew into line | 14 | 1316 | 37.2976 | -121.9422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975686 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | FUSE | 26587 | 20240926 | 1824 | 20240926 | 2015 | 2578712 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 16233 | 37.3118 | -121.9412 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0116239 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975693 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 712981 | 20240926 | 1922 | 20240926 | 2310 | 2578755 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 9804 | 37.3148 | -121.9846 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0116272 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975700 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315971028377 | 20240926 | 2000 | 20240927 | 59 | 2578431 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 2691 | 37.2711 | -121.8858 | No | Clear;32-90 F | Bushing | Broken | 24-0116059 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975632 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0410 | 82250410 | TRANSFORMER | 315955230050 | 20240927 | 26 | 20240927 | 206 | 2578910 | 100 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 1900 | 37.3169 | -121.8921 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0116294 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975732 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | TRANSFORMER | 315841630546 | 20240927 | 933 | 20240927 | 1335 | 2579288 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 4114 | 37.3305 | -121.9311 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0116441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | No | 1975904 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | SWITCH | 15353 | 20240927 | 1521 | 20240927 | 1952 | 2579580 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 22493 | 37.3143 | -121.9435 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0116210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1975997 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | OTHER | WIREDOWN 2 SPANS N/OF 40175 | 20240927 | 1816 | 20240928 | 1243 | 2579703 | 1107 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 65 | 35714 | 37.0947 | -121.6117 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0116830 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | Yes | Yes | 1976030 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | JUMPER | FB IFO 2840 EVERGREEN | 20240928 | 1013 | 20240928 | 1918 | 2580038 | 518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 37232 | 37.3063 | -121.7815 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0116862 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976168 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 19775 | 20240929 | 808 | 20240929 | 935 | 2580544 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 7308 | 37.2597 | -121.8894 | No | Clear;32-90 F |  |  | 24-0117030 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976315 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 19415 | 20240929 | 1100 | 20240929 | 1830 | 2580626 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 52650 | 37.2999 | -121.8829 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0117045 | OH | Sus | 31710425 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976328 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | TRANSFORMER | 316494024952 | 20240929 | 1339 | 20240930 | 135 | 2580746 | 716 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 716 | 37.1789 | -121.704 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117099 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976364 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | RECLOSER | XR124 | 20240930 | 1105 | 20240930 | 1556 | 2581305 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 291 | 37.2862 | -121.9143 | No | Clear;32-90 F | Insulator | Broken | 24-0117297 | OH | Sus | 31710485 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976593 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | UNNUMBERED SBCO 1 SPAN S/O 62298 | 20240930 | 1505 | 20240930 | 1715 | 2581590 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1040 | 37.3956 | -121.6557 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0117443 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976639 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 12657 | 20240930 | 1734 | 20240930 | 1821 | 2581684 | 47 | Distribution Circuit | Animal | Squirrel | 118 | 5546 | 37.3049 | -121.9684 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0117516 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976663 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | RECLOSER | XR526 | 20240930 | 2145 | 20241001 | 856 | 2581773 | 671 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 223 | 69488 | 37.3135 | -121.7591 | No | Clear;32-90 F |  |  | 24-0117548 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976679 | 0 | EPSS Ckt | Y | 2024 | C & GRD
SAN JOSE | SAN JOSE | HICKS-1113 | 83431113 | TRANSFORMER | 315873328398 | 20240930 | 2258 | 20241001 | 144 | 2581819 | 166 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 2656 | 37.2713 | -121.9195 | No | Clear;32-90 F | Secondary | Broken | 24-0117553 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Three Phase Fault | 0 | No | No | No | 1976688 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 11821 | 20241001 | 857 | 20241001 | 1709 | 2582070 | 492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 72816 | 37.2741 | -121.8852 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0117648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976816 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315803129283 | 20241001 | 920 | 20241001 | 1108 | 2582155 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1080 | 37.2953 | -121.944 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0117686 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976875 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316625222237 | 20241001 | 1153 | 20241001 | 1331 | 2582337 | 98 | Transformer only | Vegetation | Tree - grew into line | 1 | 98 | 37.105 | -121.6581 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117883 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1976994 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 43263 | 20241001 | 1238 | 20241001 | 1526 | 2582387 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 672 | 37.2222 | -121.8336 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0117853 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1976970 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 42153 | 20241001 | 1540 | 20241001 | 1845 | 2582563 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 15540 | 37.2183 | -121.8686 | No | Clear;Above 90 |  |  | 24-0118037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977040 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315890529765 | 20241001 | 1648 | 20241001 | 2340 | 2582717 | 412 | Transformer only | 3rd Party | Vehicle | 4 | 1648 | 37.3089 | -121.9141 | No | Clear;Above 90 | Transformer | Broken- wire on ground | 24-0118039 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977041 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | TRANSFORMER | T5552 | 20241001 | 1651 | 20241001 | 1817 | 2582610 | 86 | Transformer only | Equipment Failure/Involved | Underground | 15 | 1290 | 37.2631 | -121.856 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0118040 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977042 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | OTHER | WIRE DOWN 1P/NW/O 26693 | 20241001 | 1825 | 20241002 | 442 | 2582784 | 617 | Distribution Circuit | 3rd Party | Vehicle | 10 | 3750 | 36.9666 | -121.5333 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0118057 | OH | Sus | 31710646 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | Yes | 1977054 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 316016726372 | 20241001 | 1942 | 20241002 | 332 | 2582834 | 470 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3760 | 37.2161 | -121.8687 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118078 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977067 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 11181 | 20241001 | 2030 | 20241001 | 2140 | s1982371 | 70 | Distribution Circuit | Company Initiated | Operating error | 6 | 396 | 36.9685 | -121.5415 | No | Clear;Above 90 | Fuse | Failed/Faulted | 24-0118057 | OH | Sus | 31710646 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982371 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | RECLOSER | XR526 | 20241002 | 747 | 20241002 | 1622 | 2583043 | 515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 223 | 41720 | 37.3135 | -121.7591 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0118149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977122 | 0 | EPSS Ckt | Y | 2024 | C & G
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | OCB | 1105/2 | 20241002 | 1550 | 20241003 | 406 | 2583749 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 395 | 49708 | 37.341 | -121.9019 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0118550 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977365 | 0 | Non-EPSS | N | 2024 | C PHASE & GRD TRGTS
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 70553 | 20241002 | 1652 | 20241002 | 1806 | 2583876 | 74 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 493 | 36482 | 37.3677 | -121.8052 | No | Clear;Above 90 | Fuse | Burned Open | 24-0118595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1977379 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | OCB | 1111/2/NORM | 20241002 | 1751 | 20241003 | 241 | 2583941 | 530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4264 | 671552 | 37.2601 | -121.8897 | No | Clear;Above 90 | Connector or Splice (OH) | Broken- wire on ground | 24-0118609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1977388 | 0 | Non-EPSS | N | 2024 | A & B PHASE & GRD TIME OC
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 70553 | 20241002 | 1817 | 20241002 | 1959 | 2583967 | 102 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 493 | 38050 | 37.3677 | -121.8052 | No | Clear;Above 90 | Fuse | Burned Open | 24-0118595 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1977403 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315885230149 | 20241002 | 2108 | 20241003 | 1221 | 2584176 | 913 | Transformer only | Equipment Failure/Involved | Overhead | 80 | 73015 | 37.3194 | -121.9163 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118682 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1977436 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 41027 | 20241002 | 2224 | 20241003 | 1710 | 2584242 | 1126 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3378 | 36.9962 | -121.587 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0118687 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977440 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | TRANSFORMER | 316147827474 | 20241002 | 2318 | 20241003 | 1504 | 2584210 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6696 | 37.247 | -121.8245 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118688 | OH | Sus | 35584897 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977441 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 72929 | 20241003 | 737 | 20241003 | 854 | 2584383 | 77 | Distribution Circuit | Animal | Squirrel | 231 | 17787 | 37.2437 | -121.8938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118777 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1977511 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | TRANSFORMER | 316464924774 | 20241003 | 748 | 20241003 | 1203 | 2584391 | 255 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 255 | 37.174 | -121.7144 | No | Clear;32-90 F | Transformer (OH) |  | 24-0118958 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977617 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1106 | 83801106 | FUSE | 43323 | 20241003 | 800 | 20241003 | 1416 | 2584411 | 376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 502 | 37.3918 | -121.9115 | No | Clear;32-90 F |  |  | 24-0119052 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977632 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2109 | 83392109 | SWITCH | 43326 | 20241003 | 946 | 20241004 | 124 | 2584334 | 938 | Distribution Circuit | 3rd Party | Vehicle | 266 | 11908 | 37.3257 | -121.7704 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0118850 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977586 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | FUSE | 75189 | 20241003 | 1239 | 20241003 | 2031 | 2584705 | 472 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 11328 | 37.3278 | -121.9504 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0118981 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977625 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | TRANSFORMER | 316138030719 | 20241003 | 1711 | 20241003 | 1816 | 2585090 | 65 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 520 | 37.3361 | -121.8293 | No | Clear-Heat Wave;Above 90 | Transformer | Leaking | 24-0119178 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977668 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 40918 | 20241003 | 1825 | 20241004 | 1443 | 2585192 | 1218 | Distribution Circuit | Equipment Failure/Involved | Underground | 89 | 32665 | 37.199 | -121.8349 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0119232 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977691 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | INTERRUPTER | 30034 | 20241004 | 23 | 20241004 | 1838 | 2585311 | 1095 | Distribution Circuit | Equipment Failure/Involved | Underground | 1512 | 399452 | 37.2992 | -121.8232 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0119275 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977732 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | RECLOSER | XR248 | 20241004 | 655 | 20241004 | 907 | 2585425 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 416 | 54912 | 37.2105 | -121.8595 | No | Partly Cloudy;32-90 F |  |  | 24-0119295 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1977753 | 0 | EPSS Ckt | Y | 2024 | B/GRD
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | FUSE | 28865 | 20241004 | 935 | 20241004 | 1106 | 2585613 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 8099 | 37.3271 | -121.9551 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0119376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977855 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 41785 | 20241004 | 1838 | 20241004 | 2234 | 2586107 | 236 | Distribution Circuit | Vegetation | Tree - grew into line | 209 | 49324 | 37.3077 | -121.9668 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0119587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977951 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315975829469 | 20241004 | 2003 | 20241004 | 2024 | 2586145 | 21 | Transformer only | Vegetation | Tree - palm frond fell into line | 15 | 315 | 37.3011 | -121.8846 | No | Clear;32-90 F | Secondary | Normal | 24-0119706 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1977968 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | FUSE | 26259 | 20241005 | 701 | 20241005 | 1219 | 2586549 | 318 | Distribution Circuit | Equipment Failure/Involved | Underground | 163 | 44778 | 37.2715 | -121.831 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0119781 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978063 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 4621 | 20241005 | 737 | 20241005 | 1433 | 2586561 | 416 | Distribution Circuit | Animal | Bird found | 116 | 46948 | 37.0199 | -121.5727 | No | Clear;32-90 F | Jumper | Normal | 24-0119823 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978089 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 25337 | 20241005 | 803 | 20241005 | 1113 | 2586594 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 44080 | 37.257 | -121.883 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0119773 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978054 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 33322 | 20241005 | 1421 | 20241006 | 726 | 2586836 | 1025 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 30758 | 37.2999 | -121.8026 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0119853 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978101 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | OCB | 2107/2 | 20241005 | 1724 | 20241005 | 1822 | 2586970 | 58 | Distribution Circuit | 3rd Party | Metallic Balloon | 4047 | 209496 | 37.0071 | -121.5569 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0119861 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1978107 | 0 | EPSS Ckt | Y | 2024 | A & B (INST)
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 40237 | 20241005 | 2246 | 20241006 | 705 | 2587071 | 499 | Distribution Circuit | 3rd Party | Vandalism | 3 | 1497 | 37.2907 | -121.8785 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0119891 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1978129 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316214631402 | 20241005 | 2301 | 20241006 | 125 | 2587076 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 576 | 37.355 | -121.8033 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978137 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 73325 | 20241005 | 2356 | 20241006 | 137 | 2587093 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 8282 | 37.2934 | -121.8439 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0119895 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978132 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316888318739 | 20241006 | 1042 | 20241007 | 35 | 2587359 | 833 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 21520 | 37.0097 | -121.5665 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978197 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316214631402 | 20241006 | 1210 | 20241006 | 1430 | 2587458 | 140 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 560 | 37.355 | -121.8033 | No | Clear;Above 90 | Transformer (OH) | Leaking | 24-0119965 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978213 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | TRANSFORMER | 315790730759 | 20241006 | 1750 | 20241007 | 451 | 2587806 | 661 | Transformer only | Environmental/External | Flood/Erosion | 7 | 4627 | 37.3364 | -121.9483 | No | Partly Cloudy;Above 90 | Transformer | Leaking | 24-0120019 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978269 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | TRANSFORMER | 315967927583 | 20241006 | 1816 | 20241006 | 1953 | 2587673 | 97 | Transformer only | Unknown Cause | Patrol - found nothing | 12 | 1164 | 37.2494 | -121.8864 | No | Clear;32-90 F |  |  | 24-0120004 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1978255 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | 316018027984 | 20241006 | 2149 | 20241007 | 1036 | 2587803 | 767 | Transformer only | Vegetation | Tree - grew into line | 15 | 11505 | 37.2608 | -121.8697 | No | Clear;32-90 F | Secondary | Normal | 24-0120034 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978285 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1115 | 82261115 | TRANSFORMER | 315919830705 | 20241007 | 1407 | 20241008 | 311 | 2588493 | 784 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 784 | 37.3348 | -121.9046 | No | Partly Cloudy;Above 90 | Jumper | Burned Open | 24-0120420 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1978625 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20241007 | 1412 | 20241007 | 1447 | 2588501 | 35 | Distribution Circuit | Company Initiated | Personnel- company | 48 | 1680 | 37.053 | -121.5276 | No | Clear;Above 90 | Fuse | Normal | 24-0120316 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978574 | 0 | EPSS Ckt | Y | 2024 | B PHASE OC
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 33226 | 20241007 | 1524 | 20241007 | 1816 | 2588547 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 17544 | 37.2278 | -121.8846 | No | Clear;Above 90 |  |  | 24-0120403 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978612 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | OTHER | T21963 TWD T21962 | 20241007 | 1645 | 20241007 | 1737 | 2588654 | 52 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 1248 | 37.342 | -121.8743 | No | Partly Cloudy;Above 90 | Transformer (UG) | Leaking | 24-0120329 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978609 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | TRANSFORMER | T6895 | 20241007 | 1848 | 20241008 | 535 | 2588856 | 642 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 11670 | 37.2237 | -121.8846 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0120438 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978638 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | OJ @ HAYWORTH & FLINTHAVEN | 20241007 | 1950 | 20241008 | 58 | 2588933 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4620 | 37.3444 | -121.803 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0120437 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1978637 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316888318739 | 20241008 | 1138 | 20241008 | 2156 | 2589548 | 618 | Transformer only | Equipment Failure/Involved | Overhead | 32 | 19776 | 37.0097 | -121.5665 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0120750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978918 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 11329 | 20241008 | 1434 | 20241008 | 1757 | 2589727 | 203 | Distribution Circuit | Equipment Failure/Involved | Underground | 275 | 43377 | 37.4515 | -121.8936 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0120853 | UG | Sus | 46333367 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1978948 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | JUMPER | 40333 | 20241009 | 838 | 20241009 | 1438 | 2590348 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 10943 | 37.2317 | -121.8715 | No | Clear;32-90 F | Jumper | Burned Open | 24-0121218 | OH | Sus | 46333574 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979221 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315791829745 | 20241009 | 1357 | 20241009 | 1530 | 2590752 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 46 | 4278 | 37.308 | -121.9479 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0121340 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979271 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 75211 | 20241009 | 1850 | 20241010 | 15 | 2591029 | 325 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 4875 | 37.3053 | -121.9429 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0121536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979309 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | SWITCH | 30398 | 20241009 | 1915 | 20241009 | 2154 | 2591033 | 116 | Distribution Circuit | Equipment Failure/Involved | Underground | 493 | 18510 | 37.3447 | -121.8728 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0121509 | UG | Sus | 35586671 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979312 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | FUSE | 75491 | 20241009 | 2015 | 20241009 | 2331 | 2591077 | 196 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 2940 | 37.3053 | -121.9371 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0121559 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979324 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315910328155 | 20241010 | 1258 | 20241010 | 2255 | 2591621 | 597 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 10746 | 37.2649 | -121.9064 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0121931 | OH | Sus | 46337578 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1979569 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 23343 | 20241010 | 1409 | 20241010 | 1552 | 2591673 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 206 | 37.0636 | -121.583 | No | Clear;32-90 F |  |  | 24-0121935 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979571 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 13749 | 20241010 | 1902 | 20241010 | 2248 | 2591841 | 226 | Distribution Circuit | Vegetation | Tree - grew into line | 177 | 40002 | 37.2766 | -121.8986 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121995 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1979583 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20241010 | 2305 | 20241011 | 1343 | 2591910 | 878 | Distribution Circuit | Equipment Failure/Involved | Overhead | 402 | 61356 | 37.1438 | -121.669 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0122029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1979616 | 0 | EPSS Ckt | Y | 2024 | B- C & INST
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 40017 | 20241011 | 652 | 20241011 | 735 | 2592010 | 43 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 43 | 37.2898 | -121.8807 | No | Clear;32-90 F |  |  | 24-0122077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979654 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2106 | 82462106 | OCB | 2106/22 | 20241011 | 913 | 20241012 | 645 | 2592203 | 1009 | Distribution Circuit | Equipment Failure/Involved | Underground | 1375 | 149304 | 37.4209 | -121.9605 | No | Overcast;32-90 F | Switch (UG) | Failed/Faulted | 24-0122156 | UG | Sus | 31712190 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979774 | 0 | Non-EPSS | N | 2024 | GRD OC
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 28807 | 20241011 | 1611 | 20241012 | 1003 | 2592545 | 1072 | Distribution Circuit | 3rd Party | Vehicle | 14 | 15008 | 37.2326 | -121.8717 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0122429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | Yes | No | 1979867 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 4523 | 20241012 | 158 | 20241012 | 508 | 2592688 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 12350 | 37.0193 | -121.5204 | No | Partly Cloudy;32-90 F |  |  | 24-0122493 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1979906 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | OCB | 1112/2 | 20241012 | 838 | 20241012 | 1115 | 2592839 | 157 | Distribution Circuit | Animal | Squirrel | 2713 | 406865 | 37.3282 | -121.9025 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0122522 | OH | Sus | 46338424 | SOUTH BAY AND CENTRAL COAST | OCT | Open Circuit | 0 | No | No | No | 1979966 | 0 | Non-EPSS | N | 2024 | ABC
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316852319346 | 20241012 | 1256 | 20241013 | 146 | 2593055 | 770 | Transformer only | Equipment Failure/Involved | Electrical Overload | 8 | 6160 | 37.0262 | -121.5795 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0122607 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980038 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20241013 | 25 | 20241013 | 944 | 2593351 | 559 | Distribution Circuit | Animal | Bird found | 5 | 2795 | 36.9852 | -121.4853 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0122673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980117 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | T798225 | 20241013 | 257 | 20241014 | 26 | 2593380 | 1289 | Transformer only | Equipment Failure/Involved | Fire- pole | 23 | 29647 | 37.1156 | -121.6437 | No | Overcast;32-90 F | Pole - Tower- steel | Bent or Twisted | 24-0122651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980085 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2116 | 83802116 | RECLOSER | 699544 | 20241013 | 1035 | 20241013 | 1106 | 2593514 | 31 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 289 | 8959 | 37.3776 | -121.8985 | No | Overcast;32-90 F |  |  | 24-0122680 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1980126 | 0 | Non-EPSS | N | 2024 | A/B/C/GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316665922601 | 20241013 | 1514 | 20241014 | 18 | 2593617 | 544 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2720 | 37.1152 | -121.6445 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0122725 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1980156 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | T1170 | 20241014 | 48 | 20241014 | 304 | 2593791 | 136 | Transformer only | 3rd Party | Customer Equipment | 8 | 1088 | 37.3335 | -121.8575 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0122743 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980173 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | T1170 | 20241014 | 727 | 20241014 | 1017 | 2593899 | 170 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 1360 | 37.3335 | -121.8575 | No | Overcast;32-90 F | Customer Equipment | Burned/flashed | 24-0122868 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980388 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1118 | 82921118 | FUSE | 42955 | 20241014 | 1607 | 20241014 | 2123 | 2594554 | 316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 9480 | 37.2751 | -121.9201 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0123072 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980474 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 41443 | 20241014 | 1706 | 20241014 | 1810 | 2594609 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 1600 | 37.2951 | -121.886 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0123095 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980481 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | FUSE | 33322 | 20241014 | 1807 | 20241015 | 308 | 2594635 | 541 | Distribution Circuit | Equipment Failure/Involved | Underground | 66 | 14592 | 37.2999 | -121.8026 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0123114 | UG | Sus | 46339287 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980488 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | FUSE | 40719 | 20241015 | 1018 | 20241015 | 1237 | 2595170 | 139 | Distribution Circuit | Equipment Failure/Involved | Underground | 138 | 3438 | 37.2722 | -121.7423 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0123237 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980748 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | TRANSFORMER | 315849730141 | 20241015 | 1911 | 20241015 | 2205 | 2595651 | 174 | Transformer only | Vegetation | Tree - grew into line | 16 | 2784 | 37.3191 | -121.9283 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0123587 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1980841 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 12893 | 20241015 | 2123 | 20241015 | 2129 | 2595696 | 6 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 351 | 2106 | 37.3522 | -121.8463 | No | Clear;32-90 F | Fuse | Burned Open | 24-0117281 | OH | Sus | 35358721 | SOUTH BAY AND CENTRAL COAST | OCT | Multi-Fault | 0 | No | No | No | 1980864 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20241015 | 2201 | 20241015 | 2302 | 2595652 | 61 | Distribution Circuit | Animal | Bird found | 5 | 305 | 36.9852 | -121.4853 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123624 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1980868 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 12765 | 20241016 | 714 | 20241016 | 728 | 2595775 | 14 | Distribution Circuit | 3rd Party | Metallic Balloon | 230 | 3220 | 37.3201 | -121.8198 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0123672 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980889 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2110 | 83912110 | OTHER | J5195 TWD T21032 | 20241016 | 940 | 20241016 | 1403 | 2596024 | 263 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 5523 | 37.2715 | -121.7365 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0123554 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981041 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | TRANSFORMER | 315736829985 | 20241016 | 947 | 20241016 | 1913 | 2596037 | 566 | Transformer only | Equipment Failure/Involved | Overhead | 28 | 15848 | 37.3144 | -121.9666 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0123953 | OH | Sus | 31712925 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981075 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 257532 | 20241016 | 1121 | 20241016 | 1341 | 2596143 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 383 | 5156 | 37.3508 | -121.8453 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0123822 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981078 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | JUMPER | OJ AT 9931 TWD CGC 1679 | 20241016 | 1511 | 20241016 | 1812 | 2596399 | 181 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 362 | 37.362 | -121.8085 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0124116 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981149 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR144 | 20241017 | 1151 | 20241017 | 1401 | 2597106 | 130 | Distribution Circuit | 3rd Party | Other | 2612 | 325074 | 37.0009 | -121.5659 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0124523 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981311 | 0 | EPSS Ckt | Y | 2024 | B PHASE & GRD
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | TRANSFORMER | T10107 | 20241017 | 1339 | 20241017 | 1502 | 2597302 | 83 | Transformer only | Animal | Squirrel | 45 | 3735 | 37.325 | -121.8367 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981403 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 13291 | 20241017 | 1745 | 20241017 | 2204 | 2597633 | 259 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 7511 | 37.3051 | -121.9436 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0124758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981464 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | SWITCH | 11327 | 20241017 | 1947 | 20241019 | 1528 | 2597858 | 2602 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 191 | 496730 | 37.4516 | -121.8471 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124150 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981518 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20241018 | 10 | 20241019 | 1110 | 2598077 | 2100 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 214 | 449400 | 37.1869 | -121.8177 | No | Clear;32-90 F |  |  | 24-0124025 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981600 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20241018 | 18 | 20241019 | 1302 | 2598081 | 2204 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 64 | 141056 | 37.1083 | -121.7324 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124087 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981602 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20241018 | 18 | 20241019 | 1307 | 2598088 | 2209 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 64 | 141376 | 37.0838 | -121.7753 | No | Clear;32-90 F |  |  | 24-0124087 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981603 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20241018 | 30 | 20241019 | 1333 | 2598105 | 2223 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 18 | 40014 | 37.1127 | -121.7585 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124087 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981606 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 544227 | 20241018 | 31 | 20241019 | 1322 | s1981608 | 2211 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 37 | 81807 | 37.1117 | -121.7369 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124087 | OH | Sus | 8216649 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981608 | 0 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 5963 | 20241018 | 744 | 20241018 | 924 | 2598271 | 100 | Distribution Circuit | Animal | Squirrel | 2 | 200 | 37.3539 | -121.9019 | No | Clear;32-90 F | Fuse | Broken | 24-0124934 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981700 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2106 | 82462106 | OCB | 2106/22 | 20241018 | 1038 | 20241018 | 1218 | 2598565 | 100 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1319 | 131800 | 37.4209 | -121.9605 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0125027 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981779 | 0 | Non-EPSS | N | 2024 | INST OC & GRD
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | OJ'S @ 3185 DRYDEN AVE | 20241018 | 1040 | 20241018 | 1325 | 2598540 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 495 | 37.0425 | -121.5255 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0125006 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981770 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 71627 | 20241018 | 1040 | 20241018 | 1740 | 2598552 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8820 | 37.3588 | -121.832 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0125016 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981774 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | SWITCH | 29242 | 20241018 | 2253 | 20241019 | 932 | 2599044 | 639 | Distribution Circuit | Equipment Failure/Involved | Underground | 113 | 23067 | 37.3108 | -121.8813 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0125245 | UG | Sus | 35591394 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1981877 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 79927 | 20241019 | 1057 | 20241019 | 1525 | 2599328 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2736 | 36.9656 | -121.5641 | No | Clear;32-90 F | Recloser | Failed/Faulted | 24-0125392 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1981992 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316605322854 | 20241019 | 1338 | 20241019 | 2004 | 2599379 | 386 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 2702 | 37.1219 | -121.6653 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0125429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | Yes | No | 1982019 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 12207 | 20241019 | 2141 | 20241020 | 158 | 2599587 | 257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 27872 | 37.3041 | -121.8829 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0125478 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982043 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 28073 | 20241020 | 750 | 20241020 | 845 | 2599672 | 55 | Distribution Circuit | Animal | Squirrel | 101 | 5555 | 37.2858 | -121.8801 | No | Clear;32-90 F | Fuse | Normal | 24-0125511 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982084 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 18381 | 20241020 | 928 | 20241020 | 955 | 2599705 | 27 | Distribution Circuit | Animal | Squirrel | 5 | 135 | 37.3692 | -121.8923 | No | Clear;32-90 F | Fuse | Normal | 24-0125515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982094 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | OCB | 2103/2 | 20241020 | 1241 | 20241020 | 1342 | 2599802 | 61 | Distribution Circuit | 3rd Party | Metallic Balloon | 6165 | 376065 | 37.3036 | -121.8398 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0125542 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1982114 | 0 | Non-EPSS | N | 2024 | A-B & C PHASE & TIME OC
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | FUSE | 14439 | 20241021 | 929 | 20241021 | 948 | 2600250 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 19 | 37.3052 | -121.8507 | No | Clear;32-90 F |  |  | 24-0125692 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1982307 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 2227 | 20241021 | 1851 | 20241022 | 628 | 2600737 | 679 | Distribution Circuit | Equipment Failure/Involved | Underground | 57 | 15561 | 37.3114 | -121.8813 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0125845 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982413 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | FUSE | 9719 | 20241021 | 2106 | 20241022 | 1450 | 2600774 | 1064 | Distribution Circuit | Equipment Failure/Involved | Underground | 77 | 60952 | 37.2803 | -121.9223 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0126047 | UG | Sus | 46342890 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982429 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | OCB | 2102/2 | 20241022 | 1319 | 20241101 | 1449 | 2601404 | 740 | Distribution Circuit | Equipment Failure/Involved | Underground | 3808 | 418334 | 37.3226 | -121.7972 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0126379 | UG | Sus | 31713239 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982693 | 0 | EPSS Ckt | N | 2024 | GRD B PHASE
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | JUMPER | OPEN JUMPERS @ 1287 SOUTH WHITE ROAD | 20241022 | 1809 | 20241023 | 141 | 2601608 | 452 | Distribution Circuit | Vegetation | Tree - grew into line | 40 | 18080 | 37.353 | -121.8163 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0126562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982728 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | SWITCH | 13768 | 20241022 | 2145 | 20241023 | 443 | 2601682 | 418 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 7106 | 37.3882 | -121.8602 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0126598 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1982750 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | TRANSFORMER | T6681 | 20241023 | 813 | 20241023 | 1527 | 2601817 | 434 | Transformer only | Environmental/External | Water | 17 | 7378 | 37.3881 | -121.8603 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0126758 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1982945 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 40353 | 20241023 | 1300 | 20241023 | 1430 | 2602351 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 270 | 37.0924 | -121.5987 | No | Clear;32-90 F | Fuse | Normal | 24-0126992 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983041 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 40351 | 20241024 | 1228 | 20241024 | 1350 | s1983359 | 82 | Distribution Circuit | Animal | Bird found | 1 | 82 | 37.0917 | -121.5983 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127620 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983359 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | TRANSFORMER | T6681 | 20241024 | 1350 | 20241024 | 1653 | 2603158 | 183 | Transformer only | 3rd Party | Customer Equipment | 17 | 3111 | 37.3881 | -121.8603 | No | Partly Cloudy;32-90 F | Customer Equipment | Malfunctioning | 24-0127502 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983332 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4643 | 20241024 | 1603 | 20241025 | 1732 | 2603219 | 1307 | Distribution Circuit | Equipment Failure/Involved | Underground | 718 | 293857 | 37.0085 | -121.5846 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0127609 | UG | Sus | 46344065 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983351 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | JUMPER | OJ'S @ 1666 CREEK DR | 20241025 | 910 | 20241025 | 1757 | 2603717 | 527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 4216 | 37.3045 | -121.883 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0127754 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1983504 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 40353 | 20241025 | 1540 | 20241025 | 1720 | 2604047 | 100 | Distribution Circuit | Animal | Bird found | 3 | 300 | 37.0924 | -121.5987 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128064 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983619 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 6115 | 20241026 | 800 | 20241026 | 1040 | 2604668 | 160 | Distribution Circuit | Animal | Squirrel | 1 | 160 | 37.2765 | -121.8949 | No | Clear;32-90 F | Fuse | Normal | 24-0128137 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983733 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | FUSE | 26345 | 20241026 | 831 | 20241026 | 1308 | 2604620 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 24721 | 37.0179 | -121.5864 | No | Clear;32-90 F |  |  | 24-0128173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983779 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | OCB | 1105/2 | 20241026 | 1302 | 20241026 | 1615 | 2604903 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2195 | 204342 | 37.2915 | -121.9358 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0128171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983794 | 0 | Non-EPSS | N | 2024 | N/A
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | SWITCH | 4310 | 20241026 | 2044 | 20241028 | 317 | 2605133 | 1833 | Distribution Circuit | Equipment Failure/Involved | Underground | 272 | 147076 | 37.2867 | -121.8417 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0128178 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1983845 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1104 | 82921104 | TRANSFORMER | T11081 | 20241027 | 2328 | 20241028 | 1841 | 2605640 | 1153 | Distribution Circuit | Equipment Failure/Involved | Underground | 169 | 32668 | 37.2955 | -121.9236 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0128356 | UG | Sus | 35592923 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1983977 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | JUMPER | FLYING BELLS 1/SP/W/O TX CGC# 315796730661 | 20241028 | 1412 | 20241028 | 1629 | 2606377 | 137 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 3699 | 37.3339 | -121.9469 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0128621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984211 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | JUMPER | OJ SS OF CGC 315822429519 | 20241028 | 1646 | 20241028 | 1935 | 2606502 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2535 | 37.3018 | -121.9371 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0128708 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984238 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2101 | 82012101 | FUSE | 33292 | 20241028 | 1909 | 20241028 | 2313 | 2606598 | 161 | Distribution Circuit | Equipment Failure/Involved | Underground | 151 | 27910 | 37.2986 | -121.8228 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0128769 | UG | Sus | 46345319 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984257 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 41961 | 20241029 | 1022 | 20241029 | 1915 | 2607179 | 533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 19188 | 37.3386 | -121.9114 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0128923 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984494 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 71249 | 20241029 | 1130 | 20241030 | 0 | 2607175 | 750 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 750 | 37.3389 | -121.9111 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0128919 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1984493 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | SWITCH | 33216SW | 20241029 | 2046 | 20241030 | 125 | 2607814 | 279 | Distribution Circuit | Equipment Failure/Involved | Underground | 114 | 10782 | 37.2842 | -121.819 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0129107 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984628 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | TRANSFORMER | 315925827591 | 20241029 | 2323 | 20241030 | 804 | 2607853 | 521 | Transformer only | Vegetation | Tree - fell into line | 12 | 6252 | 37.2494 | -121.9008 | No | Clear;32-90 F | Secondary | Broken | 24-0129311 | OH | Sus | 46346254 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1984647 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | RECLOSER | XR086 | 20241030 | 801 | 20241030 | 1121 | 2607962 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2661 | 520725 | 37.3083 | -121.7626 | No | Overcast;32-90 F |  |  | 24-0129410 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984705 | 0 | EPSS Ckt | N | 2024 | B PH- GRD
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 6069 | 20241030 | 1005 | 20241030 | 2328 | 2608254 | 803 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 27 | 21681 | 37.3063 | -121.8895 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0129571 | UG | Sus | 46352326 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1984889 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | OTHER | T21874 TWD T21876 | 20241030 | 1100 | 20241030 | 1335 | 2608325 | 155 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 7130 | 37.3461 | -121.8522 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0129503 | UG | Sus | 35593337 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1984871 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 72039 | 20241030 | 1819 | 20241030 | 2120 | 2608666 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 216 | 15617 | 37.3768 | -121.8014 | No | Clear;32-90 F |  |  | 24-0129769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1984977 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2106 | 83182106 | FUSE | 5159 | 20241030 | 2050 | 20241030 | 2251 | 2608768 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 605 | 36.9852 | -121.4853 | No | Overcast;32-90 F |  |  | 24-0129803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1985003 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | SWITCH | X2002 | 20241031 | 138 | 20241031 | 149 | 2608874 | 11 | Distribution Circuit | Vegetation | Tree - grew into line | 8176 | 89936 | 37.285 | -121.8577 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 24-0129824 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985020 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20241031 | 619 | 20241031 | 818 | 2609093 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 6902 | 37.053 | -121.5276 | No | Overcast-Fog;32-90 F |  |  | 24-0129877 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985065 | 0 | EPSS Ckt | Y | 2024 | B
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | SWITCH | X1892 | 20241031 | 731 | 20241031 | 1551 | 2609099 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 6085 | 37.012 | -121.5389 | No | Overcast-Fog-Rain;32-90 F | Jumper | Burned/flashed | 24-0129899 | OH | Sus | 31714177 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985073 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13925 | 20241031 | 908 | 20241031 | 1253 | 2609306 | 131 | Distribution Circuit | Equipment Failure/Involved | Underground | 136 | 24677 | 37.3267 | -121.848 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0130044 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1985234 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | SWITCH | 14760 | 20241031 | 935 | 20241031 | 1010 | 2609355 | 35 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 35 | 37.4473 | -121.877 | No | Clear;32-90 F | Insulator | Broken | 24-0129976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1985191 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 18493 | 20241031 | 1329 | 20241031 | 1442 | 2609684 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 2993 | 37.3991 | -121.844 | No | Clear;32-90 F |  |  | 24-0130222 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Line | 0 | No | No | No | 1985310 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1108 | 82921108 | FUSE | 12473 | 20241101 | 1120 | 20241101 | 1715 | 2610310 | 355 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 66 | 21330 | 37.3061 | -121.9497 | No | Overcast;32-90 F | Conductor- Overhead | Contaminated | 24-0130477 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985540 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | TRANSFORMER | 316050231362 | 20241101 | 1613 | 20241102 | 248 | 2610682 | 617 | Transformer only | Equipment Failure/Involved | Overhead | 36 | 22212 | 37.3535 | -121.8599 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0130701 | OH | Sus | 31714711 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985600 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | T25089 | 20241101 | 1618 | 20241102 | 1412 | 2610675 | 1314 | Transformer only | Equipment Failure/Involved | Underground | 2 | 2628 | 37.3614 | -121.8968 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 24-0130703 | UG | Sus | 46365279 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985602 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 13949 | 20241102 | 223 | 20241102 | 1123 | 2611114 | 540 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 51429 | 37.3192 | -121.8566 | No | Partly Cloudy;32-90 F |  |  | 24-0130938 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1985835 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316218031091 | 20241102 | 229 | 20241102 | 1521 | 2611006 | 772 | Transformer only | Vegetation | Tree - grew into line | 8 | 6176 | 37.3467 | -121.8017 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 24-0130809 | OH | Sus | 46368664 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985674 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20241102 | 240 | 20241102 | 1017 | 2611140 | 457 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1008 | 460114 | 37.0163 | -121.5446 | No | Overcast-Rain;32-90 F |  |  | 24-0130810 | OH | Sus | 46369787 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985675 | 0 | EPSS Ckt | Y | 2024 | B & C GRD
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 21231 | 20241102 | 612 | 20241102 | 1013 | 2611189 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 30848 | 37.3775 | -121.8315 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 24-0130835 | OH | Sus | 31714714 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985699 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 28291 | 20241102 | 711 | 20241102 | 1206 | 2611269 | 295 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 70 | 20650 | 37.3121 | -121.9592 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0130845 | OH | Sus | 31715155 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985715 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 71011 | 20241102 | 810 | 20241102 | 2205 | 2611418 | 835 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 3235 | 37.2374 | -121.8636 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0130966 | UG | Sus | 35595590 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985867 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 28839 | 20241102 | 1251 | 20241102 | 1521 | 2611696 | 150 | Distribution Circuit | Vegetation | Tree - grew into line | 50 | 7500 | 37.3467 | -121.8017 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0130953 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985848 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 2517 | 20241102 | 1747 | 20241103 | 1426 | 2611917 | 1239 | Distribution Circuit | 3rd Party | Vehicle | 2 | 2478 | 37.0971 | -121.6188 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0131038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985905 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | 1 | 20241103 | 849 | 20241103 | 1058 | 2612245 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2709 | 37.0648 | -121.5598 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131093 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985959 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 27979 | 20241103 | 930 | 20241103 | 1126 | 2612301 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 4408 | 37.2278 | -121.9005 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1985990 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 72141 | 20241103 | 1000 | 20241103 | 1346 | 2612313 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 510 | 33045 | 37.3557 | -121.83 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0130970 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1985975 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | OCB | 1107/2 | 20241103 | 2219 | 20241104 | 635 | 2612751 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3908 | 628989 | 37.3043 | -121.8681 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0131217 | OH | Sus | 46379952 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986050 | 0 | Non-EPSS | N | 2024 | B & GRD
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 2337 | 20241104 | 856 | 20241104 | 957 | 2613082 | 61 | Distribution Circuit | Animal | Squirrel | 25 | 1525 | 37.2757 | -121.8024 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131336 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986229 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | TRANSFORMER | 316625020290 | 20241104 | 911 | 20241104 | 1009 | 2613152 | 58 | Transformer only | Animal | Squirrel | 4 | 232 | 37.052 | -121.658 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0131361 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1986263 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | TRANSFORMER | 315791230694 | 20241104 | 1034 | 20241104 | 1702 | 2613278 | 388 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 1552 | 37.3348 | -121.9479 | No | Clear;32-90 F | Transformer | Broken | 24-0131375 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986272 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 25501 | 20241104 | 1516 | 20241104 | 2304 | 2613574 | 468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 936 | 37.3331 | -121.7525 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131606 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986365 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 11941 | 20241104 | 2021 | 20241105 | 543 | 2613711 | 562 | Distribution Circuit | Vegetation | Tree - grew into line | 183 | 102846 | 37.223 | -121.8636 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131707 | OH | Sus | 46381584 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986389 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR246 | 20241104 | 2159 | 20241106 | 30 | 2613751 | 1591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4002 | 70221 | 37.1236 | -121.641 | No | Clear;32-90 F | Pole-Wood | On Ground | 24-0131719 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986398 | 0 | EPSS Ckt | Y | 2024 | NONE
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | FUSE | 28671 | 20241105 | 1048 | 20241105 | 1936 | 2614264 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 11088 | 37.3053 | -121.9947 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0132029 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986617 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 100000159918 | 20241105 | 1050 | 20241105 | 1214 | 2614253 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1512 | 37.2835 | -121.83 | Yes | Partly Cloudy;32-90 F | Secondary | Bent or Twisted | 24-0132025 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986615 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | SWITCH | 42948 | 20241105 | 1057 | 20241105 | 1232 | 2614271 | 95 | Distribution Circuit | Equipment Failure/Involved | Underground | 105 | 9975 | 37.278 | -121.8544 | Yes | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0131579 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986618 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | RECLOSER | 574315 | 20241105 | 2313 | 20241106 | 1531 | 2615130 | 978 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 214 | 209292 | 37.1869 | -121.8177 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986852 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20241105 | 2319 | 20241106 | 1814 | 2615144 | 1135 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 18 | 20430 | 37.1127 | -121.7585 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986860 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 123422 | 20241105 | 2319 | 20241106 | 1748 | 2615149 | 1109 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 15 | 16635 | 37.0845 | -121.7133 | Yes | Clear;32-90 F |  |  | 24-0131752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986862 | 0 | EPSS Ckt | Y | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 419718 | 20241105 | 2319 | 20241106 | 1732 | 2615152 | 1093 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 64 | 69952 | 37.0838 | -121.7753 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986864 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 699122 | 20241105 | 2319 | 20241106 | 1717 | 2615154 | 1078 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 63 | 67914 | 37.1694 | -121.757 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986866 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20241105 | 2320 | 20241106 | 1709 | 2615134 | 1069 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 176 | 188144 | 37.1263 | -121.7284 | Yes | Clear;32-90 F |  |  | 24-0131752 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986856 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 919856 | 20241105 | 2327 | 20241106 | 1727 | 2615158 | 1080 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 64 | 69120 | 37.1083 | -121.7324 | Yes | Clear;32-90 F |  |  | 24-0131752 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986870 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR044 | 20241106 | 18 | 20241107 | 1002 | 2615306 | 2024 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 103224 | 37.4385 | -121.8718 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986878 | 0 | EPSS Ckt | N | 2024 | n/a
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR374 | 20241106 | 18 | 20241107 | 1003 | 2615325 | 2025 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 15 | 30375 | 37.4464 | -121.8577 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986885 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | XR524 | 20241106 | 18 | 20241107 | 1138 | 2615327 | 2120 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 45 | 95400 | 37.4495 | -121.8476 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986887 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20241106 | 18 | 20241107 | 1139 | 2615328 | 2121 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 214 | 453894 | 37.4483 | -121.8461 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986888 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | SWITCH | 616022 | 20241106 | 19 | 20241107 | 1104 | 2615301 | 2085 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 119 | 248115 | 37.3256 | -121.6734 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1986877 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | 712931 SB | 20241106 | 19 | 20241107 | 1104 | 2617151 | 2085 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2085 | 37.392 | -121.4503 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987313 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | FUSE | 19341 | 20241106 | 27 | 20241106 | 1748 | 2615330 | 1041 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 5205 | 37.3632 | -121.7577 | No | Partly Cloudy;32-90 F |  |  | 24-0131784 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1986889 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 25031 | 20241106 | 755 | 20241106 | 1101 | 2615974 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 930 | 37.0624 | -121.597 | No | Clear;32-90 F |  |  | 24-0132565 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1987204 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316070131222 | 20241106 | 853 | 20241106 | 1617 | 2616184 | 444 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 6216 | 37.3496 | -121.8531 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0132491 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987117 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315884434389 | 20241106 | 1023 | 20241106 | 1930 | 2616142 | 547 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 5470 | 37.436 | -121.9188 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0132586 | OH | Sus | 46382209 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1987216 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2110 | 82462110 | FUSE | 1687 | 20241106 | 1230 | 20241106 | 1916 | 2616810 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1218 | 37.4318 | -121.9634 | No | Clear;32-90 F | Insulator | Broken | 24-0132665 | OH | Sus | 31716782 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987257 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 40263 | 20241106 | 1411 | 20241106 | 1545 | 2616933 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 94 | 37.0127 | -121.5672 | No | Clear;32-90 F |  |  | 24-0132809 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987303 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | OTHER | J5667 TWD T25055 | 20241107 | 855 | 20241107 | 918 | 2617692 | 23 | Distribution Circuit | Company Initiated | Improper Construction | 1 | 23 | 37.2755 | -121.8017 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0132621 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987487 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | OTHER | J5667 TWD T10075 | 20241107 | 921 | 20241107 | 931 | 2617716 | 10 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 240 | 37.2755 | -121.8017 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0132621 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987501 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1110 | 83531110 | INTERRUPTER | 31628 | 20241107 | 1021 | 20241107 | 1129 | 2617806 | 68 | Distribution Circuit | Animal | Squirrel | 556 | 37808 | 37.3824 | -121.8818 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0133097 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1987551 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | OTHER | J5667 TWD T10075 | 20241107 | 1235 | 20241107 | 1249 | 2617966 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 24 | 336 | 37.2755 | -121.8017 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0132621 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987578 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 18263 | 20241107 | 1347 | 20241107 | 1400 | 2618010 | 13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 442 | 37.3657 | -121.8343 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0133163 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987586 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316104628837 | 20241108 | 1037 | 20241108 | 1219 | 2618893 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 816 | 37.2844 | -121.8401 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0133515 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987863 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 42095 | 20241108 | 1040 | 20241108 | 1144 | 2618858 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1152 | 37.2991 | -121.9055 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0133500 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987853 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315904328717 | 20241108 | 1946 | 20241108 | 2327 | 2619366 | 221 | Transformer only | Vegetation | Tree - grew into line | 13 | 2873 | 37.2802 | -121.9089 | No | Clear;32-90 F | Secondary | Contaminated | 24-0133738 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987953 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1110 | 82261110 | FUSE | 79345 | 20241108 | 2316 | 20241109 | 658 | 2619389 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 7392 | 37.3372 | -121.9052 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987964 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 18263 | 20241109 | 5 | 20241109 | 51 | 2619393 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 1564 | 37.3657 | -121.8343 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0133750 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1987970 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | INTERRUPTER | 31926 | 20241109 | 718 | 20241110 | 755 | 2619533 | 1477 | Distribution Circuit | Equipment Failure/Involved | Underground | 199 | 39658 | 37.3048 | -121.9317 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0133793 | UG | Sus | 46383676 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988049 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | 315903029301 | 20241109 | 821 | 20241109 | 2131 | 2619563 | 790 | Transformer only | Equipment Failure/Involved | Overhead | 102 | 80580 | 37.2962 | -121.9096 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0133811 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988077 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1108 | 82261108 | FUSE | 25625 | 20241109 | 946 | 20241109 | 1322 | 2619754 | 216 | Distribution Circuit | Animal | Squirrel | 1 | 216 | 37.3622 | -121.9059 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133827 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988089 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | MTR#TRANSFORMER MTR#1010219898 | 20241109 | 1215 | 20241109 | 1606 | 2619809 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 21554 | 37.2872 | -121.8397 | No | Clear;32-90 F | Fuse | Broken | 24-0133829 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988093 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | FUSE | 19507 | 20241109 | 1225 | 20241109 | 1244 | 2619644 | 19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 19 | 37.2915 | -121.8894 | No | Clear;32-90 F |  |  | 24-0133818 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988082 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | FUSE | 26857 | 20241110 | 1419 | 20241110 | 1604 | 2620255 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 5603 | 37.3366 | -121.9172 | No | Partly Cloudy;32-90 F |  |  | 24-0133959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988229 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 4643 | 20241110 | 1653 | 20241110 | 1914 | 2620298 | 141 | Distribution Circuit | Equipment Failure/Involved | Underground | 718 | 84238 | 37.0085 | -121.5846 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0133974 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988240 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | TRANSFORMER | 316106832788 | 20241110 | 1725 | 20241110 | 1942 | 2620347 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 959 | 37.3928 | -121.8411 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0133987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988250 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | FUSE | 10899 | 20241110 | 1821 | 20241111 | 251 | 2620325 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6043 | 37.3226 | -121.9706 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0133994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988270 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2117 | 83802117 | OCB | 2117/2 | 20241110 | 2042 | 20241110 | 2229 | s1988269 | 107 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1662 | 177826 | 37.3828 | -121.9262 | No | Partly Cloudy-Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0133993 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988269 | 0 | Non-EPSS | N | 2024 | GRD- PH OC TIME- PH OC INST
SAN JOSE | SAN JOSE | HICKS-1114 | 83431114 | TRANSFORMER | 315907727358 | 20241111 | 1038 | 20241111 | 1508 | 2620843 | 270 | Transformer only | Unknown Cause | Patrol - found nothing | 37 | 9990 | 37.2429 | -121.9069 | No | Overcast-Rain;32-90 F |  |  | 24-0134210 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1988524 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 8171 | 20241111 | 1123 | 20241111 | 1425 | 2620940 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 422 | 76727 | 37.2513 | -121.8275 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0134130 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988439 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 10719 | 20241111 | 1133 | 20241111 | 1748 | 2620954 | 375 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 3738 | 37.0346 | -121.5824 | No | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0134298 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988599 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | FUSE | 44470 | 20241111 | 1515 | 20241111 | 1715 | 2621226 | 120 | Distribution Circuit | Equipment Failure/Involved | Underground | 35 | 1029 | 37.3883 | -121.9007 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0134224 | UG | Sus | 46387447 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988536 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | SWITCH | 34010SW | 20241111 | 1639 | 20241111 | 1907 | 2621786 | 135 | Distribution Circuit | Equipment Failure/Involved | Underground | 139 | 12937 | 37.3177 | -121.7757 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0134108 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1988563 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 3081 | 20241111 | 1906 | 20241112 | 519 | 2622081 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 18024 | 37.0221 | -121.5761 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0134348 | OH | Sus | 46387544 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1988652 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1105 | 82831105 | FUSE | 21395 | 20241112 | 1505 | 20241112 | 1726 | 2623195 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1035 | 37.4464 | -121.8888 | No | Clear;32-90 F | Fuse | Broken | 24-0134836 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989099 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315799329632 | 20241113 | 1006 | 20241113 | 1603 | 2623901 | 357 | Transformer only | Vegetation | Tree - grew into line | 11 | 3927 | 37.3049 | -121.9454 | No | Partly Cloudy;32-90 F | Transformer | Arcing | 24-0135018 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989339 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2105 | 82012105 | OTHER | J5278 TWD T20946 | 20241113 | 1047 | 20241113 | 1642 | 2623932 | 355 | Distribution Circuit | Equipment Failure/Involved | Underground | 164 | 16295 | 37.2781 | -121.8583 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0134824 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989349 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2108 | 83242108 | TRANSFORMER | 316555424365 | 20241113 | 1707 | 20241114 | 1614 | 2624114 | 1387 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1387 | 37.1631 | -121.683 | No | Overcast;32-90 F |  |  | 24-0135279 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1989459 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | T5481 | 20241113 | 1800 | 20241114 | 1006 | 2624397 | 966 | Distribution Circuit | Equipment Failure/Involved | Underground | 260 | 160038 | 37.2719 | -121.8718 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0135303 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989474 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | FUSE | 6961 | 20241114 | 950 | 20241114 | 1100 | 2624934 | 70 | Distribution Circuit | Animal | Squirrel | 3 | 210 | 37.3225 | -121.9518 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0135469 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989720 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | TRANSFORMER | 316231030064 | 20241114 | 957 | 20241114 | 1029 | 2624944 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 192 | 37.3184 | -121.7972 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0135442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989691 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | C3801 | 20241114 | 1254 | 20241115 | 837 | 2625082 | 1183 | Transformer only | Unknown Cause | Patrol - not conducted | 19 | 22477 | 37.2139 | -121.8394 | No | Partly Cloudy;32-90 F |  |  | 24-0135559 | OH | Sus | 46389007 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1989764 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 100000138943 | 20241114 | 1345 | 20241114 | 1753 | 2625179 | 248 | Transformer only | Vegetation | Tree - grew into line | 4 | 992 | 37.3039 | -121.9477 | No | Partly Cloudy;32-90 F | Conductor- Overhead |  | 24-0135600 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989775 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | TRANSFORMER | 315886329112 | 20241114 | 1650 | 20241115 | 230 | 2625326 | 580 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 6380 | 37.291 | -121.9153 | No | Clear;32-90 F | Secondary | Arcing | 24-0135707 | OH | Sus | 46389175 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1989815 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2111 | 83392111 | FUSE | 32392 | 20241114 | 1944 | 20241114 | 2146 | 2625422 | 122 | Distribution Circuit | Equipment Failure/Involved | Underground | 72 | 8388 | 37.314 | -121.8355 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0135731 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1989826 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20241114 | 2037 | 20241115 | 1925 | 2625456 | 1368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 168 | 57756 | 37.3339 | -121.7556 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0135734 | OH | Sus | 46389179 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1989827 | 0 | EPSS Ckt | N | 2024 | A C & GRD
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | TRANSFORMER | 316107728905 | 20241115 | 930 | 20241115 | 1247 | 2625931 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2955 | 37.2862 | -121.8391 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0135856 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990029 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-1101 | 82951101 | INTERRUPTER | 40010 | 20241115 | 1330 | 20241116 | 1306 | 2626237 | 1416 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 449 | 139566 | 37.2368 | -121.8168 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0135995 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990107 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | OCB | 1110/2/NORM | 20241116 | 58 | 20241116 | 2058 | 2626492 | 1200 | Distribution Circuit | 3rd Party | Vehicle | 2198 | 875411 | 37.2601 | -121.8898 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136142 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990157 | 0 | Non-EPSS | N | 2024 | SET A: B & C- PH INST OC-
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | 72853 | 20241116 | 501 | 20241116 | 721 | 2626518 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 16058 | 37.1218 | -121.6621 | No | Clear;32-90 F |  |  | 24-0136149 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1990165 | 0 | EPSS Ckt | N | 2024 | A- B- TIME OC- INST OC
SAN JOSE | SAN JOSE | HICKS-1115 | 83431115 | OCB | 1115/2 | 20241116 | 734 | 20241117 | 1319 | 2626542 | 1785 | Distribution Circuit | 3rd Party | Vehicle | 2618 | 865843 | 37.2332 | -121.9011 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136161 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990179 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | EL PATIO-1109 | 82921109 | RECLOSER | XR540 | 20241116 | 1006 | 20241116 | 1306 | 2626927 | 124 | Distribution Circuit | Equipment Failure/Involved | Underground | 3060 | 234041 | 37.3207 | -121.9847 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0136206 | UG | Sus | 46390209 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990264 | 0 | Non-EPSS | N | 2024 | C & GRD
SAN JOSE | SAN JOSE | MABURY-1103 | 82191103 | FUSE | 13779 | 20241116 | 1337 | 20241116 | 1440 | 2627056 | 63 | Distribution Circuit | Animal | Squirrel | 133 | 8404 | 37.3562 | -121.879 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0136253 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990291 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40123 | 20241116 | 1743 | 20241117 | 1750 | 2627149 | 1447 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 4038 | 37.0846 | -121.6304 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0136274 | UG | Sus | 46389954 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990303 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | TRANSFORMER | 315921728476 | 20241117 | 1156 | 20241117 | 1341 | 2627429 | 105 | Transformer only | Vegetation | Tree - grew into line | 8 | 840 | 37.2737 | -121.9028 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0136315 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990379 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | SWITCH | 28156 | 20241117 | 1942 | 20241117 | 2044 | 2627667 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 203 | 37.3873 | -121.9011 | No | Overcast;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0134224 | UG | Sus | 46387447 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990420 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2102 | 83392102 | FUSE | 40257 | 20241118 | 1432 | 20241118 | 1445 | 2628466 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 13 | 37.3037 | -121.77 | No | Clear;32-90 F |  |  | 24-0136681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990703 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-2114 | 83802114 | INTERRUPTER | 43464 | 20241118 | 1519 | 20241118 | 1915 | 2628503 | 236 | Distribution Circuit | 3rd Party | Vandalism | 1 | 236 | 37.397 | -121.9353 | No | Partly Cloudy;32-90 F | Interrupter | Normal | 24-0136796 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990749 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 72039 | 20241118 | 1654 | 20241118 | 1841 | 2628539 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 15344 | 37.3768 | -121.8014 | No | Clear;32-90 F |  |  | 24-0136790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1990745 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1105 | 83531105 | FUSE | 13651 | 20241119 | 707 | 20241119 | 1827 | 2628809 | 680 | Distribution Circuit | Animal | Squirrel | 45 | 21656 | 37.3863 | -121.8319 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0137079 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991016 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | TRANSFORMER | T291673 | 20241119 | 923 | 20241119 | 934 | 2628854 | 11 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 11 | 37.2954 | -121.9161 | No | Overcast;32-90 F |  |  | 24-0136972 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1990959 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12061 | 20241119 | 950 | 20241119 | 1257 | 2629134 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 5610 | 37.3303 | -121.8226 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0136990 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1990972 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0410 | 82250410 | JUMPER | OJ'S @ CGC 315936429989 | 20241119 | 1021 | 20241119 | 1438 | 2629195 | 257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3341 | 37.3152 | -121.8985 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0137036 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991002 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12063 | 20241119 | 1317 | 20241119 | 1601 | 2629377 | 164 | Distribution Circuit | Vegetation | Tree - grew into line | 40 | 6560 | 37.3282 | -121.8234 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0137180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991049 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | RECLOSER | XR084 | 20241120 | 910 | 20241120 | 939 | 2630425 | 29 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1616 | 46864 | 37.4294 | -121.914 | No | Overcast;32-90 F |  |  | 24-0137573 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1991315 | 0 | Non-EPSS | N | 2024 | A-B-C PHASE & GRD
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 1617 | 20241120 | 1018 | 20241120 | 1139 | 2630617 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 212 | 17181 | 37.307 | -121.9134 | No | Partly Cloudy;32-90 F |  |  | 24-0137648 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1991368 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1109 | 83701109 | FUSE | 6069 | 20241120 | 1020 | 20241120 | 1505 | 2630625 | 285 | Distribution Circuit | Equipment Failure/Involved | Underground | 27 | 7695 | 37.3063 | -121.8895 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0137600 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991384 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | FUSE | 2089 | 20241120 | 1022 | 20241120 | 1150 | 2630635 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 11000 | 37.3957 | -121.841 | No | Overcast;32-90 F |  |  | 24-0137694 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1991394 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1111 | 83371111 | TRANSFORMER | 315690029530 | 20241120 | 1149 | 20241120 | 2315 | 2630893 | 686 | Transformer only | Vegetation | Tree - grew into line | 9 | 6174 | 37.3021 | -121.9827 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0138128 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991674 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | FUSE | 1617 | 20241120 | 1220 | 20241121 | 257 | 2630969 | 877 | Distribution Circuit | Vegetation | Tree - grew into line | 318 | 278886 | 37.307 | -121.9134 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0137769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991442 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | TRANSFORMER | 315761929734 | 20241120 | 1228 | 20241121 | 508 | 2631068 | 1000 | Transformer only | Vegetation | Tree - grew into line | 8 | 8000 | 37.3076 | -121.9579 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0137760 | OH | Sus | 46396070 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991435 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315655730054 | 20241120 | 1236 | 20241120 | 1538 | 2630853 | 182 | Transformer only | Vegetation | Tree - grew into line | 19 | 3458 | 37.3164 | -121.9947 | No | Overcast;32-90 F | Secondary | Contaminated | 24-0137764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991439 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | TRANSFORMER | 315932229814 | 20241120 | 1244 | 20241120 | 1505 | 2631006 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 2115 | 37.3104 | -121.8995 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0137755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991431 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 28143 | 20241120 | 1413 | 20241121 | 1023 | 2631347 | 1210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 35090 | 37.2424 | -121.8331 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0138065 | OH | Sus | 46396468 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1991612 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | TRANSFORMER | 315959727220 | 20241120 | 1424 | 20241120 | 1451 | 2631295 | 27 | Transformer only | Vegetation | Tree - grew into line | 11 | 297 | 37.2394 | -121.889 | No | Clear-Strong Winds;32-90 F | Secondary | Arcing | 24-0137890 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1991514 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 100000002551 | 20241120 | 1529 | 20241121 | 307 | 2632025 | 698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 22591 | 37.2998 | -121.9063 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0138115 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991660 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 13749 | 20241120 | 1603 | 20241121 | 253 | 2631324 | 650 | Distribution Circuit | Vegetation | Tree - grew into line | 177 | 115050 | 37.2766 | -121.8986 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0137939 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991541 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316215331322 | 20241120 | 1603 | 20241120 | 2234 | 2631497 | 391 | Transformer only | Vegetation | Tree - grew into line | 14 | 5474 | 37.3529 | -121.8031 | No | Overcast;32-90 F | Secondary | Arcing | 24-0137942 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991542 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | JUMPER | FB @ FIRESIDE DR | 20241120 | 1620 | 20241120 | 1936 | 2631269 | 196 | Distribution Circuit | Vegetation | Tree - grew into line | 22 | 4312 | 37.304 | -121.9466 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0137949 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991547 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | FUSE | 49981 | 20241120 | 1627 | 20241121 | 409 | 2631572 | 702 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 9488 | 37.3156 | -121.9046 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0137879 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991551 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | SWITCH | 43594 | 20241120 | 2022 | 20241120 | 2249 | 2631890 | 147 | Distribution Circuit | Equipment Failure/Involved | Underground | 268 | 3689 | 37.3154 | -121.783 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0138008 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991631 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1103 | 82921103 | FUSE | 28013 | 20241120 | 2032 | 20241120 | 2123 | 2631750 | 51 | Distribution Circuit | Vegetation | Tree - grew into line | 174 | 8874 | 37.3084 | -121.9546 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0138080 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991628 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | OTHER | J145 TWD 12783 | 20241120 | 2057 | 20241121 | 439 | 2631805 | 462 | Distribution Circuit | Vegetation | Tree - grew into line | 20 | 9240 | 37.3532 | -121.8387 | No | Overcast;32-90 F | Conductor- Overhead | Arcing | 24-0138091 | OH | Sus | 46396273 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991640 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRIP-SAVER | 41435 | 20241120 | 2158 | 20241121 | 314 | 2632003 | 316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 9480 | 37.2997 | -121.8906 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0137157 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991654 | 0 | Non-EPSS | N | 2024 | n/a
SAN JOSE | SAN JOSE | STONE-1110 | 83701110 | FUSE | 13029 | 20241121 | 1110 | 20241121 | 1252 | 2632654 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 182 | 18564 | 37.3087 | -121.8888 | No | Partly Cloudy;32-90 F |  |  | 24-0138418 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1991842 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | SWITCH | 42117 | 20241121 | 1154 | 20241121 | 1452 | 2632718 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 12460 | 37.3015 | -121.886 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0138309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991829 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | JUMPER | CGC 315816729508 & 315816729478 DISCONNECTED | 20241121 | 1205 | 20241121 | 1345 | 2632746 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 7100 | 37.3015 | -121.9393 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0138398 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991834 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315663630047 | 20241121 | 1329 | 20241121 | 1928 | 2632775 | 359 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 5744 | 37.3162 | -121.9919 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0138664 | OH | Sus | 31718038 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991938 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1105 | 82921105 | TRANSFORMER | 315816829447 | 20241121 | 1408 | 20241121 | 1707 | 2632952 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5960 | 37.2998 | -121.9393 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0138499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991881 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRANSFORMER | 315907929304 | 20241121 | 1455 | 20241121 | 1920 | 2633034 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2116 | 37.2963 | -121.9079 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0138541 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991897 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC SUB | 8387 | FUSE | 6307 | 20241121 | 1513 | 20241121 | 1806 | 2632758 | 173 | Distribution Circuit | Vegetation | Tree - grew into line | 59 | 10207 | 37.3331 | -121.9355 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0138442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991852 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | FUSE | 3797 | 20241121 | 1535 | 20241121 | 1558 | 2633090 | 23 | Distribution Circuit | 3rd Party | Other | 40 | 920 | 37.0728 | -121.588 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0138570 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991907 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | FUSE | 27033 | 20241121 | 2053 | 20241122 | 145 | 2632842 | 292 | Distribution Circuit | Vegetation | Tree - grew into line | 49 | 14308 | 37.223 | -121.9048 | No | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0138681 | OH | Sus | 46397942 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991947 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | FUSE | 14773 | 20241121 | 2127 | 20241122 | 144 | 2633352 | 257 | Distribution Circuit | Vegetation | Tree - grew into line | 28 | 7196 | 37.2771 | -121.8985 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0138702 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1991957 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1112 | 83431112 | TRANSFORMER | 315924127502 | 20241122 | 1255 | 20241122 | 1312 | 2634501 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 170 | 37.2469 | -121.9014 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0139044 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992174 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1105 | 83871105 | OCB | 1105/2 | 20241122 | 1848 | 20241123 | 1430 | 2635256 | 1129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1204 | 664226 | 37.3473 | -121.9225 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139262 | OH | Sus | 31718204 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1992279 | 0 | Non-EPSS | N | 2024 | INST- A- B
SAN JOSE | SAN JOSE | MILPITAS-1101 | 82831101 | INTERRUPTER | 30016 | 20241122 | 1926 | 20241122 | 2317 | 2635422 | 231 | Distribution Circuit | Equipment Failure/Involved | Underground | 209 | 45579 | 37.3958 | -121.8736 | No | Partly Cloudy-Rain;32-90 F | Conductor- Underground | Broken | 24-0139308 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992316 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 41533 | 20241122 | 2140 | 20241123 | 1010 | 2635563 | 750 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 24750 | 37.3375 | -121.8378 | No | Partly Cloudy-Rain;32-90 F | Crossarm- Wood | Broken | 24-0139321 | OH | Sus | 31718501 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992329 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-0404 | 82250404 | OCB | 404/2 | 20241123 | 3 | 20241123 | 103 | 2635682 | 60 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 291 | 17460 | 37.3281 | -121.9025 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0139360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1992367 | 0 | Non-EPSS | N | 2024 | B C & GRD TIME
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 12215 | 20241123 | 36 | 20241123 | 223 | 2635711 | 107 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 84 | 8988 | 37.3877 | -121.8307 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0139376 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992382 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | RECLOSER | XR106 | 20241123 | 758 | 20241123 | 905 | 2635951 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1146 | 76782 | 37.2416 | -121.8309 | No | Clear;32-90 F |  |  | 24-0139429 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1992434 | 0 | EPSS Ckt | N | 2024 | A-B-C
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | TRANSFORMER | 315980028386 | 20241123 | 915 | 20241123 | 1016 | 2636083 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 610 | 37.2714 | -121.8827 | No | Clear;32-90 F | Secondary | Arcing | 24-0139457 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992465 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 6265 | 20241123 | 1050 | 20241123 | 1342 | 2636265 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 4644 | 37.3394 | -121.7685 | No | Clear;32-90 F |  |  | 24-0139544 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992532 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 14887 | 20241123 | 1900 | 20241123 | 1908 | 2636604 | 8 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 40 | 37.0541 | -121.5805 | No | Clear;32-90 F |  |  | 24-0139615 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992573 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | JUMPER | 316009029899 | 20241124 | 1059 | 20241124 | 1536 | 2636983 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4886 | 37.3131 | -121.8735 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0139695 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992641 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | JUMPER | OPEN JUMPERS 2SP/N/O CGC 316171828602 | 20241124 | 1137 | 20241124 | 1228 | 2636999 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 1224 | 37.2785 | -121.8168 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0139700 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992644 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | JUMPER | 28985 OPEN (MAPPED INCORRECTLY) | 20241124 | 1601 | 20241125 | 213 | 2637188 | 612 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1492 | 37.213 | -121.8246 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139764 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992687 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | JUMPER | OJ IFO 589 SERENADE WAY | 20241124 | 2025 | 20241125 | 135 | 2637225 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7440 | 37.2785 | -121.8168 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0139781 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992692 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 71485 | 20241125 | 952 | 20241125 | 1256 | 2637504 | 184 | Distribution Circuit | Animal | Squirrel | 1 | 184 | 37.2617 | -121.8046 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0140013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992787 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 8507 | 20241125 | 1316 | 20241126 | 144 | 2637717 | 748 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 74052 | 37.2666 | -121.8047 | No | Overcast-Drizzle;32-90 F | Secondary | Broken- wire on ground | 24-0140023 | OH | Sus | 46400143 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992792 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 5153 | 20241125 | 1516 | 20241126 | 925 | 2637889 | 899 | Distribution Circuit | Equipment Failure/Involved | Underground | 252 | 111709 | 37.3213 | -121.9816 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 24-0140151 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992835 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | SWITCH | 64048SW | 20241125 | 1523 | 20241125 | 1626 | 2637848 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 5985 | 37.0253 | -121.5839 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0140105 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1992818 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | JUMPER | JUMPERS 1 P/NW/O CGC#100000121659 | 20241125 | 1526 | 20241125 | 2058 | 2637904 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8964 | 37.3461 | -121.9273 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0140094 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992813 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 5127 | 20241126 | 739 | 20241126 | 1220 | 2638328 | 281 | Distribution Circuit | Animal | Squirrel | 469 | 131789 | 37.2626 | -121.8309 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0140441 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1993001 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | 315913426650 | 20241126 | 915 | 20241126 | 1231 | 2638504 | 196 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 784 | 37.2235 | -121.9048 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0140333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1992956 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | SWITCH | 44128 | 20241126 | 1214 | 20241126 | 1233 | 2638681 | 19 | Distribution Circuit | Equipment Failure/Involved | Underground | 388 | 7372 | 37.0252 | -121.5865 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 24-0140105 | UG | Sus | 35600282 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993015 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316043931590 | 20241126 | 2211 | 20241127 | 1504 | 2638997 | 1013 | Transformer only | Environmental/External | Fire- Forest/Grass | 16 | 16208 | 37.3596 | -121.8622 | No | Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0140722 | OH | Sus | 46400896 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1993084 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1104 | 82191104 | FUSE | 27011 | 20241126 | 2220 | 20241127 | 739 | 2639044 | 559 | Distribution Circuit | 3rd Party | Vehicle | 259 | 144781 | 37.3454 | -121.8662 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0140734 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993091 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1108 | 83431108 | FUSE | 19633 | 20241127 | 535 | 20241127 | 1430 | 2639099 | 535 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 33705 | 37.2525 | -121.8832 | No | Partly Cloudy;32-90 F |  |  | 24-0141073 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993189 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | T13249 | 20241127 | 538 | 20241127 | 558 | 2639100 | 20 | Transformer only | Equipment Failure/Involved | Underground | 5 | 100 | 37.199 | -121.8448 | No | Partly Cloudy;32-90 F | Service conductor | Deteriorated | 24-0140737 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993095 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 71035 | 20241127 | 1929 | 20241127 | 2252 | s1993216 | 203 | Distribution Circuit | Vegetation | Tree - grew into line | 96 | 7868 | 37.3531 | -121.8001 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993216 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | FUSE | 644559 | 20241127 | 2223 | 20241128 | 141 | 2639702 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 9900 | 37.3417 | -121.8683 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0141171 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993218 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | JUMPER | CARPOLE WIRE DOWN 1 OF 2 PHASES A PH | 20241128 | 12 | 20241128 | 1333 | 2639731 | 801 | Distribution Circuit | 3rd Party | Vehicle | 40 | 32040 | 37.1715 | -121.825 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0141180 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1993225 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | NORTECH-2109 | 82462109 | RECLOSER | XR004 | 20241128 | 1025 | 20241128 | 1132 | 2639830 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 268 | 37.42 | -121.9386 | No | Partly Cloudy;32-90 F |  |  | 24-0141197 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Multi-Fault | 0 | No | No | No | 1993240 | 0 | Non-EPSS | N | 2024 | A- B & GRD
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | TRANSFORMER | 316059730424 | 20241128 | 1044 | 20241128 | 1357 | 2639841 | 193 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 193 | 37.3278 | -121.8561 | No | Partly Cloudy;32-90 F |  |  | 24-0141213 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1993257 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | SWITCH | 95814 | 20241129 | 400 | 20241129 | 1216 | 2640018 | 496 | Distribution Circuit | 3rd Party | Vehicle | 211 | 8555 | 37.3673 | -121.8695 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0141243 | OH | Sus | 35600673 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993290 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 316282931009 | 20241130 | 824 | 20241130 | 1721 | 2640501 | 537 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1611 | 37.3443 | -121.7794 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0141383 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993398 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | O/J SSD OF 40091 | 20241130 | 856 | 20241130 | 1115 | 2640540 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 278 | 37.0258 | -121.4849 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 24-0141373 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993393 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | SWITCH | 1042 | 20241130 | 1020 | 20241130 | 1230 | 2640599 | 130 | Distribution Circuit | Equipment Failure/Involved | Underground | 133 | 5489 | 37.2383 | -121.834 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0135148 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Force Out | 0 | No | No | No | 1993402 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 8885 | 20241130 | 1250 | 20241130 | 1358 | 2640712 | 68 | Distribution Circuit | Animal | Squirrel | 66 | 4488 | 37.2888 | -121.8417 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0141414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1993422 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | C251 | 20241130 | 1426 | 20241130 | 1826 | 2640757 | 240 | Transformer only | Unknown Cause | Patrol - found nothing | 19 | 4560 | 37.2383 | -121.8233 | No | Clear;32-90 F |  |  | 24-0141448 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1993436 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | OCB | 1105/2 | 20241130 | 1837 | 20241130 | 2042 | 2640872 | 125 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 879 | 37340 | 37.341 | -121.9019 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0141449 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Three Phase Fault | 0 | No | No | No | 1993437 | 0 | Non-EPSS | N | 2024 | NO TRGTS
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | TRANSFORMER | 316059031128 | 20241130 | 1907 | 20241130 | 1954 | 2640883 | 47 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 846 | 37.347 | -121.8568 | No | Overcast;32-90 F |  |  | 24-0141460 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1993439 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | SWITCH | 40178SW | 20241201 | 748 | 20241201 | 923 | 2640962 | 95 | Distribution Circuit | Animal | Squirrel | 23 | 2185 | 37.1369 | -121.6704 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0141492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993467 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | TRANSFORMER | 316106425590 | 20241201 | 1820 | 20241202 | 533 | 2641233 | 673 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 3365 | 37.1965 | -121.8388 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0141563 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993510 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | JUMPER | OJ N/O 25409 | 20241202 | 1905 | 20241203 | 227 | 2642341 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 884 | 37.0691 | -121.5796 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141932 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1993815 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | SWITCH | 68434SW | 20241202 | 2236 | 20241203 | 56 | 2642388 | 140 | Distribution Circuit | Equipment Failure/Involved | Underground | 71 | 8478 | 37.1349 | -121.6484 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0141973 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1993831 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2108 | 82952108 | SWITCH | 10168 | 20241204 | 1002 | 20241204 | 1028 | 2643857 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 459 | 9512 | 37.2714 | -121.8464 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0107752 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1994441 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 4313 | 20241204 | 1134 | 20241204 | 1310 | 2643902 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 192 | 37.1811 | -121.703 | No | Clear;32-90 F |  |  | 24-0142554 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994485 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | TRANSFORMER | 315993429117 | 20241204 | 1313 | 20241205 | 534 | 2644029 | 981 | Transformer only | Equipment Failure/Involved | Electrical Overload | 10 | 9810 | 37.2916 | -121.8784 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0142649 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994518 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | FUSE | 238663 | 20241204 | 1428 | 20241204 | 1943 | 2644100 | 315 | Distribution Circuit | Equipment Failure/Involved | Underground | 4394 | 70278 | 37.3447 | -121.8992 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0142696 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1994529 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | TRANSFORMER | 315949531665 | 20241205 | 1406 | 20241205 | 2334 | 2645142 | 568 | Transformer only | Equipment Failure/Involved | Electrical Overload | 11 | 6248 | 37.3614 | -121.8949 | No | Clear;32-90 F | Transformer | Broken | 24-0143006 | OH | Sus | 31719360 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994857 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1105 | 82261105 | SWITCH | 30118 | 20241205 | 1702 | 20241206 | 59 | 2645360 | 477 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 3820 | 37.3466 | -121.8982 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0142696 | UG | Sus | 31719322 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1994898 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | SWITCH | 5100 | 20241206 | 1414 | 20241206 | 1425 | 2646104 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 68 | 598 | 37.275 | -121.891 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0125530 | UG | Sus | 35409717 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995201 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2105 | 82952105 | FUSE | 4311 | 20241206 | 1925 | 20241206 | 2040 | 2646215 | 75 | Distribution Circuit | 3rd Party | Kite | 32 | 2400 | 37.1801 | -121.7022 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143494 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1995222 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | JUMPER | JUMPERS 1 P/S/O CGC 316619223054 | 20241207 | 1154 | 20241207 | 1433 | 2646537 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 318 | 37.1271 | -121.6605 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0143589 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995346 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1102 | 82311102 | JUMPER | FLYING BELLS EAST OF FUCO 28071 | 20241207 | 1219 | 20241207 | 1516 | 2646490 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 23718 | 37.2861 | -121.8813 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0143581 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995337 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | FUSE | 28307 | 20241207 | 1242 | 20241207 | 1411 | 2646574 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 2403 | 37.2977 | -121.8814 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0143604 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995358 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1107 | 82261107 | TRANSFORMER | 315986330872 | 20241208 | 1256 | 20241208 | 2014 | 2647040 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 16 | 7008 | 37.3396 | -121.8818 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0143749 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995508 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRANSFORMER | 317010118320 | 20241208 | 1719 | 20241208 | 1843 | 2647056 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 323 | 36.9986 | -121.5247 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143759 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995515 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | TRANSFORMER | 316859118878 | 20241209 | 208 | 20241209 | 1421 | 2647190 | 733 | Transformer only | 3rd Party | Vehicle | 8 | 5864 | 37.0135 | -121.5767 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0143790 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995544 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 70023 | 20241209 | 1148 | 20241209 | 1318 | 2647753 | 90 | Distribution Circuit | Animal | Squirrel | 134 | 4126 | 37.2293 | -121.8726 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0143941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995788 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1101 | 83701101 | TRIP-SAVER | 72569 | 20241209 | 1510 | 20241209 | 1815 | 2647917 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 9688 | 37.2942 | -121.9052 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 24-0143921 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995830 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | EL PATIO-1119 | 82921119 | JUMPER | FB 1 SP/SE/O CGC 315925329024 | 20241209 | 1545 | 20241209 | 1824 | 2647931 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 6678 | 37.2886 | -121.9017 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0143980 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1995825 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28261 | 20241209 | 2058 | 20241210 | 540 | 2648158 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1044 | 37.1256 | -121.6867 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0144063 | OH | Sus | 46411084 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995892 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2111 | 83432111 | FUSE | 29810 | 20241209 | 2132 | 20241211 | 206 | 2648169 | 1714 | Distribution Circuit | Equipment Failure/Involved | Underground | 1338 | 72652 | 37.2409 | -121.8616 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0144056 | UG | Sus | 46410956 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1995882 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | OCB | 2106/2 | 20241210 | 1128 | 20241211 | 431 | 2648821 | 1023 | Distribution Circuit | 3rd Party | Vehicle | 6001 | 254572 | 37.3226 | -121.7971 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0144183 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1996178 | 0 | Non-EPSS | N | 2024 | A- B- C & TIME OC
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | TRANSFORMER | 316229532135 | 20241210 | 1551 | 20241210 | 1934 | 2648941 | 223 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 446 | 37.3752 | -121.7988 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0144273 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996245 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | TRANSFORMER | 315790230818 | 20241211 | 911 | 20241211 | 1929 | 2649635 | 618 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2472 | 37.338 | -121.9485 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0144374 | OH | Sus | 31719790 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996515 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1112 | 83371112 | RECLOSER | 247122 | 20241211 | 1811 | 20241211 | 1933 | 2650184 | 82 | Distribution Circuit | Company Initiated | Operating error | 5088 | 368965 | 37.2939 | -121.9897 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0144442 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Multi-Fault | 0 | No | No | No | 1996628 | 0 | Non-EPSS | N | 2024 | A- TIME- INST
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | SWITCH | 24908 | 20241211 | 2037 | 20241212 | 423 | 2650297 | 454 | Distribution Circuit | Equipment Failure/Involved | Underground | 82 | 6404 | 37.1156 | -121.6366 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 24-0144502 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996651 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HOLLISTER-2102 | 182492102 | FUSE | 889 | 20241211 | 2133 | 20241212 | 225 | 2650311 | 292 | Distribution Circuit | 3rd Party | Vehicle | 9 | 2596 | 36.9472 | -121.5098 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0144509 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996654 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | T11853 | 20241211 | 2133 | 20241212 | 1309 | 2650176 | 936 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1872 | 37.1113 | -121.6348 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0144514 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996652 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2106 | 83242106 | TRANSFORMER | 316720622612 | 20241212 | 636 | 20241212 | 811 | 2650447 | 95 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 380 | 37.1156 | -121.6257 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 24-0144560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1996718 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | TRIMBLE-1111 | 83801111 | OCB | 1111/2 | 20241212 | 733 | 20241213 | 409 | 2650483 | 805 | Distribution Circuit | Equipment Failure/Involved | Underground | 61 | 26021 | 37.3828 | -121.9265 | No | Overcast-Drizzle;32-90 F | Switch (UG) | Burned/flashed | 24-0144549 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996695 | 0 | Non-EPSS | N | 2024 | GRD I & PHASE OC I
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 11737 | 20241212 | 901 | 20241212 | 1044 | 2650625 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3605 | 37.3983 | -121.8547 | No | Overcast;32-90 F |  |  | 24-0144596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1996823 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | SWITCH | 42350 | 20241212 | 928 | 20241212 | 1008 | 2650707 | 40 | Distribution Circuit | Company Initiated | Improper Construction | 68 | 2720 | 37.3077 | -121.7651 | No | Overcast-Drizzle;32-90 F | Switch (UG) | Normal | 24-0117028 | UG | Sus | 35330834 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1996839 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | OTHER | J2209 TWD 24948 | 20241212 | 1120 | 20241212 | 1227 | 2650693 | 67 | Distribution Circuit | 3rd Party | Vandalism | 3 | 201 | 37.3274 | -121.8623 | No | Overcast-Drizzle;32-90 F | Elbow | Broken | 24-0144627 | UG | Sus | 46416275 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996862 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1108 | 83701108 | SWITCH | 24972 | 20241212 | 1948 | 20241213 | 144 | 2651298 | 356 | Distribution Circuit | Equipment Failure/Involved | Underground | 10 | 3560 | 37.3244 | -121.8685 | No | Overcast-Drizzle;32-90 F | Other | Contaminated | 24-0144627 | UG | Sus | 46416275 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996958 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1106 | 82191106 | SWITCH | 46642 | 20241213 | 232 | 20241213 | 244 | 2651378 | 12 | Distribution Circuit | 3rd Party | Other | 354 | 4215 | 37.3323 | -121.8544 | No | Overcast;32-90 F | Elbow | Broken | 24-0144627 | UG | Sus | 46416275 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1996981 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SANTA TERESA-2101 | 82962101 | FUSE | 60234 | 20241213 | 609 | 20241213 | 1245 | 2651445 | 396 | Distribution Circuit | Equipment Failure/Involved | Underground | 17 | 3089 | 37.2329 | -121.7734 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0144825 | UG | Sus | 46417677 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997133 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | DIXON LANDING-2102 | 14722102 | TRANSFORMER | 315891734239 | 20241213 | 1104 | 20241213 | 1905 | 2651797 | 481 | Transformer only | Vegetation | Tree - grew into line | 13 | 6253 | 37.4318 | -121.9163 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144834 | OH | Sus | 46417671 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997139 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 59185 | 20241213 | 1130 | 20241213 | 1800 | 2651348 | 390 | Distribution Circuit | Vegetation | Tree - grew into line | 115 | 44850 | 37.3642 | -121.8414 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0144818 | OH | Sus | 31719879 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1997123 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | TRANSFORMER | 316277033646 | 20241213 | 1342 | 20241213 | 1538 | 2651473 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 232 | 37.417 | -121.7832 | No | Overcast;32-90 F | Connector or Splice (OH) | Contaminated | 24-0144912 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997207 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | RECLOSER | 864438 | 20241213 | 1506 | 20241213 | 1604 | 2652081 | 58 | Distribution Circuit | 3rd Party | Metallic Balloon | 896 | 51968 | 37.3761 | -121.8208 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0144903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997201 | 0 | EPSS Ckt | N | 2024 | A- B- C
SAN JOSE | SAN JOSE | SWIFT-2106 | 83392106 | FUSE | 12537 | 20241213 | 1724 | 20241213 | 1908 | 2652207 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 13000 | 37.3269 | -121.8307 | No | Overcast;32-90 F |  |  | 24-0144945 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997239 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | FUSE | 17021 | 20241214 | 209 | 20241214 | 1127 | 2652876 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 39618 | 37.3317 | -121.9342 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0145075 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997379 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1104 | 83531104 | FUSE | 11997 | 20241214 | 501 | 20241214 | 1114 | 2652971 | 373 | Distribution Circuit | Environmental/External | Lightning | 49 | 11487 | 37.3487 | -121.8324 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145245 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997555 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 28843 | 20241214 | 501 | 20241214 | 930 | 2652972 | 269 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 19906 | 37.3432 | -121.8071 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997697 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | OJ 2 E/OF CGC# 316450930832 | 20241214 | 548 | 20241214 | 1003 | 2653056 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 39352 | 37.3403 | -121.7209 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Jumper | Broken | 24-0145195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1997502 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | FUSE | 28143 | 20241214 | 653 | 20241214 | 1548 | 2653779 | 535 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 15515 | 37.2424 | -121.8331 | Yes | Clear;32-90 F |  |  | 24-0145899 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998230 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-1109 | 82831109 | RECLOSER | 903328 | 20241214 | 655 | 20241214 | 1510 | 2653905 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 214 | 89810 | 37.4483 | -121.8461 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145152 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997458 | 0 | EPSS Ckt | N | 2024 | AC GRD TIME OC TGT
SAN JOSE | SAN JOSE | ALMADEN-1111 | 82311111 | FUSE | 6909 | 20241214 | 700 | 20241214 | 1347 | 2654095 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 256 | 104192 | 37.2698 | -121.8849 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0145339 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997653 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | INTERRUPTER | 80866 | 20241214 | 704 | 20241214 | 1204 | 2653998 | 300 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 222 | 66600 | 37.3238 | -121.9041 | Yes | Strong Winds-Heavy Rain; |  |  | 24-0145435 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997757 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 15043 | 20241214 | 718 | 20241214 | 1513 | 2654582 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 202 | 95950 | 37.283 | -121.8393 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0145850 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998184 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1116 | 83431116 | FUSE | 73275 | 20241214 | 756 | 20241214 | 1418 | 2654701 | 382 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 62934 | 37.2393 | -121.9077 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 24-0145769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998101 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 15919 | 20241214 | 834 | 20241214 | 1325 | 2655281 | 291 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 16005 | 37.1947 | -121.8067 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998079 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20241214 | 838 | 20241214 | 1928 | 2655380 | 650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 11700 | 37.1127 | -121.7585 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998003 | 0 | EPSS Ckt | N | 2024 | A PHASE OC
SAN JOSE | SAN JOSE | MORGAN HILL-2109 | 83242109 | RECLOSER | XR104 | 20241214 | 841 | 20241214 | 1751 | 2655585 | 550 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 855 | 470250 | 37.133 | -121.6122 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 24-0145312 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997625 | 0 | EPSS Ckt | N | 2024 | BC GRD TGT
SAN JOSE | SAN JOSE | LLAGAS-2102 | 83182102 | OCB | 2102/2 | 20241214 | 848 | 20241214 | 1240 | 2655799 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4792 | 316474 | 37.0072 | -121.5571 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0145330 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997644 | 0 | Non-EPSS | N | 2024 | PH TIMED OC TGT
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315666430192 | 20241214 | 848 | 20241215 | 619 | 2653679 | 1291 | Transformer only | Unknown Cause | Patrol - found nothing | 15 | 19365 | 37.3195 | -121.9911 | Yes | Partly Cloudy-Heavy Rain;32-90 F |  |  | 24-0145536 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1997859 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 3747 | 20241214 | 849 | 20241215 | 1107 | 2655785 | 1578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 21443 | 37.087 | -121.655 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145967 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998303 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | XR244 | 20241214 | 850 | 20241214 | 2001 | 2655880 | 671 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 157 | 105347 | 37.0163 | -121.5446 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0145369 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997686 | 0 | EPSS Ckt | N | 2024 | BC TGT
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR144 | 20241214 | 850 | 20241214 | 1217 | 2655982 | 207 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2613 | 540891 | 37.0009 | -121.5659 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0145357 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1997672 | 0 | EPSS Ckt | N | 2024 | ABC TGT
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR070 | 20241214 | 850 | 20241215 | 1344 | 2655933 | 1734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 208369 | 37.0428 | -121.6546 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997647 | 0 | EPSS Ckt | N | 2024 | A PH- GRD
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26163 | 20241214 | 851 | 20241214 | 1900 | 2657764 | 609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2436 | 37.049 | -121.5462 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0145492 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997815 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2111 | 83242111 | FUSE | 28259 | 20241214 | 853 | 20241214 | 1830 | 2655772 | 577 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2308 | 37.116 | -121.6878 | Yes | Clear;32-90 F |  |  | 24-0146014 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998354 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 25341 | 20241214 | 854 | 20241214 | 1614 | 2659783 | 440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 29920 | 37.0618 | -121.5875 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 24-0145838 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998172 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | RECLOSER | 152774 | 20241214 | 856 | 20241214 | 1914 | 2655988 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 554 | 268911 | 37.1503 | -121.6194 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145894 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998227 | 0 | EPSS Ckt | N | 2024 | B GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 10541 | 20241214 | 856 | 20241215 | 1608 | 2655927 | 1872 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 25382 | 37.1035 | -121.6165 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0145863 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998197 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 13333 | 20241214 | 858 | 20241215 | 1105 | s1998234 | 1567 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1567 | 37.0135 | -121.6356 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145903 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1998234 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SWIFT-2108 | 83392108 | OCB | 2108/2 | 20241214 | 902 | 20241214 | 2100 | 2656124 | 718 | Distribution Circuit | Equipment Failure/Involved | Underground | 5966 | 1205284 | 37.3226 | -121.797 | Yes | Overcast-Rain;32-90 F | Connector or Splice (UG) | Burned/flashed | 24-0145385 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1997705 | 0 | Non-EPSS | N | 2024 | C OC TIME- GRD
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 17279 | 20241214 | 920 | 20241214 | 2154 | 2660674 | 754 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 16320 | 37.0095 | -121.5779 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0146102 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998446 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 17601 | 20241214 | 929 | 20241215 | 1718 | 2659622 | 1909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7636 | 37.0335 | -121.5272 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145778 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | Yes | No | 1998111 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26155 | 20241214 | 929 | 20241214 | 1456 | 2659142 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 3597 | 37.0416 | -121.5421 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145797 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998130 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 3835 | 20241214 | 930 | 20241214 | 1447 | 2658057 | 317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 14567 | 37.037 | -121.5394 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998141 | 1 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 4887 | 20241214 | 933 | 20241215 | 1311 | 2656619 | 1658 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 24870 | 37.0135 | -121.6388 | Yes | Clear;32-90 F |  |  | 24-0146310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998681 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | RECLOSER | XR312 | 20241214 | 941 | 20241214 | 1933 | 2660460 | 553 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 59534 | 37.0394 | -121.6032 | Yes | Clear;32-90 F |  |  | 24-0146023 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998362 | 0 | EPSS Ckt | N | 2024 | A & B
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | TRANSFORMER | 315660530118 | 20241214 | 956 | 20241214 | 1448 | 2660238 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 584 | 37.3182 | -121.9929 | Yes | Clear;32-90 F | Secondary | Broken | 24-0145959 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998291 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 14371 | 20241214 | 1002 | 20241214 | 1939 | 2656993 | 577 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 13848 | 37.0072 | -121.5791 | Yes | Clear;32-90 F | Transformer (OH) | Contaminated | 24-0146045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998385 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | TRANSFORMER | 316736021606 | 20241214 | 1003 | 20241215 | 1438 | 2660621 | 1715 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 5145 | 37.088 | -121.62 | Yes | Clear;32-90 F | Transformer | Broken | 24-0146083 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998426 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | FUSE | 14763 | 20241214 | 1021 | 20241214 | 1429 | 2657431 | 248 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 156 | 38688 | 37.3901 | -121.8141 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Contaminated | 24-0145793 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998125 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 26079 | 20241214 | 1038 | 20241214 | 1835 | 2656625 | 477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 13356 | 37.0467 | -121.5746 | Yes | Clear;32-90 F |  |  | 24-0146011 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998350 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | TRANSFORMER | 316220731077 | 20241214 | 1039 | 20241215 | 1053 | 2657727 | 1454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 21810 | 37.3462 | -121.8011 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145868 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 1998202 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 7867 | 20241214 | 1050 | 20241214 | 1418 | 2659689 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1872 | 37.193 | -121.8032 | Yes | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 24-0145817 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998150 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | FUSE | 26345 | 20241214 | 1222 | 20241214 | 1314 | 2658831 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 268 | 13936 | 37.0179 | -121.5864 | Yes | Clear;32-90 F |  |  | 24-0145653 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1997977 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | 524360 | 20241214 | 1230 | 20241214 | 1320 | 2659012 | 48 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1995 | 92135 | 36.9756 | -121.5564 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145703 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998030 | 0 | EPSS Ckt | N | 2024 | NONE
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316874319035 | 20241214 | 1339 | 20241215 | 911 | 2659653 | 1172 | Transformer only | Vegetation | Tree - branch fell on line | 17 | 19924 | 37.0179 | -121.5714 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0145794 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998126 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | OCB | 2103/2 | 20241214 | 1339 | 20241215 | 1013 | 2656207 | 1234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5874 | 1047684 | 37.0071 | -121.557 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0145799 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998132 | 0 | Non-EPSS | N | 2024 | B PHASE T/OC & GRD
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 26057 | 20241214 | 1343 | 20241214 | 1840 | 2659447 | 297 | Distribution Circuit | 3rd Party | Vehicle | 67 | 19899 | 37.0874 | -121.6269 | Yes | Clear;32-90 F | Pole-Wood | Broken | 24-0145755 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998088 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 10719 | 20241214 | 1400 | 20241214 | 1637 | s1998465 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 4239 | 37.0346 | -121.5824 | Yes | Clear;32-90 F |  |  | 24-0146119 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998465 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1112 | 82251112 | TRANSFORMER | T14553 | 20241214 | 1405 | 20241215 | 1534 | 2659628 | 1529 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 24644 | 37.3236 | -121.9075 | Yes | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 24-0145935 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998281 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 3835 | 20241214 | 1518 | 20241214 | 1636 | 2660183 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 10764 | 37.037 | -121.5394 | Yes | Overcast;32-90 F |  |  | 24-0145808 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998279 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | SWITCH | 603392 | 20241214 | 1702 | 20241215 | 1547 | 2661837 | 1365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 16380 | 36.9652 | -121.5654 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146364 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1998735 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 40723 | 20241214 | 1812 | 20241214 | 1845 | 2660441 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 33 | 37.0643 | -121.6922 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 24-0146013 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998352 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MONTAGUE-2109 | 83892109 | OCB | 2109/2 | 20241214 | 1959 | 20241216 | 258 | 2660561 | 44 | Distribution Circuit | Equipment Failure/Involved | Underground | 601 | 26444 | 37.403 | -121.9055 | Yes | Overcast;32-90 F | Switch (UG) | Leaking | 24-0146067 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998404 | 0 | Non-EPSS | N | 2024 | C PHASE- CURRENT TGT A- B- C
SAN JOSE | SAN JOSE | EDENVALE-2113 | 82952113 | TRANSFORMER | 316121327421 | 20241214 | 2026 | 20241215 | 1505 | 2660557 | 1119 | Transformer only | Equipment Failure/Involved | Overhead | 14 | 15666 | 37.2454 | -121.8336 | Yes | Clear;32-90 F | Transformer | Contaminated | 24-0146084 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998427 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1107 | 82921107 | JUMPER | WIRE DOWN | 20241214 | 2123 | 20241215 | 1054 | 2660673 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 119217 | 37.3103 | -121.9197 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146101 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | Yes | No | 1998445 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | FUSE | 40851 | 20241214 | 2158 | 20241216 | 207 | 2660785 | 1689 | Distribution Circuit | 3rd Party | Vandalism | 452 | 74028 | 37.3629 | -121.8644 | Yes | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0146133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998482 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 75463 | 20241214 | 2259 | 20241215 | 1204 | 2660661 | 785 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 9471 | 37.3154 | -121.9879 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146118 | OH | Sus | 35605807 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998464 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2105 | 83182105 | RECLOSER | XR320 | 20241215 | 434 | 20241215 | 1423 | 2660875 | 589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5815 | 691961 | 37.0019 | -121.5672 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0146154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998505 | 0 | EPSS Ckt | N | 2024 | A & GRD TARGET
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4373 | 20241215 | 756 | 20241215 | 1208 | 2661172 | 252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 3780 | 37.0718 | -121.5189 | No | Overcast-Fog;32-90 F |  |  | 24-0146281 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998657 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1112 | 83531112 | FUSE | 28843 | 20241215 | 856 | 20241215 | 1053 | 2661132 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 6903 | 37.3432 | -121.8071 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0146190 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998539 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SARATOGA-1114 | 83371114 | FUSE | 75463 | 20241215 | 1100 | 20241215 | 1158 | 2661401 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 2552 | 37.3154 | -121.9879 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0146244 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998616 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | FUSE | 42233 | 20241215 | 1153 | 20241215 | 1517 | 2661484 | 204 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 12648 | 37.2447 | -121.8402 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0146274 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998649 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | TRANSFORMER | 316876019075 | 20241215 | 1233 | 20241215 | 1948 | 2661403 | 435 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2175 | 37.019 | -121.5708 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0146300 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998673 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2106 | 82952106 | TRANSFORMER | 316135727578 | 20241215 | 1523 | 20241215 | 2200 | 2661790 | 397 | Transformer only | Vegetation | Tree - grew into line | 9 | 3573 | 37.2498 | -121.8287 | No | Clear;32-90 F | Secondary | Broken | 24-0146424 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998787 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1101 | 82311101 | TRANSFORMER | 315950428210 | 20241215 | 1618 | 20241215 | 2124 | 2661927 | 306 | Transformer only | Vegetation | Tree - grew into line | 6 | 1836 | 37.2665 | -121.8927 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0146384 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1998753 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | FUSE | 14895 | 20241216 | 804 | 20241216 | 1022 | 2662398 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 414 | 37.0515 | -121.5874 | No | Clear;32-90 F |  |  | 24-0146538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 1998924 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 5127 | 20241216 | 815 | 20241216 | 1027 | 2662457 | 132 | Distribution Circuit | Animal | Squirrel | 469 | 61908 | 37.2626 | -121.8309 | No | Clear;32-90 F | Fuse | Normal | 24-0146534 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1998921 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 73247 | 20241216 | 1130 | 20241216 | 1335 | 2662933 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 375 | 37.0653 | -121.5774 | No | Overcast-Drizzle;32-90 F |  |  | 24-0146614 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1998996 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2105 | 83242105 | FUSE | 27285 | 20241216 | 1339 | 20241216 | 1956 | 2663132 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 15457 | 37.0889 | -121.6648 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0146641 | OH | Sus | 31720376 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999023 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 32220 | 20241216 | 1433 | 20241216 | 1718 | 2663256 | 165 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 291 | 31129 | 37.0263 | -121.6094 | No | Clear;32-90 F |  |  | 24-0146657 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999040 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | ALMADEN-1110 | 82311110 | JUMPER | OJ'S @ BLOSSOMVIEW DR | 20241216 | 1522 | 20241216 | 2157 | 2663322 | 395 | Distribution Circuit | Vegetation | Tree - grew into line | 31 | 12245 | 37.2666 | -121.8943 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146647 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999030 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | TRIP-SAVER | 3835 | 20241216 | 1603 | 20241216 | 1658 | 2663242 | 55 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 138 | 7590 | 37.037 | -121.5394 | No | Overcast-Rain;32-90 F |  |  | 24-0146675 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999054 | 0 | EPSS Ckt | N | 2024 | N/A
SAN JOSE | SAN JOSE | MONTAGUE-2104 | 83892104 | OCB | 2104/2 | 20241216 | 1707 | 20241216 | 1850 | 2663522 | 103 | Distribution Circuit | 3rd Party | Vandalism | 2821 | 144863 | 37.403 | -121.9057 | No | Overcast;32-90 F | Pothead(Riser Termination) | Broken | 24-0146677 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999056 | 0 | Non-EPSS | N | 2024 | GRD
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | FUSE | 73341 | 20241216 | 1708 | 20241216 | 2207 | 2663050 | 299 | Distribution Circuit | Vegetation | Tree - grew into line | 60 | 17940 | 37.3504 | -121.8446 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0146680 | OH | Sus | 46419507 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999059 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | RECLOSER | 247498 | 20241217 | 1032 | 20241218 | 16 | 2664109 | 824 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 145 | 76340 | 37.354 | -121.7871 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146773 | OH | Sus | 31720440 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999253 | 0 | EPSS Ckt | N | 2024 | SGF & INST OC
SAN JOSE | SAN JOSE | FMC-1112 | 83871112 | OCB | 1112/2 | 20241218 | 903 | 20241218 | 947 | 2664963 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3243 | 142692 | 37.3474 | -121.9225 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0138194 | OH | Sus | 35132537 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999531 | 0 | Non-EPSS | N | 2024 | A PHASE T/OC & GRD
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316089731592 | 20241218 | 1544 | 20241219 | 348 | 2665375 | 724 | Transformer only | Equipment Failure/Involved | Overhead | 44 | 31856 | 37.3598 | -121.8464 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0147028 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999668 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | JUMPER | OJ E/O CGC#316092031610 | 20241218 | 2050 | 20241219 | 333 | 2665555 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 6448 | 37.3603 | -121.8455 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0147051 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1999693 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EL PATIO-1112 | 82921112 | TRANSFORMER | 315806329307 | 20241218 | 2101 | 20241218 | 2159 | 2665568 | 58 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 406 | 37.2959 | -121.9429 | No | Partly Cloudy;32-90 F |  |  | 24-0147056 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1999702 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | STONE-1107 | 83701107 | FUSE | 83401 | 20241219 | 1700 | 20241219 | 1929 | 2666210 | 149 | Distribution Circuit | 3rd Party | Thrown Object | 2 | 298 | 37.3282 | -121.8688 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0147159 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999887 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | TRANSFORMER | 316095531235 | 20241219 | 2205 | 20241220 | 536 | 2666306 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 14445 | 37.3501 | -121.8443 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147177 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 1999914 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2110 | 83242110 | SWITCH | 23377 | 20241219 | 2207 | 20241219 | 2227 | s1999911 | 20 | Distribution Circuit | Company Initiated | Return Circuit Normal | 6 | 120 | 37.1262 | -121.6514 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0144699 | UG | Sus | 35575902 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 1999911 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MABURY-1105 | 82191105 | TRANSFORMER | 316042931753 | 20241219 | 2211 | 20241220 | 310 | 2666299 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 35 | 10465 | 37.3641 | -121.8626 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 24-0147176 | OH | Sus | 31720577 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 1999913 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MILPITAS-2110 | 82832110 | FUSE | 2083 | 20241220 | 542 | 20241220 | 735 | 2666356 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 588 | 66444 | 37.4142 | -121.8671 | No | Partly Cloudy;32-90 F |  |  | 24-0147194 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 1999939 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2104 | 82012104 | RECLOSER | XR348 | 20241220 | 1530 | 20241220 | 1540 | 2666982 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 20 | 37.2887 | -121.8752 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 24-0142324 | UG | Sus | 35575901 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000158 | 0 | Non-EPSS | N | 2024 | NONE
SAN JOSE | SAN JOSE | MC KEE-1106 | 83531106 | SWITCH | 25590 | 20241220 | 1724 | 20241220 | 1758 | 2667066 | 34 | Distribution Circuit | Company Initiated | Return Circuit Normal | 330 | 11220 | 37.3601 | -121.8502 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0142605 | OH | Sus | 35358671 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000172 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20241221 | 733 | 20241221 | 1213 | 2667229 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 4200 | 37.0697 | -121.5204 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147323 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000278 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE B-1112 | 82261112 | INTERRUPTER | 231112 | 20241221 | 742 | 20241224 | 445 | 2667212 | 4143 | Distribution Circuit | 3rd Party | Vandalism | 2 | 4455 | 37.3663 | -121.8829 | No | Overcast;32-90 F | Conductor- Underground | Broken | 24-0147325 | UG | Sus | 31720667 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000280 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | OCB | 1110/2 | 20241222 | 1715 | 20241222 | 1900 | 2667868 | 105 | Distribution Circuit | Equipment Failure/Involved | Underground | 2767 | 184014 | 37.2332 | -121.9012 | No | Overcast;32-90 F | Elbow | Burned/flashed | 24-0147411 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000396 | 0 | Non-EPSS | N | 2024 | B & GRD TARGET. TIME OC TARGET
SAN JOSE | SAN JOSE | EDENVALE-2109 | 82952109 | FUSE | 40214 | 20241222 | 2113 | 20241224 | 114 | 2667935 | 910 | Distribution Circuit | Equipment Failure/Involved | Underground | 127 | 77459 | 37.2573 | -121.8514 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 24-0147428 | UG | Sus | 46432806 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000412 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 71540 | 20241223 | 1811 | 20241223 | 1850 | 2668567 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 93 | 37.2917 | -121.8067 | No | Partly Cloudy;32-90 F |  |  | 24-0147510 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000558 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 42104 | 20241224 | 331 | 20241224 | 1404 | 2668765 | 633 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 9202 | 37.3102 | -121.8445 | No | Overcast-Rain;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0147602 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000656 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | HICKS-1111 | 83431111 | OTHER | WIRE DOWN @ 1847 CHARMERAN | 20241224 | 331 | 20241224 | 1045 | 2668763 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 21269 | 37.2591 | -121.9206 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0147548 | OH | Sus | 31720903 | SOUTH BAY AND CENTRAL COAST | DEC | Open Circuit | 0 | No | No | No | 2000600 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2103 | 83182103 | FUSE | 4621 | 20241224 | 501 | 20241224 | 728 | 2668805 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 17052 | 37.0199 | -121.5727 | No | Clear;32-90 F |  |  | 24-0147569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000621 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316130532073 | 20241224 | 549 | 20241224 | 621 | 2668832 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 25 | 800 | 37.3732 | -121.8323 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 24-0147560 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000613 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-1110 | 83431110 | OCB | 24363 | 20241224 | 922 | 20241224 | 1824 | 2669032 | 540 | Distribution Circuit | Equipment Failure/Involved | Underground | 1253 | 428048 | 37.2437 | -121.8939 | No | Overcast-Drizzle;32-90 F | Switch (UG) | Failed/Faulted | 24-0147607 | UG | Sus | 35607012 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000662 | 0 | Non-EPSS | N | 2024 | C & GRD (INST & TRIP TARGET)
SAN JOSE | SAN JOSE | SWIFT-2107 | 83392107 | SWITCH | X2162 | 20241224 | 1154 | 20241224 | 1933 | 2669160 | 454 | Distribution Circuit | Vegetation | Tree - grew into line | 2658 | 1216518 | 37.2995 | -121.7609 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0147641 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2000698 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 28009 | 20241224 | 1528 | 20241224 | 1737 | 2669366 | 129 | Distribution Circuit | 3rd Party | Metallic Balloon | 157 | 20253 | 37.2623 | -121.8062 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0147684 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000744 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | SAN JOSE A-1110 | 82251110 | SWITCH | 34606 | 20241225 | 356 | 20241225 | 524 | 2669533 | 88 | Distribution Circuit | 3rd Party | Vehicle | 3420 | 282564 | 37.3235 | -121.91 | No | Partly Cloudy;32-90 F | Other | Broken | 24-0147707 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | None | 0 | No | No | No | 2000767 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | PIERCY-2109 | 83912109 | FUSE | 43099 | 20241225 | 728 | 20241225 | 809 | 2669551 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 5371 | 37.2755 | -121.8207 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147710 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000770 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | MORGAN HILL-2104 | 83242104 | FUSE | 70407 | 20241226 | 757 | 20241226 | 902 | 2669890 | 65 | Distribution Circuit | Animal | Bird found | 143 | 9295 | 37.156 | -121.6116 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0147786 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000857 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | SWITCH | 61550 | 20241226 | 1619 | 20241226 | 1647 | 2670244 | 28 | Distribution Circuit | Equipment Failure/Involved | Underground | 15 | 315 | 37.3106 | -121.8475 | No | Overcast;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0147602 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000922 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4373 | 20241226 | 2052 | 20241226 | 2320 | 2670379 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2220 | 37.0718 | -121.5189 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2000952 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | RECLOSER | 783467 | 20241227 | 251 | 20241227 | 302 | 2670443 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 58 | 638 | 37.053 | -121.5276 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147876 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2000972 | 0 | EPSS Ckt | N | 2024 | B & C PHASE
SAN JOSE | SAN JOSE | EVERGREEN-2103 | 82012103 | FUSE | 25235 | 20241228 | 842 | 20241228 | 1020 | 2671215 | 98 | Distribution Circuit | Equipment Failure/Involved | Underground | 50 | 4900 | 37.2881 | -121.8194 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0148021 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001155 | 0 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | EVERGREEN-2102 | 82012102 | FUSE | 25035 | 20241228 | 1049 | 20241228 | 1208 | 2671289 | 79 | Distribution Circuit | Animal | Squirrel | 3 | 237 | 37.3284 | -121.8496 | No | Overcast;32-90 F | Fuse | Normal | 24-0148038 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001177 | 1 | Non-EPSS | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2101 | 83182101 | FUSE | 4373 | 20241229 | 141 | 20241229 | 445 | 2671570 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2760 | 37.0718 | -121.5189 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0148077 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001219 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | HICKS-2103 | 83432103 | TRANSFORMER | C29 | 20241230 | 946 | 20241230 | 1434 | 2672393 | 288 | Transformer only | Equipment Failure/Involved | Underground | 19 | 5472 | 37.2107 | -121.8731 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 24-0148196 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001419 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17557 | 20241230 | 1241 | 20241230 | 1919 | 2672527 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16716 | 37.3808 | -121.809 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148224 | OH | Sus | 46442301 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | Yes | No | 2001470 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1108 | 83531108 | SWITCH | 36082SW | 20241230 | 1405 | 20241231 | 527 | 2672613 | 922 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 17149 | 37.3725 | -121.8458 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0148236 | UG | Sus | 35607953 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001484 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1107 | 83531107 | FUSE | 17557 | 20241230 | 2059 | 20241230 | 2314 | 2672833 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 5670 | 37.3808 | -121.809 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0148255 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 2001508 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1103 | 83531103 | TRANSFORMER | 316209532661 | 20241231 | 721 | 20241231 | 1541 | 2672967 | 500 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 500 | 37.3896 | -121.8059 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148285 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001572 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2107 | 83182107 | FUSE | 25251 | 20241231 | 1315 | 20250101 | 1700 | 2673263 | 1665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6660 | 37.0119 | -121.6224 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148325 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Three Phase Fault | 0 | No | No | No | 2001622 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | LLAGAS-2104 | 83182104 | FUSE | 1985 | 20241231 | 1346 | 20250101 | 2004 | 2673277 | 1818 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 21816 | 36.9585 | -121.551 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0148337 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Line | 0 | No | No | No | 2001634 | 0 | EPSS Ckt | N | 2024
SAN JOSE | SAN JOSE | MC KEE-1111 | 83531111 | TRANSFORMER | 316332031744 | 20241231 | 1348 | 20241231 | 1715 | 2673132 | 207 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 414 | 37.365 | -121.7633 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0148307 | OH | Sus | 46443263 | SOUTH BAY AND CENTRAL COAST | DEC | Line to Ground | 0 | No | No | No | 2001600 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS 1109 | 152691109 | FUSE | 328161 | 20230101 | 519 | 20230101 | 1421 | 1907816 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 22162 | 39.0344 | -121.096 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1794925 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS 1103 | 152261103 | FUSE | 57613 | 20230101 | 550 | 20230102 | 1408 | 1907829 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15504 | 38.7006 | -120.8466 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0004338 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1794933 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN 1104 | 153701104 | FUSE | 7799 | 20230101 | 639 | 20230101 | 1703 | 1907862 | 624 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 3744 | 38.9412 | -121.2288 | No | Clear;32-90F |  |  | 23-0004519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1795119 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS 1103 | 152691103 | JUMPER | OJS 3 SPANS E/OF CGC#222600051287 | 20230101 | 735 | 20230101 | 1745 | 1908859 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1220 | 39.0712 | -121.0837 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004486 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1795086 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS 2102 | 153132102 | RECLOSER | 2718 | 20230101 | 800 | 20230101 | 950 | 1907956 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1168 | 128480 | 39.2349 | -121.2209 | No | Clear;32-90F | Recloser | Malfunctioning | 23-0004326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1794922 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | SHINGLE SPRINGS 2110 | 153652110 | TRANSFORMER | 223109535485 | 20230101 | 933 | 20230101 | 2045 | 1908139 | 672 | Transformer only | Vegetation | Tree - fell into line | 1 | 672 | 38.6359 | -120.9121 | No | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0004468 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1795067 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE 1101 | 152571101 | FUSE | 63209 | 20230101 | 1002 | 20230101 | 1904 | 1909086 | 542 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1626 | 38.7813 | -121.1607 | No | Clear;32-90F |  |  | 23-0004560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795160 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS 1104 | 152691104 | TRANSFORMER | 222688453036 | 20230101 | 1011 | 20230101 | 1818 | 1908199 | 487 | Transformer only | Vegetation | Tree - fell into line | 3 | 1461 | 39.1193 | -121.054 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0004438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795037 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222265557079 | 20230101 | 1027 | 20230101 | 1830 | 1908225 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1449 | 39.2318 | -121.2012 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0004418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795014 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER 1103 | 152461103 | SWITCH | 39699 | 20230101 | 1150 | 20230101 | 1737 | 1908986 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 5297 | 38.9343 | -121.0751 | No | Clear;32-90F | Jumper | Burned Open | 23-0004510 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1795124 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING 1101 | 152251101 | FUSE | 6703 | 20230101 | 1315 | 20230102 | 1331 | 1908557 | 1456 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 16 | 23296 | 39.3202 | -120.6232 | No | Clear;32-90F |  |  | 23-0004774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1795376 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3781 | 20230101 | 1403 | 20230101 | 1833 | 1908686 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 3990 | 38.7224 | -121.175 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004471 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1795070 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32943 | 20230101 | 1428 | 20230102 | 1434 | 1908779 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5784 | 39.2565 | -121.2108 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0004464 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1795063 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE 1102 | 152271102 | JUMPER | OJS 1 W/OF CGC 22254404483 | 20230101 | 1524 | 20230103 | 1245 | s1795594 | 2721 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2721 | 38.894 | -121.1072 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0005015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795594 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS 2108 | 153652108 | TRANSFORMER | 222895336550 | 20230101 | 1648 | 20230103 | 954 | 1908748 | 2466 | Transformer only | Vegetation | Tree - fell into line | 2 | 4932 | 38.6656 | -120.9868 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0004505 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795105 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 37593 | 20230101 | 1750 | 20230102 | 1640 | 1909041 | 1370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 25125 | 38.8025 | -121.4503 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1795178 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | TRANSFORMER | 222189640682 | 20230102 | 915 | 20230103 | 1154 | 1909686 | 1599 | Transformer only | Vegetation | Tree - fell into line | 6 | 9594 | 38.7809 | -121.2331 | No | Clear;32-90F | Secondary | Broken- wire on ground | 23-0004777 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1795379 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | FUSE | 2485 | 20230102 | 1026 | 20230102 | 1308 | 1909818 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 10196 | 38.8188 | -121.2554 | No | Clear;32-90F |  |  | 23-0004730 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795337 | 1 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2104 | 153612104 | TRANSFORMER | 222782538580 | 20230102 | 1046 | 20230103 | 1346 | 1909628 | 1620 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 4860 | 38.7223 | -121.0247 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0004716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795322 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES 2101 | 152282101 | TRANSFORMER | 222961445337 | 20230102 | 1140 | 20230102 | 1322 | 1909693 | 102 | Transformer only | Vegetation | Tree - fell into line | 1 | 102 | 38.9066 | -120.9607 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0004769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795371 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223241044790 | 20230102 | 1726 | 20230103 | 1015 | 1911374 | 1009 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1009 | 38.8911 | -120.8622 | No | Clear;32-90 F | Jumper | Broken | 23-0005078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795639 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1105 | 152481105 | TRANSFORMER | 222913059493 | 20230102 | 1934 | 20230103 | 956 | 1910602 | 862 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3448 | 39.2955 | -120.9715 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0004902 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795506 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1103 | 152481103 | RECLOSER | 262343 | 20230102 | 2041 | 20230103 | 1224 | 1910659 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 91471 | 39.2647 | -121.0232 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1795499 | 0 | EPSS Ckt | N | 2023 | C PHASE
SIERRA | EL DORADO | PLACERVILLE 2106 | 153082106 | FUSE | 1491 | 20230103 | 703 | 20230103 | 1042 | 1910995 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1021 | 38.7941 | -120.8199 | No | Clear;32-90 F |  |  | 23-0005051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795613 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL 1108 | 152701108 | TRANSFORMER | 222473448722 | 20230103 | 1016 | 20230103 | 1507 | 1911349 | 291 | Transformer only | Animal | Squirrel | 1 | 291 | 39.0009 | -121.131 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0005134 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795684 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6863 | 20230103 | 1102 | 20230103 | 1419 | 1911357 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1773 | 38.8671 | -120.8672 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0005128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1795679 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND 1104 | 152811104 | FUSE | 7207 | 20230103 | 1326 | 20230103 | 1549 | 1911587 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3815 | 38.9788 | -121.3691 | No | Clear;32-90 F |  |  | 23-0005249 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1795746 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT 1101 | 158031101 | RECLOSER | 927328 | 20230103 | 1516 | 20230103 | 1657 | 1911783 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1165 | 114452 | 38.8205 | -120.0758 | No | Clear;32-90 F |  |  | 23-0005244 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1795742 | 0 | EPSS Ckt | N | 2023 | C
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 927328 | 20230103 | 1741 | 20230103 | 1927 | 1911977 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 9964 | 38.8205 | -120.0758 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0005279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795765 | 0 | EPSS Ckt | N | 2023 | C
SIERRA | EL DORADO | EL DORADO PH 2101 | 152762101 | FUSE | 2557 | 20230103 | 2100 | 20230103 | 2210 | 1912125 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 70 | 38.8015 | -120.1165 | No | Clear;32-90F |  |  | 23-0005417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795898 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY 1101 | 152241101 | TRANSFORMER | T6763 | 20230104 | 839 | 20230104 | 1207 | 1912731 | 208 | Transformer only | Vegetation | Tree - grew into line | 2 | 416 | 39.0009 | -121.0223 | Yes | Clear;32-90F | Secondary | Normal | 23-0005620 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1796059 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 4667 | 20230104 | 1139 | 20230105 | 1615 | 1913562 | 1716 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 17352 | 38.7448 | -121.1867 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1796417 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223234644734 | 20230104 | 1206 | 20230104 | 1502 | 1913426 | 176 | Transformer only | Vegetation | Tree - fell into line | 3 | 528 | 38.8896 | -120.8651 | Yes | Clear;32-90F | Service conductor | Broken | 23-0005874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1796253 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS 2105 | 153652105 | FUSE | 22967 | 20230104 | 1222 | 20230104 | 1723 | 1913748 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3913 | 38.6744 | -120.9831 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796297 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20230104 | 1449 | 20230104 | 1547 | 1914610 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 3074 | 38.8428 | -121.029 | Yes | Clear;32-90F |  |  | 23-0006082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796410 | 0 | EPSS Ckt | N | 2023 | A+B
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20230104 | 1457 | 20230105 | 1438 | 1914661 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 68257 | 39.1336 | -121.0717 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1796424 | 0 | EPSS Ckt | N | 2023 | B+GRD
SIERRA | EL DORADO | APPLE HILL 2102 | 153662102 | FUSE | 21469 | 20230104 | 1617 | 20230104 | 1731 | 1915170 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 592 | 38.6015 | -120.6965 | Yes | Clear;32-90F |  |  | 23-0006306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796609 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 449556 | 20230104 | 1703 | 20230104 | 1810 | 1916330 | 67 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 88 | 5896 | 38.8922 | -121.1253 | Yes | Clear;32-90F |  |  | 23-0006360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1796659 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 6057 | 20230104 | 1719 | 20230105 | 1323 | 1915937 | 1204 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 10626 | 38.9427 | -121.0567 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1796736 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223844537355 | 20230104 | 1737 | 20230105 | 1140 | 1916187 | 1083 | Transformer only | Vegetation | Tree - fell into line | 1 | 1083 | 38.6844 | -120.6558 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0006498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1796797 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | RECLOSER | 1252 | 20230104 | 1744 | 20230105 | 1533 | 1916318 | 1309 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 154552 | 38.8967 | -121.4874 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1796645 | 0 | Non-EPSS | N | 2023 | A & GRD
SIERRA | PLACER | HORSESHOE 1106 | 152571106 | OCB | 1106/2 | 20230104 | 1748 | 20230104 | 1946 | 1916377 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1675 | 197650 | 38.7444 | -121.161 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796652 | 0 | EPSS Ckt | N | 2023 | B+C+TIME OC
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5359 | 20230104 | 1748 | 20230105 | 752 | 1916319 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 54016 | 38.8842 | -121.1543 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0006436 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796734 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN 1105 | 152561105 | RECLOSER | 168616 | 20230104 | 1749 | 20230104 | 1904 | 1916389 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 14850 | 38.8543 | -121.1728 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796658 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2704 | 20230104 | 1749 | 20230105 | 1635 | 1916636 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 98449 | 38.8107 | -121.1649 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1796769 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5325 | 20230104 | 1757 | 20230105 | 1244 | 1916515 | 1127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 52969 | 38.9488 | -121.2191 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797652 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN 1106 | 152561106 | FUSE | 5021 | 20230104 | 1758 | 20230105 | 1747 | 1916521 | 1429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 71450 | 38.8305 | -121.2013 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1796872 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS 1107 | 152691107 | FUSE | 5727 | 20230104 | 1808 | 20230105 | 1006 | 1916731 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 4429 | 39.0189 | -121.0519 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0006483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1796782 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT 1101 | 152531101 | JUMPER | OJS 1P S/O CGC#222642244362 | 20230104 | 1814 | 20230105 | 1934 | 1916797 | 1520 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10640 | 38.8804 | -121.0729 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1796889 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS 2105 | 153132105 | RECLOSER | 2748 | 20230104 | 1819 | 20230105 | 950 | 1916817 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 897 | 172251 | 39.2082 | -121.2033 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1796700 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15257 | 20230104 | 1821 | 20230105 | 1907 | 1916650 | 1486 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19318 | 38.9265 | -121.2597 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1797702 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | SWITCH | 2511 | 20230104 | 1827 | 20230105 | 1322 | 1916951 | 1135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 92942 | 38.8242 | -121.4828 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006428 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1796726 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN 1107 | 152561107 | RECLOSER | 346 | 20230104 | 1831 | 20230104 | 2100 | 1916971 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 975 | 109014 | 38.8253 | -121.1632 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006425 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1796723 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222340053473 | 20230104 | 1846 | 20230105 | 1630 | 1917179 | 1304 | Transformer only | Vegetation | Tree - fell into line | 2 | 2608 | 39.1316 | -121.1765 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797586 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222680739271 | 20230104 | 1908 | 20230105 | 1503 | 1921735 | 1195 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2390 | 38.7422 | -121.061 | Yes | Clear;32-90 F |  |  | 23-0007260 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1797528 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY 1103 | 152031103 | FUSE | 7817 | 20230104 | 1917 | 20230105 | 1336 | 1916981 | 1099 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 98910 | 39.1527 | -121.1348 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1796823 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4483 | 20230104 | 1929 | 20230105 | 1139 | 1917673 | 970 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 33950 | 38.9059 | -120.9756 | Yes | Clear;32-90F |  |  | 23-0007350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797609 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER 1101 | 152461101 | RECLOSER | 106534 | 20230104 | 1938 | 20230104 | 2004 | 1917397 | 26 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 6266 | 38.8903 | -121.079 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006508 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1796806 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | EL DORADO | SHINGLE SPRINGS 1104 | 153651104 | TRANSFORMER | 222968235350 | 20230104 | 1943 | 20230106 | 1753 | 1917798 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5540 | 38.6327 | -120.9618 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0008328 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1798340 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | FUSE | 2485 | 20230104 | 1946 | 20230105 | 857 | 1917818 | 791 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 49783 | 38.8188 | -121.2554 | Yes | Clear;32-90F |  |  | 23-0007084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797377 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7207 | 20230104 | 1955 | 20230105 | 1404 | 1917884 | 1089 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 29055 | 38.9788 | -121.3691 | Yes | Clear;32-90 F |  |  | 23-0007530 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797746 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRIP-SAVER | 7559 | 20230104 | 1958 | 20230105 | 1020 | 1917948 | 862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 14400 | 39.0202 | -121.0625 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1796982 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | WEIMAR 1102 | 152491102 | FUSE | 8459 | 20230104 | 1959 | 20230105 | 958 | 1917922 | 839 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 9229 | 39.0275 | -121.0037 | Yes | Clear;32-90F |  |  | 23-0007190 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797470 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS 1105 | 152261105 | JUMPER | WIRE DOWN 1 SS OF MTR#1009890912 | 20230104 | 2008 | 20230105 | 1050 | 1918034 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1764 | 38.6952 | -120.8616 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1796912 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 222702649326 | 20230104 | 2019 | 20230105 | 1002 | 1918143 | 823 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 7407 | 39.0171 | -121.0499 | Yes | Clear;32-90F |  |  | 23-0007215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1797490 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 5187 | 20230104 | 2024 | 20230105 | 1927 | 1918196 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 24894 | 38.876 | -121.1361 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1797621 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL 1101 | 152181101 | RECLOSER | 50486 | 20230104 | 2043 | 20230105 | 1513 | 1918462 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 920 | 654009 | 38.9928 | -120.8828 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1796893 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31037 | 20230104 | 2046 | 20230106 | 853 | 1918547 | 2167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 6501 | 38.9311 | -120.9039 | Yes | Clear;32-90F | Cutout- fuse holder | Broken | 23-0007479 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797703 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12255 | 20230104 | 2048 | 20230105 | 1235 | 1922156 | 947 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 947 | 38.7683 | -120.617 | Yes | Clear;32-90F | Lightning Arrestor | Broken | 23-0007396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1797643 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19552 | 20230104 | 2048 | 20230105 | 1533 | 1918518 | 1125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 480 | 477670 | 38.7436 | -120.7818 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1796896 | 0 | EPSS Ckt | N | 2023 | B+C+TIME OC
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 92903 | 20230104 | 2049 | 20230105 | 1316 | 1921841 | 987 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 36519 | 38.7448 | -120.7826 | Yes | Clear;32-90F |  |  | 23-0007302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797565 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL 1103 | 153661103 | OCB | 1103/2 | 20230104 | 2050 | 20230105 | 1039 | 1918524 | 829 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1295 | 1073555 | 38.7393 | -120.6773 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1796899 | 0 | EPSS Ckt | N | 2023 | A+B+C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11439 | 20230104 | 2051 | 20230105 | 1005 | 1918503 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 48434 | 38.7331 | -120.789 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | Yes | 1797071 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OJ'S 1 POLE SS OF CGC 221937849025 | 20230104 | 2113 | 20230105 | 1115 | 1916906 | 842 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1684 | 39.0105 | -121.3187 | Yes | Clear;32-90F | Transformer (OH) | Arcing | 23-0006732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797034 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224252035772 | 20230104 | 2135 | 20230105 | 1940 | 1920268 | 1325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2405 | 38.6397 | -120.5118 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0006921 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1797221 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2027 | 20230104 | 2140 | 20230105 | 1618 | 1919050 | 1118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 131924 | 38.6358 | -120.6358 | Yes | Clear;32-90 F |  |  | 23-0007679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797871 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30573 | 20230104 | 2153 | 20230105 | 1020 | 1919132 | 747 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 26145 | 38.8208 | -121.0293 | Yes | Clear;32-90F |  |  | 23-0007253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797522 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 2102 | 20230104 | 2236 | 20230104 | 2253 | 1917998 | 17 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1091 | 18547 | 38.6825 | -120.8522 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006787 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797088 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20230104 | 2254 | 20230105 | 936 | 1919586 | 642 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 34026 | 38.8428 | -121.029 | Yes | Clear;32-90F |  |  | 23-0007170 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1797455 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | EL DORADO | DIAMOND SPRINGS 1107 | 152261107 | OTHER | J785L TWD 22433 | 20230104 | 2303 | 20230106 | 1326 | 1919632 | 2303 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6909 | 38.7091 | -120.8365 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0007119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797440 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | RECLOSER | 2222 | 20230104 | 2304 | 20230105 | 1120 | 1919667 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 216384 | 38.7708 | -121.2524 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797126 | 0 | Non-EPSS | N | 2023 | A C
SIERRA | EL DORADO | APPLE HILL 1104 | 153661104 | FUSE | 7965 | 20230104 | 2309 | 20230105 | 1224 | 1918632 | 795 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 14317 | 38.7533 | -120.6117 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007393 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797640 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38015 | 20230104 | 2334 | 20230106 | 1642 | 1919795 | 2468 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12340 | 38.8252 | -121.1589 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0007438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1797677 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 2135 | 20230104 | 2346 | 20230105 | 1320 | 1920044 | 814 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 59 | 48026 | 38.6955 | -120.8621 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797660 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS 1110 | 152691110 | FUSE | 7489 | 20230104 | 2349 | 20230105 | 1344 | 1919866 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 18409 | 39.0799 | -121.0125 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797422 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 9101 | 20230104 | 2357 | 20230105 | 1134 | 1919901 | 697 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 16031 | 38.6829 | -120.8914 | Yes | Clear;32-90F |  |  | 23-0007337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797594 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 154362 | 20230105 | 1 | 20230106 | 1151 | 1919993 | 2150 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 145516 | 38.8545 | -121.2009 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797186 | 0 | EPSS Ckt | N | 2023 | A GRD
SIERRA | PLACER | PENRYN 1103 | 152561103 | FUSE | 5265 | 20230105 | 19 | 20230105 | 1022 | 1919682 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 27738 | 38.8411 | -121.1552 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006893 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797193 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2109 | 153612109 | RECLOSER | 51742 | 20230105 | 141 | 20230105 | 908 | 1920275 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1260 | 563220 | 38.7292 | -121.082 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797225 | 0 | EPSS Ckt | N | 2023 | A C
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | RECLOSER | 50020 | 20230105 | 150 | 20230105 | 1535 | 1920306 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 473 | 285178 | 38.7361 | -121.171 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0006930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1797230 | 0 | Non-EPSS | N | 2023 | A B C
SIERRA | PLACER | DEL MAR 1103 | 152581103 | RECLOSER | 2702 | 20230105 | 205 | 20230105 | 1311 | 1920340 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 631 | 301748 | 38.8103 | -121.2068 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1797237 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 16741 | 20230105 | 208 | 20230105 | 1534 | 1920328 | 806 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1074 | 38.8462 | -121.377 | Yes | Clear;32-90 F |  |  | 23-0007655 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797852 | 1 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 20230105 | 232 | 20230105 | 2057 | 1920389 | 1105 | Distribution Circuit | Vegetation | Tree - fell into line | 4774 | 957238 | 38.7394 | -120.6774 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797252 | 0 | EPSS Ckt | N | 2023 | n/a
SIERRA | NEVADA | ALLEGHANY 1102 | 152101102 | RECLOSER | 1102/2 | 20230105 | 307 | 20230105 | 900 | 1920470 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 164 | 57892 | 39.4655 | -120.8443 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797263 | 0 | EPSS Ckt | N | 2023 | A C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 20230105 | 401 | 20230105 | 907 | 1920553 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 8874 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0007127 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797413 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS 1106 | 152261106 | FUSE | 41193 | 20230105 | 446 | 20230105 | 1536 | s1797846 | 650 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 650 | 38.6701 | -120.7766 | Yes | Clear;32-90 F |  |  | 23-0007643 |  | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797846 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1110 | 152481110 | FUSE | 32643 | 20230105 | 731 | 20230105 | 1626 | 1920931 | 535 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1070 | 39.2393 | -121.0578 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007103 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1797397 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4753 | 20230105 | 812 | 20230105 | 1059 | 1921109 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1503 | 39.3124 | -120.8823 | Yes | Clear;32-90F |  |  | 23-0007288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797552 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15287 | 20230105 | 918 | 20230105 | 1550 | 1921393 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3136 | 38.9369 | -121.2902 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0007281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797546 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1106 | 152481106 | JUMPER | WIRE DOWN @ CGC#222859652943 | 20230105 | 1000 | 20230105 | 1440 | 1921585 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1073 | 39.1158 | -120.9939 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | Yes | 1797541 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 7495 | 20230105 | 1011 | 20230105 | 1306 | 1921632 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1925 | 39.0643 | -121.0259 | Yes | Clear;32-90F |  |  | 23-0007382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797632 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN 1102 | 152161102 | FUSE | 29472 | 20230105 | 1047 | 20230105 | 1507 | 1921777 | 260 | Distribution Circuit | Animal | Bird found | 18 | 4680 | 38.8984 | -121.0698 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0007520 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797737 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20230105 | 1129 | 20230105 | 1144 | 1921978 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1013 | 14265 | 38.7759 | -120.4031 | Yes | Clear;32-90F |  |  | 23-0007342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797601 | 0 | EPSS Ckt | N | 2023 | C+GRD
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 33331 | 20230105 | 1204 | 20230105 | 1650 | 1921321 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4576 | 38.7432 | -121.1662 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0007358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797612 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1551 | 20230105 | 1230 | 20230105 | 1622 | 1922566 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 232 | 38.7679 | -120.6169 | Yes | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0007519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797736 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12257 | 20230105 | 1240 | 20230105 | 1814 | 1922593 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 334 | 38.769 | -120.6206 | Yes | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0007533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797748 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT 1101 | 152591101 | RECLOSER | 742 | 20230105 | 1413 | 20230106 | 1355 | 1922611 | 1422 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 152 | 213476 | 39.3236 | -120.3792 | Yes | Clear;32-90 F |  |  | 23-0007550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797767 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 836878 | 20230105 | 1516 | 20230105 | 1534 | 1920596 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3951 | 71118 | 38.7371 | -120.6759 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0007502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797835 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10291 | 20230105 | 1534 | 20230105 | 1705 | 1923023 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2912 | 38.6692 | -120.6696 | Yes | Clear;32-90 F |  |  | 23-0007664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797861 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12121 | 20230105 | 1553 | 20230105 | 1617 | 1923060 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 288 | 38.6376 | -120.6493 | Yes | Clear;32-90 F |  |  | 23-0007705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797889 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21469 | 20230105 | 1601 | 20230105 | 1912 | 1923094 | 191 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 1528 | 38.6015 | -120.6965 | Yes | Clear;32-90 F |  |  | 23-0007886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798047 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1053 | 20230105 | 1645 | 20230109 | 1725 | 1923703 | 5800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 298705 | 38.6534 | -120.6273 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0008009 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798141 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20230105 | 1655 | 20230106 | 1904 | 1923293 | 1505 | Distribution Circuit | Environmental/External | Ice or snow | 703 | 894809 | 38.773 | -120.2933 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007782 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797950 | 0 | EPSS Ckt | N | 2023 | A+GRD
SIERRA | EL DORADO | SHINGLE SPRINGS 2109 | 153652109 | TRANSFORMER | 223030238388 | 20230105 | 1736 | 20230106 | 1142 | 1923417 | 1086 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1086 | 38.7161 | -120.9391 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0008149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798238 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 741586 | 20230105 | 1811 | 20230106 | 1911 | 1923522 | 1500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 151246 | 38.8251 | -120.0374 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0007834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797998 | 0 | EPSS Ckt | N | 2023 | A+C TARGETS
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12319 | 20230105 | 1916 | 20230106 | 944 | 1923711 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6292 | 38.6221 | -120.7394 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1798035 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 8922 | 20230105 | 1959 | 20230106 | 1324 | s1798057 | 1045 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 40387 | 38.8227 | -120.0299 | Yes | Clear;32-90 F | Regulator | Burned/flashed | 23-0007834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1798057 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12257 | 20230105 | 2008 | 20230105 | 2014 | 1923776 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 6 | 38.769 | -120.6206 | Yes | Clear;32-90 F | Elbow | Normal | 23-0007903 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1798056 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 34407 | 20230105 | 2217 | 20230106 | 1358 | 1923951 | 941 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 11292 | 39.3251 | -120.372 | Yes | Clear;32-90F |  |  | 23-0008291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798319 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR 2109 | 152582109 | SWITCH | 50467 | 20230105 | 2234 | 20230106 | 719 | 1924170 | 525 | Distribution Circuit | 3rd Party | Vandalism | 645 | 338625 | 38.8383 | -121.2323 | Yes | Clear;32-90F | Switch (UG) | Normal | 23-0008085 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1798197 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230106 | 710 | 20230106 | 1225 | 1924152 | 315 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1469 | 38.7941 | -120.8199 | No | Clear;32-90F |  |  | 23-0008210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798279 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN 1101 | 152431101 | RECLOSER | 145584 | 20230106 | 940 | 20230106 | 1045 | 1924426 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 6240 | 39.1016 | -120.954 | No | Clear;32-90F | Recloser | Malfunctioning | 23-0008164 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1798250 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | TAMARACK 1101 | 152291101 | FUSE | 6653 | 20230106 | 1558 | 20230107 | 1140 | 1925323 | 1182 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 8274 | 39.322 | -120.4288 | No | Clear;32-90F | Insulator | Broken | 23-0008491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798421 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1101 | 152461101 | FUSE | 3819 | 20230106 | 1652 | 20230106 | 1859 | 1925207 | 127 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 147 | 18669 | 38.8993 | -121.0799 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0008522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1798450 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223149445087 | 20230106 | 1904 | 20230107 | 1029 | 1925585 | 925 | Transformer only | Vegetation | Tree - fell into line | 1 | 925 | 38.8995 | -120.8945 | No | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0008606 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798524 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223345338485 | 20230106 | 2008 | 20230107 | 1930 | 1925649 | 1402 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1402 | 38.7178 | -120.8286 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798701 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2543 | 20230107 | 947 | 20230107 | 1738 | 1926267 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 40506 | 38.7883 | -120.1531 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0008774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798646 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18709 | 20230107 | 1028 | 20230107 | 1724 | 1926144 | 416 | Distribution Circuit | Environmental/External | Lightning | 1 | 416 | 38.75 | -120.6132 | Yes | Clear;32-90F | Pothead(Riser Termination) | Failed/Faulted | 23-0008734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798617 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13362 | 20230107 | 1228 | 20230107 | 1434 | 1926566 | 126 | Distribution Circuit | Environmental/External | Ice or snow | 386 | 35604 | 38.7897 | -120.1519 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0008787 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798655 | 0 | EPSS Ckt | N | 2023 | TIME
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20265 | 20230107 | 1754 | 20230108 | 1449 | 1927415 | 1255 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 10040 | 38.5946 | -120.847 | Yes | Clear;32-90F |  |  | 23-0010222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800072 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | JUMPER | UNMAPPED FUCO 928615 | 20230107 | 1800 | 20230107 | 1930 | 1927947 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 810 | 38.905 | -121.265 | Yes | Clear;32-90F | Transformer (OH) | Normal | 23-0009057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798886 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1111 | 20230107 | 1805 | 20230108 | 1528 | 1931125 | 1283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 295090 | 38.7476 | -120.859 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1799805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222297441928 | 20230107 | 1808 | 20230109 | 1720 | 1927470 | 2832 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 5664 | 38.815 | -121.1944 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0009052 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798881 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 89934 | 20230107 | 1810 | 20230109 | 1658 | 1927476 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 1030 | 1197021 | 38.6491 | -120.6764 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1798815 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20230107 | 1811 | 20230108 | 1145 | 1927501 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 75910 | 39.0014 | -121.0224 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008990 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1798820 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 394169 | 20230107 | 1817 | 20230108 | 2059 | 1927510 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 38448 | 38.6965 | -120.8366 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009090 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1798919 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3689 | 20230107 | 1832 | 20230107 | 2127 | 1927573 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1225 | 39.261 | -121.1929 | Yes | Clear;32-90F |  |  | 23-0009095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798924 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 32747 | 20230107 | 1833 | 20230108 | 1848 | 1927593 | 1455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 224070 | 39.1426 | -121.0613 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1798875 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9349 | 20230107 | 1834 | 20230107 | 2226 | 1927613 | 232 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 10904 | 38.9354 | -120.7471 | Yes | Clear;32-90F |  |  | 23-0009242 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799072 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2140 | 20230107 | 1844 | 20230108 | 1428 | 1927634 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 127973 | 39.2895 | -120.9854 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009017 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1798844 | 0 | EPSS Ckt | N | 2023 | A+C+GRD
SIERRA | PLACER | PLACER 1104 | 152461104 | RECLOSER | 51734 | 20230107 | 1849 | 20230108 | 1311 | 1927650 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 1013 | 80707 | 38.9045 | -121.0827 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1798849 | 0 | EPSS Ckt | N | 2023 | B & GRD
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 591351 | 20230107 | 1914 | 20230109 | 1104 | 1927880 | 2390 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 198370 | 39.3222 | -120.3792 | Yes | Clear;32-90 F |  |  | 23-0011039 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800863 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20230107 | 1947 | 20230108 | 2025 | 1927938 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 1908 | 209108 | 38.6569 | -120.9928 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1798885 | 0 | EPSS Ckt | N | 2023 | C+GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 8605 | 20230107 | 2000 | 20230110 | 1242 | 1927975 | 3882 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 51786 | 38.8676 | -121.4787 | Yes | Clear;32-90F |  |  | 23-0010206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800058 | 1 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21469 | 20230107 | 2036 | 20230108 | 1159 | 1932596 | 923 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 7384 | 38.6015 | -120.6965 | Yes | Clear;32-90F |  |  | 23-0010062 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799906 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9329 | 20230107 | 2046 | 20230109 | 1502 | 1928032 | 2536 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 187326 | 38.8402 | -121.0386 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1799217 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 19910 | 20230107 | 2104 | 20230108 | 658 | 1928063 | 594 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 424 | 251856 | 38.6313 | -120.8542 | Yes | Rain-Strong Winds-Clear;32-90F |  |  | 23-0009116 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798944 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5385 | 20230107 | 2110 | 20230109 | 1227 | 1928076 | 2357 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 56568 | 38.9478 | -121.197 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0011195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800995 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 20230107 | 2141 | 20230107 | 2220 | 1928136 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 1131 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0009230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799060 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230107 | 2143 | 20230107 | 2336 | 1928139 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 105768 | 38.7391 | -120.6681 | Yes | Clear;32-90F |  |  | 23-0009146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799000 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 20305 | 20230107 | 2202 | 20230108 | 1410 | 1928221 | 968 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 15488 | 38.7189 | -121.0215 | Yes | Clear;32-90F |  |  | 23-0010111 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799959 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222422344400 | 20230107 | 2204 | 20230108 | 1149 | 1928062 | 825 | Transformer only | Vegetation | Tree - grew into line | 3 | 2475 | 38.8826 | -121.1495 | Yes | Clear;32-90 F | Transformer | Together | 23-0009372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799205 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 11169 | 20230107 | 2221 | 20230108 | 1112 | 1928325 | 771 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 34695 | 38.6932 | -120.8616 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0010054 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799898 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS 1104 | 152261104 | FUSE | 183495 | 20230107 | 2226 | 20230108 | 1702 | 1928363 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 81829 | 38.6733 | -120.8368 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009904 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799754 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18247 | 20230107 | 2242 | 20230109 | 1039 | 1931208 | 2157 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 21570 | 38.6921 | -120.6534 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011052 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800874 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 9889 | 20230107 | 2311 | 20230109 | 1427 | 1928930 | 2356 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 160208 | 38.7118 | -120.851 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799973 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | FUSE | 32167 | 20230107 | 2317 | 20230108 | 1954 | 1929089 | 1237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 18555 | 38.7869 | -121.2588 | Yes | Clear;32-90 F |  |  | 23-0010458 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800304 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | BELL 1107 | 152701107 | FUSE | 5679 | 20230107 | 2334 | 20230108 | 2022 | 1929286 | 1248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 36192 | 38.985 | -121.1355 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0010472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800319 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL 1109 | 152701109 | FUSE | 30273 | 20230107 | 2336 | 20230108 | 1632 | 1930399 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 61976 | 38.9576 | -121.0612 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009499 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799331 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY 1102 | 152241102 | RECLOSER | 39104 | 20230107 | 2338 | 20230108 | 1827 | 1929470 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 710 | 610587 | 38.9732 | -121.0141 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799243 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | RECLOSER | 1050 | 20230107 | 2342 | 20230108 | 1912 | 1929673 | 1170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 30420 | 38.7916 | -121.2372 | Yes | Clear;32-90F |  |  | 23-0009429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | No | No | 1799262 | 0 | Non-EPSS | N | 2023 | A B C GRD
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 35637 | 20230107 | 2348 | 20230113 | 1812 | 1934289 | 8304 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8304 | 38.795 | -121.4791 | Yes | Clear;32-90F | Service conductor | Normal | 23-0010373 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1800221 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2103 | 153612103 | RECLOSER | 6842 | 20230107 | 2349 | 20230111 | 1336 | 1929724 | 5147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1549 | 828936 | 38.6419 | -121.0734 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799686 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | RECLOSER | 1826 | 20230108 | 0 | 20230108 | 1952 | 1930185 | 1192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 752 | 423309 | 38.7523 | -121.1933 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0009918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799770 | 0 | EPSS Ckt | N | 2023 | A+C
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20230108 | 0 | 20230108 | 1245 | 1930259 | 765 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 409 | 312885 | 38.7121 | -120.9501 | Yes | Clear;32-90F |  |  | 23-0009453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799286 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230108 | 2 | 20230112 | 1750 | 1930256 | 6828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 286776 | 38.8458 | -121.482 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Insulator | Broken | 23-0011011 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800842 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 3103 | 20230108 | 4 | 20230109 | 1035 | 1930286 | 2071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 113905 | 38.7516 | -121.3464 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0010302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800150 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18773 | 20230108 | 5 | 20230111 | 1420 | 1930348 | 5175 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 102050 | 38.6472 | -120.9436 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0009905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799755 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 6502 | 20230108 | 14 | 20230108 | 1421 | 1932279 | 847 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1700 | 1439900 | 38.7126 | -121.0782 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799867 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 30659 | 20230108 | 14 | 20230109 | 1058 | 1934137 | 2084 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 31260 | 38.9082 | -121.1046 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0010339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800188 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | RECLOSER | 50022 | 20230108 | 15 | 20230109 | 1341 | 1930743 | 2246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 543 | 613164 | 38.7357 | -121.1705 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0009480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799313 | 0 | Non-EPSS | N | 2023 | B C
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5405 | 20230108 | 16 | 20230108 | 1723 | 1930677 | 1027 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 66755 | 38.9096 | -121.0882 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0010334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800183 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2106 | 153612106 | RECLOSER | 19642 | 20230108 | 18 | 20230108 | 1341 | 1930755 | 803 | Distribution Circuit | Vegetation | Tree - branch fell on line | 847 | 680141 | 38.6832 | -121.0684 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799318 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | LINCOLN 1101 | 153701101 | TRANSFORMER | 222153545155 | 20230108 | 19 | 20230109 | 1501 | 1931368 | 2322 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2322 | 38.9039 | -121.2447 | Yes | Clear;32-90 F | Transformer (OH) | Leaking | 23-0010442 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800286 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7585 | 20230108 | 27 | 20230109 | 1906 | 1934756 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 43503 | 38.7722 | -121.4512 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1800333 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7585 | 20230108 | 27 | 20230109 | 1906 | 1934756 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 43503 | 38.7722 | -121.4512 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1800333 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 3861 | 20230108 | 27 | 20230108 | 1605 | 1930945 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 46900 | 38.7827 | -121.1456 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009910 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1799761 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 33531 | 20230108 | 27 | 20230109 | 1118 | 1930940 | 2091 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 25092 | 38.8488 | -121.159 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800281 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 50550 | 20230108 | 30 | 20230108 | 1504 | 1931049 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 181723 | 38.8511 | -121.1794 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799349 | 0 | EPSS Ckt | N | 2023 | A B TIME
SIERRA | EL DORADO | SHINGLE SPRINGS 1103 | 153651103 | FUSE | 8317 | 20230108 | 31 | 20230108 | 1531 | 1931024 | 900 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 63900 | 38.6523 | -120.9663 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0010152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800001 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11039 | 20230108 | 31 | 20230109 | 2049 | 1931008 | 2658 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31896 | 38.7888 | -120.9323 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800130 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223094036462 | 20230108 | 31 | 20230109 | 1806 | 1931650 | 2495 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2495 | 38.6629 | -120.9175 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0011135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800943 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7207 | 20230108 | 31 | 20230108 | 855 | 1931089 | 504 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 20160 | 38.9788 | -121.3691 | Yes | Clear;32-90F |  |  | 23-0009906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799756 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2218 | 20230108 | 34 | 20230108 | 1554 | 1929976 | 920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 101476 | 38.9803 | -121.4147 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0009526 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799358 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230108 | 37 | 20230108 | 1359 | s1813639 | 802 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 750672 | 38.7391 | -120.6681 | Yes | Clear;32-90F |  |  | 23-0009146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1813639 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15315 | 20230108 | 37 | 20230108 | 755 | 1931080 | 438 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 9198 | 38.9851 | -121.3403 | Yes | Clear;32-90F |  |  | 23-0009881 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799730 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | JUMPER | WIRE DOWN 2 SPANS E/OF CGC 222283043460 | 20230108 | 46 | 20230109 | 1739 | 1931328 | 2453 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 18599 | 38.8578 | -121.1984 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009820 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | No | 1799660 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 9651 | 20230108 | 47 | 20230109 | 1110 | 1931238 | 2063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 57764 | 38.736 | -121.1843 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800196 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE 1104 | 152571104 | FUSE | 30095 | 20230108 | 48 | 20230108 | 1106 | 1931273 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 108 | 66744 | 38.7671 | -121.154 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 23-0010050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799895 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20230108 | 49 | 20230108 | 2041 | 1931323 | 1192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 679 | 305686 | 38.8546 | -121.1508 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799371 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 41039 | 20230108 | 50 | 20230108 | 1339 | 1931288 | 769 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 128 | 98432 | 38.9304 | -121.075 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0010167 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800017 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 6873 | 20230108 | 52 | 20230108 | 915 | 1931329 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12072 | 39.0673 | -121.0343 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0009928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1799778 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 2073 | 20230108 | 54 | 20230109 | 2101 | 1932496 | 2647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 13235 | 38.6118 | -120.9285 | Yes | Clear;32-90 F | Insulator | Broken | 23-0010451 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800297 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20230108 | 58 | 20230108 | 1042 | 1931467 | 584 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 30952 | 38.8428 | -121.029 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0010028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1799873 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 84093 | 20230108 | 58 | 20230109 | 1349 | 1931409 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 68541 | 38.8402 | -121.1311 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010079 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799925 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5359 | 20230108 | 100 | 20230108 | 1351 | 1931415 | 771 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 49344 | 38.8842 | -121.1543 | Yes | Clear;32-90F |  |  | 23-0010155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800005 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | OTHER | WIRE DOWN 1 SPAN LD SIDE 290705 | 20230108 | 102 | 20230108 | 2105 | 1933556 | 1203 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 180154 | 38.6868 | -120.8138 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010144 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1799993 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 69443 | 20230108 | 102 | 20230108 | 2048 | 1931466 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41510 | 38.8649 | -121.1526 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800074 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 8353 | 20230108 | 103 | 20230109 | 1202 | 1931638 | 2099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 48277 | 38.884 | -121.3774 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1800135 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 16741 | 20230108 | 105 | 20230109 | 1755 | 1931493 | 2450 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 3263 | 38.8462 | -121.377 | Yes | Clear;32-90F |  |  | 23-0011500 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801257 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | OTHER | WIRE DOWN FUCO 5153 | 20230108 | 107 | 20230112 | 2044 | 1941522 | 6937 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 126225 | 38.7462 | -121.1861 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012153 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801921 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 22603 | 20230108 | 109 | 20230108 | 1432 | 1931515 | 803 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 1606 | 38.7422 | -121.0605 | Yes | Clear;32-90F |  |  | 23-0010240 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800090 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE 1112 | 153081112 | OCB | 1112/2 | 20230108 | 109 | 20230109 | 2118 | 1931516 | 2649 | Distribution Circuit | Vegetation | Tree - fell into line | 2113 | 1796302 | 38.7313 | -120.7839 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799407 | 0 | EPSS Ckt | N | 2023 | C GRD TIME
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | RECLOSER | 2222 | 20230108 | 112 | 20230108 | 1737 | 1931420 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 229390 | 38.7708 | -121.2524 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799414 | 0 | Non-EPSS | N | 2023 | C GRD
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 4039 | 20230108 | 113 | 20230108 | 2121 | 1931666 | 1208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 16912 | 38.8566 | -121.1637 | Yes | Clear;32-90F |  |  | 23-0010529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800380 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20230108 | 113 | 20230109 | 910 | 1931673 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 3018 | 2769564 | 38.7716 | -120.8148 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799425 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 40665 | 20230108 | 115 | 20230109 | 1116 | 1931564 | 2041 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 8164 | 38.9809 | -121.0732 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800416 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1107 | 152691107 | FUSE | 9901 | 20230108 | 115 | 20230108 | 2008 | 1931567 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 101833 | 39.0041 | -121.055 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800060 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 9453 | 20230108 | 115 | 20230109 | 1039 | 1931562 | 2004 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 62124 | 38.9421 | -121.1957 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0010949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800788 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21969 | 20230108 | 119 | 20230108 | 1640 | 1931831 | 921 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 3684 | 38.6912 | -120.8868 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800178 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 40666 | 20230108 | 119 | 20230108 | 837 | 1931693 | 438 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 228 | 99864 | 38.8869 | -121.0707 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0009635 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799467 | 0 | EPSS Ckt | N | 2023 | B C & INST
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 20230108 | 120 | 20230108 | 656 | 1931698 | 336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 9744 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0009838 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799688 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | RECLOSER | 13312 | 20230108 | 124 | 20230109 | 1624 | 1931732 | 2316 | Distribution Circuit | Vegetation | Tree - fell into line | 1295 | 1074348 | 38.7435 | -120.7341 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0009643 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799476 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20230108 | 124 | 20230108 | 1230 | 1931724 | 666 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 51948 | 38.7309 | -120.8421 | Yes | Overcast-Strong Winds;32-90 F |  |  | 23-0010097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799944 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 8785 | 20230108 | 125 | 20230109 | 1625 | 1931704 | 2340 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 60840 | 38.8587 | -121.1786 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800144 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1593 | 20230108 | 125 | 20230109 | 1732 | 1931720 | 2407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 322538 | 38.619 | -120.9296 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800235 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5671 | 20230108 | 127 | 20230108 | 1209 | 1931728 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 102078 | 38.9203 | -121.0865 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0010044 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799889 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE 1109 | 153081109 | FUSE | 21001 | 20230108 | 130 | 20230108 | 959 | 1931741 | 509 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 45301 | 38.7321 | -120.761 | Yes | Clear;32-90F |  |  | 23-0009953 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799803 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20230108 | 132 | 20230109 | 1629 | 1931818 | 2337 | Distribution Circuit | Vegetation | Tree - fell into line | 1276 | 1983006 | 38.7617 | -120.5592 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009647 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799480 | 0 | EPSS Ckt | N | 2023 | B GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20230108 | 133 | 20230109 | 2154 | 1931772 | 2661 | Distribution Circuit | Vegetation | Tree - fell into line | 453 | 1136163 | 38.7166 | -120.5803 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009898 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1799747 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 38885 | 20230108 | 133 | 20230108 | 1517 | 1931825 | 824 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 14008 | 38.8234 | -121.116 | Yes | Clear;32-90F |  |  | 23-0010268 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1800115 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 3503 | 20230108 | 136 | 20230109 | 1509 | 1931766 | 2253 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 56316 | 39.1937 | -121.253 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0009885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799734 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 1381 | 20230108 | 137 | 20230109 | 1823 | 1933817 | 2446 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 53812 | 38.7557 | -120.6013 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010234 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800084 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5119 | 20230108 | 143 | 20230108 | 1246 | 1931828 | 663 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 37128 | 38.8102 | -121.1543 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799997 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OTHER | WIRE DOWN 1 LD SIDE CGC2240008240567 | 20230108 | 146 | 20230109 | 1400 | 1931839 | 2174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 23201 | 38.7722 | -120.5955 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1800103 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 41187 | 20230108 | 151 | 20230109 | 1342 | 1931854 | 2151 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 75285 | 38.6786 | -120.7709 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799776 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 20239 | 20230108 | 151 | 20230109 | 1458 | 1931857 | 2227 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 57902 | 38.6457 | -120.9852 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010236 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800085 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18507 | 20230108 | 158 | 20230109 | 1629 | 1933211 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27732 | 38.762 | -120.5384 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010040 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799885 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1351 | 20230108 | 203 | 20230108 | 1044 | 1931977 | 521 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 11971 | 38.5954 | -120.6169 | Yes | Clear;32-90F |  |  | 23-0009969 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799818 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1361 | 20230108 | 210 | 20230109 | 1423 | 1933027 | 2173 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 42845 | 38.5813 | -120.5699 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799837 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1037 | 20230108 | 359 | 20230108 | 2130 | 1932133 | 1051 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 83422 | 38.7018 | -120.8451 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 23-0010041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799886 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH 2102 | 152762102 | RECLOSER | 19542 | 20230108 | 359 | 20230108 | 1444 | 1932157 | 412 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 593 | 380113 | 38.7617 | -120.5776 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0009799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799638 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | SHADY GLEN 1102 | 152431102 | FUSE | 6575 | 20230108 | 536 | 20230109 | 1520 | 1932265 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 26609 | 39.1392 | -120.9663 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799946 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 33485 | 20230108 | 543 | 20230108 | 2112 | 1932274 | 929 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1858 | 38.8658 | -121.0803 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800298 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222353855603 | 20230108 | 544 | 20230108 | 1933 | 1932277 | 829 | Transformer only | Vegetation | Tree - fell into line | 2 | 1658 | 39.1903 | -121.1705 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0010146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799995 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18743 | 20230108 | 723 | 20230109 | 2055 | 1932512 | 2252 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13056 | 38.6153 | -120.8576 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799984 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7227 | 20230108 | 724 | 20230108 | 1740 | 1932516 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8624 | 39.2305 | -121.1361 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799859 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 63099 | 20230108 | 840 | 20230109 | 1923 | 1931858 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10415 | 38.7335 | -120.7926 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800009 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21581 | 20230108 | 856 | 20230108 | 1153 | 1932820 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5664 | 38.6618 | -120.8666 | Yes | Clear;32-90F |  |  | 23-0010094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799940 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18741 | 20230108 | 954 | 20230108 | 1056 | 1933208 | 62 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 48 | 2952 | 38.7144 | -121.0565 | Yes | Strong Winds-Rain-Clear;32-90F |  |  | 23-0010038 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1799883 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1285 | 20230108 | 955 | 20230109 | 1924 | 1933016 | 2009 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26117 | 38.6238 | -120.9094 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0010304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800152 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1107 | 152481107 | SWITCH | 969778 | 20230108 | 958 | 20230108 | 1833 | s1800270 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 72615 | 39.2213 | -121.0602 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0009993 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1800270 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223059334564 | 20230108 | 1059 | 20230110 | 1226 | 1934579 | 2967 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2967 | 38.611 | -120.9296 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0010450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1800296 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 3377 | 20230108 | 1216 | 20230108 | 1720 | 1933465 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 173 | 52592 | 38.9439 | -120.7215 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010308 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800155 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 30651 | 20230108 | 1243 | 20230108 | 1905 | 1933533 | 382 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3438 | 39.0009 | -121.0239 | Yes | Clear;32-90 F |  |  | 23-0010457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800303 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32971 | 20230108 | 1256 | 20230108 | 1440 | 1933581 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 312 | 39.2726 | -121.2052 | Yes | Clear;32-90F |  |  | 23-0010195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800047 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18997 | 20230108 | 1348 | 20230109 | 1355 | 1933685 | 1447 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 5788 | 38.6312 | -120.7941 | Yes | Clear;32-90F |  |  | 23-0011266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801048 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE 1110 | 153081110 | TRANSFORMER | 223381739080 | 20230108 | 1353 | 20230108 | 2111 | 1933699 | 438 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3066 | 38.7335 | -120.8155 | Yes | Clear;32-90F | Service conductor | Burned/flashed | 23-0010512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800362 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 22909 | 20230108 | 1357 | 20230109 | 1904 | 1933709 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7540 | 38.7509 | -120.7392 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010311 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800158 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18563 | 20230108 | 1407 | 20230108 | 1738 | 1933721 | 211 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1055 | 38.7431 | -120.6394 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010368 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800217 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | TRANSFORMER | 222392139286 | 20230108 | 1423 | 20230109 | 1035 | 1933783 | 1212 | Transformer only | Environmental/External | Water | 5 | 6060 | 38.7422 | -121.1624 | Yes | Heavy Rain-Clear;32-90 F | Transformer | Broken | 23-0010218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1800069 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 13777 | 20230108 | 1439 | 20230108 | 1536 | 1933805 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 3135 | 38.7292 | -121.092 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800141 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 41079 | 20230108 | 1456 | 20230108 | 1821 | 1933871 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2870 | 38.7321 | -120.7464 | Yes | Clear;32-90F |  |  | 23-0010412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800259 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | RECLOSER | 51674 | 20230108 | 1537 | 20230108 | 1559 | 1933514 | 22 | Distribution Circuit | Company Initiated | Return Circuit Normal | 168 | 3696 | 38.8252 | -121.1919 | Yes | Clear;32-90F | Other | Normal | 23-0009517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1800127 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 2259 | 20230108 | 1702 | 20230112 | 1806 | 1934199 | 5824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 75712 | 38.9657 | -121.4051 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802265 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2543 | 20230108 | 1852 | 20230110 | 1221 | 1938549 | 2489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 214054 | 38.7883 | -120.1531 | Yes | Overcast-Drizzle;32-90 F | Insulator | Broken | 23-0011348 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801123 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2543 | 20230108 | 1852 | 20230110 | 1221 | 1938549 | 2489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 214054 | 38.7883 | -120.1531 | Yes | Overcast-Drizzle;32-90 F | Insulator | Broken | 23-0011348 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801123 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5837 | 20230108 | 1914 | 20230111 | 2148 | 1934517 | 4474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 35792 | 38.8578 | -120.8381 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801019 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 84017 | 20230108 | 1924 | 20230108 | 1945 | 1934609 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 42 | 38.9121 | -121.2416 | Yes | Clear;32-90 F |  |  | 23-0010454 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800300 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | JUMPER | OJ 2 SS OF CGC# 222624543828 | 20230108 | 2111 | 20230109 | 1611 | 1934801 | 1140 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1140 | 38.8659 | -121.0793 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0010452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1800378 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7945 | 20230109 | 12 | 20230109 | 1015 | 1935043 | 603 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 25929 | 38.748 | -121.4698 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 23-0010971 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800811 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 215201 | 20230109 | 16 | 20230110 | 1618 | 1938623 | 2334 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 72510 | 38.7512 | -121.4391 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1801328 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20230109 | 28 | 20230109 | 1324 | 1935076 | 776 | Distribution Circuit | Vegetation | Tree - branch fell on line | 388 | 301088 | 39.2034 | -121.0788 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1800527 | 0 | EPSS Ckt | N | 2023 | ABC GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 8929 | 20230109 | 28 | 20230110 | 1329 | 1937392 | 2221 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 75514 | 39.2121 | -121.098 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010988 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1800824 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1102 | 152151102 | FUSE | 7933 | 20230109 | 48 | 20230112 | 2045 | 1935118 | 5517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 75798 | 38.8018 | -121.4513 | Yes | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken | 23-0011327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801103 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10595 | 20230109 | 206 | 20230109 | 1129 | 1935446 | 563 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 17453 | 38.598 | -120.6485 | Yes | Clear;32-90F |  |  | 23-0011154 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800959 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21469 | 20230109 | 318 | 20230109 | 1010 | 1935418 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3296 | 38.6015 | -120.6965 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0011073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800889 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | OTHER | WIRE DOWN LS/OF CGC 223397939251 | 20230109 | 332 | 20230109 | 1906 | 1937719 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 28190 | 38.739 | -120.8097 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | No | 1800893 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 173934 | 20230109 | 338 | 20230109 | 1755 | 1935489 | 857 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 142317 | 39.2841 | -121.0236 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010749 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800615 | 0 | EPSS Ckt | N | 2023 | SGF 50(INST)
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20230109 | 357 | 20230110 | 812 | 1935386 | 1695 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5085 | 38.8544 | -121.1507 | Yes | Overcast-Rain;32-90 F | Secondary | Normal | 23-0010752 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1800618 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 20230109 | 404 | 20230109 | 950 | 1937165 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 27334 | 38.686 | -120.6419 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800772 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222439156298 | 20230109 | 429 | 20230110 | 1307 | 1935605 | 1958 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 5874 | 39.21 | -121.14 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0010891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800739 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 51564 | 20230109 | 608 | 20230109 | 637 | 1936013 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1352 | 34439 | 38.6449 | -121.0682 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Switch (OH) | Arcing | 23-0010807 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1800666 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7055 | 20230109 | 646 | 20230109 | 1750 | 1936288 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14608 | 39.1909 | -120.9915 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1800945 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 6755 | 20230109 | 722 | 20230110 | 1105 | 1936481 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 10800 | 39.2962 | -120.9866 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0010978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800817 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230109 | 734 | 20230109 | 1338 | 1936530 | 364 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 5096 | 38.7941 | -120.8199 | Yes | Clear;32-90F |  |  | 23-0011241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801030 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20230109 | 741 | 20230109 | 1214 | 1936555 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1365 | 38.8986 | -120.8986 | Yes | Clear;32-90F |  |  | 23-0011087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800902 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 20230109 | 742 | 20230109 | 1006 | 1936562 | 144 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 25200 | 38.9133 | -120.9318 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010859 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800708 | 0 | EPSS Ckt | N | 2023 | B & C
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 4169 | 20230109 | 755 | 20230109 | 943 | 1936605 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 4320 | 39.11 | -121.0303 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20230109 | 758 | 20230109 | 1931 | 1936628 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 31014 | 38.9463 | -121.2467 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 23-0010863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800715 | 0 | EPSS Ckt | N | 2023 | A & B
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 30649 | 20230109 | 808 | 20230109 | 1111 | 1936697 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 3477 | 39.2777 | -121.2074 | Yes | Clear;32-90F |  |  | 23-0011089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800903 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20230109 | 822 | 20230109 | 836 | 1936866 | 14 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 409 | 5726 | 38.7121 | -120.9501 | Yes | Clear;32-90F |  |  | 23-0010894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800742 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 4875 | 20230109 | 833 | 20230109 | 1051 | 1936977 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 4830 | 39.0832 | -121.0013 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011061 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800881 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 20230109 | 841 | 20230109 | 1331 | 1937041 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 22330 | 38.7941 | -120.7143 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011232 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801023 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 196418 | 20230109 | 924 | 20230109 | 1828 | 1937286 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 42432 | 38.8592 | -121.157 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 23-0010958 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800797 | 0 | EPSS Ckt | N | 2023 | A & B
SIERRA | PLACER | EAST NICOLAUS-1102 | 152151102 | FUSE | 37577 | 20230109 | 1035 | 20230109 | 1746 | 1937655 | 431 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2155 | 38.8242 | -121.4761 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801243 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | JUMPER | 2 SPAN SS CGC 223298836947 | 20230109 | 1040 | 20230110 | 955 | 1937699 | 1395 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2790 | 38.6766 | -120.8453 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0011082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1800897 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | JUMPER | OJS @ CGC# 223095736444 TO THE S/E | 20230109 | 1040 | 20230110 | 948 | 1937671 | 1388 | Distribution Circuit | Vegetation | Other ground vegetation | 2 | 2776 | 38.6623 | -120.9168 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801127 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 38093 | 20230109 | 1153 | 20230111 | 1827 | 1938091 | 3274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3274 | 38.926 | -121.2136 | Yes | Clear;32-90F | Insulator | Broken | 23-0011177 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800981 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | RECLOSER | 50514 | 20230109 | 1205 | 20230110 | 1623 | 1938037 | 1698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 630 | 125149 | 38.8385 | -121.3225 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0010844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1800960 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8953 | 20230109 | 1316 | 20230109 | 1435 | 1938259 | 79 | Distribution Circuit | Animal | Bird found | 6 | 474 | 39.1869 | -120.9724 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801081 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 5999 | 20230109 | 1345 | 20230109 | 1430 | 1938388 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 225 | 39.316 | -120.6138 | Yes | Clear;32-90F |  |  | 23-0011278 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801055 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5891 | 20230109 | 1427 | 20230109 | 1758 | 1938448 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3413 | 38.8911 | -120.8621 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011369 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801138 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 20497 | 20230109 | 1459 | 20230110 | 1127 | 1938544 | 1228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 4912 | 38.7621 | -120.8625 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0012059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801838 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5279 | 20230109 | 1531 | 20230109 | 1748 | 1938665 | 137 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 11 | 1507 | 38.8113 | -121.1232 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011464 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801222 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 8901 | 20230109 | 1551 | 20230109 | 2036 | 1938719 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6270 | 38.8628 | -121.1313 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801165 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 33411 | 20230109 | 1650 | 20230109 | 1659 | 1938979 | 9 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9 | 38.8727 | -121.3401 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0011457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801215 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18507 | 20230109 | 1656 | 20230109 | 1911 | 1938947 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1620 | 38.762 | -120.5384 | Yes | Clear;32-90F |  |  | 23-0011541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801303 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20521 | 20230109 | 1725 | 20230109 | 1926 | 1939050 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 726 | 38.6497 | -120.676 | Yes | Clear;32-90F |  |  | 23-0011570 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801333 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1102 | 152151102 | FUSE | 7885 | 20230109 | 1755 | 20230109 | 1845 | 1939312 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 100 | 38.8968 | -121.4698 | Yes | Clear;32-90F |  |  | 23-0011533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801292 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20230109 | 1839 | 20230109 | 1936 | 1939323 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4315 | 245955 | 39.2082 | -121.2033 | Yes | Clear;32-90 F | Recloser | Burned/flashed | 23-0011528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801298 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 196418 | 20230109 | 1856 | 20230110 | 1539 | 1939304 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 96954 | 38.8592 | -121.157 | Yes | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801309 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 20307 | 20230109 | 2010 | 20230110 | 940 | 1939541 | 810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 810 | 38.719 | -121.0186 | Yes | Clear;32-90F | Fuse | Arcing | 23-0011591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801356 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR 1101 | 152491101 | FUSE | 30745 | 20230109 | 2010 | 20230109 | 2130 | 1939550 | 80 | Distribution Circuit | 3rd Party | Vehicle | 56 | 4480 | 39.0433 | -120.9863 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1801398 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 30745 | 20230109 | 2159 | 20230109 | 2341 | 1939733 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 3810 | 39.0433 | -120.9863 | Yes | Clear;32-90F |  |  | 23-0011699 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801459 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20230110 | 357 | 20230113 | 1413 | 1941432 | 4936 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 586820 | 38.9847 | -121.366 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0011850 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1801614 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3643 | 20230110 | 358 | 20230110 | 2036 | 1944476 | 998 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 10989 | 38.7363 | -121.196 | Yes | Clear;32-90 F | Insulator | Broken | 23-0012089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801956 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2308 | 20230110 | 358 | 20230110 | 2017 | 1941529 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 515963 | 38.9265 | -121.2905 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011890 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1801658 | 0 | EPSS Ckt | N | 2023 | BC GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 685276 | 20230110 | 402 | 20230110 | 1040 | 1941538 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 80867 | 38.9848 | -121.2917 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1801616 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 3861 | 20230110 | 404 | 20230111 | 1918 | 1941502 | 2354 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 56401 | 38.7827 | -121.1456 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802082 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | JUMPER | OJ @ LINE & BUCK TWDS 89297 | 20230110 | 404 | 20230112 | 1203 | 1946077 | 3359 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10077 | 38.8865 | -121.2147 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1802429 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7207 | 20230110 | 404 | 20230110 | 1527 | 1941513 | 683 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 18222 | 38.9788 | -121.3691 | Yes | Clear;32-90 F |  |  | 23-0012678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802324 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | OTHER | WIRE DOWN SPAN N/OF 5015 | 20230110 | 405 | 20230111 | 1736 | 1941507 | 2224 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 174743 | 38.8398 | -121.2011 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1802133 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 30101 | 20230110 | 406 | 20230112 | 2039 | s1802210 | 3873 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11619 | 38.762 | -121.1919 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012514 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802210 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 89455 | 20230110 | 406 | 20230110 | 1524 | 1941598 | 678 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 13560 | 38.8195 | -121.1398 | Yes | Clear;32-90 F |  |  | 23-0012670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802322 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20230110 | 406 | 20230110 | 1518 | 1941555 | 672 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1916 | 372386 | 38.6569 | -120.9928 | Yes | Overcast-Rain;32-90 F | Jumper | Broken | 23-0011887 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1801655 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20230110 | 407 | 20230110 | 1713 | 1941623 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 782 | 119325 | 38.8544 | -121.1507 | Yes | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0011894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801662 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | OTHER | WIRE DOWN CGC#223188638303 | 20230110 | 413 | 20230110 | 1235 | 1941636 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4729 | 38.7129 | -120.8831 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1801971 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE 1101 | 152271101 | FUSE | 5435 | 20230110 | 413 | 20230110 | 1338 | 1941716 | 565 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 41245 | 38.8793 | -121.1264 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0012484 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802187 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222680739271 | 20230110 | 414 | 20230110 | 1639 | 1941655 | 745 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1490 | 38.7422 | -121.061 | Yes | Clear;32-90 F | Transformer | Burned Open | 23-0012773 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802374 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1101 | 152461101 | OCB | 1101/2 | 20230110 | 414 | 20230111 | 1513 | 1941699 | 2099 | Distribution Circuit | Vegetation | Tree - fell into line | 1116 | 406394 | 38.9015 | -121.088 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1801642 | 0 | EPSS Ckt | N | 2023 | A B C GRD INST OC
SIERRA | PLACER | PLACER-1104 | 152461104 | RECLOSER | 2097 | 20230110 | 414 | 20230110 | 1105 | 1941682 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 1104 | 374249 | 38.9175 | -121.059 | Yes | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0011884 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801651 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 30273 | 20230110 | 415 | 20230112 | 1504 | 1941658 | 3529 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 22789 | 38.9576 | -121.0612 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801855 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222444856050 | 20230110 | 415 | 20230110 | 1648 | 1944369 | 753 | Transformer only | Vegetation | Tree - fell into line | 1 | 753 | 39.2031 | -121.1387 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012521 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802218 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5403 | 20230110 | 415 | 20230110 | 1745 | 1941659 | 810 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 22680 | 38.8943 | -121.097 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802341 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 8987 | 20230110 | 416 | 20230110 | 853 | 1941680 | 277 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 5263 | 39.0573 | -121.1401 | Yes | Clear;32-90 F |  |  | 23-0012068 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801846 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18377 | 20230110 | 417 | 20230110 | 1245 | 1941857 | 508 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 7620 | 38.6295 | -120.7936 | Yes | Strong Winds-Heavy Rain; |  |  | 23-0012403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802129 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | TRANSFORMER | 222670545355 | 20230110 | 418 | 20230111 | 1315 | 1941715 | 1977 | Transformer only | Environmental/External | Water | 20 | 39540 | 38.9083 | -121.0627 | Yes | Strong Winds-Heavy Rain;32-90 F | Transformer | Broken- wire on ground | 23-0012419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802140 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL 1110 | 152701110 | FUSE | 31617 | 20230110 | 418 | 20230110 | 1240 | 1941704 | 502 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 8032 | 38.9346 | -121.0883 | Yes | Strong Winds-Heavy Rain; |  |  | 23-0012397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802123 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20230110 | 418 | 20230110 | 927 | 1941811 | 309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 647 | 199923 | 39.0757 | -121.1143 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0011880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801647 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | PLACER | HIGGINS-1107 | 152691107 | FUSE | 9901 | 20230110 | 418 | 20230110 | 1732 | 1942359 | 794 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 56667 | 39.0041 | -121.055 | Yes | Overcast-Rain;32-90 F |  |  | 23-0012861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802441 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18939 | 20230110 | 420 | 20230111 | 1443 | 1945545 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10315 | 38.6302 | -120.8255 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802277 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20230110 | 420 | 20230111 | 1816 | 1942018 | 2202 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 2679319 | 38.7716 | -120.8148 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801641 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230110 | 420 | 20230110 | 1242 | 1944063 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7028 | 38.7941 | -120.8199 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0012093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801866 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 24189 | 20230110 | 420 | 20230111 | 1512 | 1944897 | 2092 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18828 | 38.8025 | -120.7947 | Yes | Strong Winds-Heavy Rain; | Pole-Wood | Broken | 23-0012326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802073 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3817 | 20230110 | 420 | 20230111 | 1454 | 1945819 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 31110 | 38.9126 | -120.8265 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012738 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1802354 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32369 | 20230110 | 420 | 20230112 | 1300 | 1946060 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6800 | 38.8424 | -120.812 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1802421 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223635534844 | 20230110 | 421 | 20230110 | 1556 | 1944950 | 695 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 4170 | 38.6161 | -120.7289 | Yes | Clear;32-90 F |  |  | 23-0012737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1802353 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20230110 | 421 | 20230111 | 1422 | 1941948 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 1153 | 453934 | 38.6779 | -120.8495 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801636 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20230110 | 421 | 20230110 | 1358 | 1941946 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 70971 | 38.6701 | -120.7775 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012039 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801821 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1130 | 20230110 | 421 | 20230110 | 1430 | 1941932 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 177219 | 38.9127 | -120.9157 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1801639 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4483 | 20230110 | 421 | 20230110 | 929 | 1941822 | 308 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 10780 | 38.9059 | -120.9756 | Yes | Clear;32-90 F |  |  | 23-0012117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801889 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 6265 | 20230110 | 421 | 20230112 | 1750 | 1941916 | 3689 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 47957 | 39.0442 | -120.9973 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0013434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802958 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20230110 | 422 | 20230110 | 1805 | 1942090 | 823 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 135376 | 39.2034 | -121.0788 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801645 | 0 | EPSS Ckt | N | 2023 | SENSITIVE GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7847 | 20230110 | 422 | 20230110 | 1456 | 1943827 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15216 | 39.1984 | -121.0934 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801836 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3689 | 20230110 | 422 | 20230110 | 1110 | 1941837 | 408 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2856 | 39.261 | -121.1929 | Yes | Clear;32-90 F |  |  | 23-0012243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802003 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2669 | 20230110 | 422 | 20230110 | 1035 | 1942010 | 373 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 5595 | 38.7475 | -120.7978 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801825 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 22945 | 20230110 | 422 | 20230111 | 2243 | 1941840 | 2541 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 49407 | 38.8094 | -120.9066 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0012041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801823 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11491 | 20230110 | 423 | 20230110 | 1325 | 1944054 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 47154 | 38.6367 | -120.7207 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0012091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801864 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20230110 | 423 | 20230110 | 1749 | 1942026 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 29294 | 39.0914 | -121.0565 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012101 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801874 | 1 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4113 | 20230110 | 423 | 20230111 | 1141 | 1941864 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 30048 | 38.9046 | -120.8663 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0012191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801954 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | RECLOSER | 8412 | 20230110 | 424 | 20230110 | 1848 | 1942035 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 201000 | 38.7272 | -120.7379 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 23-0011879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801646 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 32113 | 20230110 | 424 | 20230110 | 1122 | 1941876 | 418 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2926 | 39.0454 | -121.0511 | Yes | Clear;32-90 F |  |  | 23-0012268 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802025 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | SWITCH | 5851 | 20230110 | 424 | 20230112 | 1703 | 1948683 | 3639 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 469431 | 38.8399 | -120.8193 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1803231 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 30745 | 20230110 | 424 | 20230110 | 1755 | 1941886 | 811 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 45416 | 39.0433 | -120.9863 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0012833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1802415 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20230110 | 425 | 20230110 | 1111 | 1942162 | 406 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3495 | 1418970 | 38.6943 | -120.6784 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0011877 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801644 | 0 | EPSS Ckt | N | 2023 | BC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9979 | 20230110 | 426 | 20230110 | 1950 | 1942150 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 16632 | 38.683 | -120.6626 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012106 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801880 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 6873 | 20230110 | 426 | 20230110 | 1049 | 1941941 | 383 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 9192 | 39.0673 | -121.0343 | Yes | Clear;32-90 F |  |  | 23-0012233 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801996 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1511 | 20230110 | 427 | 20230110 | 1017 | 1941962 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 41300 | 38.7377 | -120.7124 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0012133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801903 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2591 | 20230110 | 427 | 20230111 | 1955 | 1941993 | 2368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 85866 | 38.6596 | -120.7811 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 23-0012013 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801793 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 8637 | 20230110 | 428 | 20230111 | 1544 | 1941648 | 2116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 97336 | 38.9053 | -121.0693 | Yes | Strong Winds-Heavy Rain; | Conductor- Overhead | Broken- wire on ground | 23-0012321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802069 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12615 | 20230110 | 429 | 20230111 | 1459 | 1942055 | 2070 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 110022 | 38.7994 | -120.7287 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802052 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 8463 | 20230110 | 429 | 20230113 | 1115 | 1942065 | 4726 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 56562 | 39.0463 | -120.9816 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0012943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802507 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12623 | 20230110 | 430 | 20230110 | 920 | 1942141 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 6090 | 38.7856 | -120.6992 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801869 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230110 | 430 | 20230110 | 1844 | 1942234 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15242 | 39.2788 | -120.9795 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012259 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802016 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 30845 | 20230110 | 433 | 20230110 | 2025 | 1942182 | 952 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 18088 | 39.0929 | -120.9445 | Yes | Clear;32-90 F |  |  | 23-0012984 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802545 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | TRANSFORMER | 223296637659 | 20230110 | 434 | 20230110 | 2043 | 1942216 | 969 | Transformer only | Vegetation | Tree - fell into line | 6 | 5814 | 38.6947 | -120.8458 | Yes | Strong Winds-Heavy Rain; | Conductor- Overhead | Broken- wire on ground | 23-0012494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802193 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 21415 | 20230110 | 434 | 20230110 | 1125 | 1942201 | 411 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 7809 | 38.7136 | -120.632 | Yes | Clear;32-90 F |  |  | 23-0012271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802029 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30899 | 20230110 | 435 | 20230110 | 1937 | 1942209 | 902 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 23452 | 39.0205 | -120.8136 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0012952 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802519 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 30145 | 20230110 | 438 | 20230111 | 1004 | 1942356 | 1766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 15894 | 39.1623 | -120.8618 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803003 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230110 | 440 | 20230110 | 1438 | 1942331 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 1874 | 359957 | 39.0997 | -121.05 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0011891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801659 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20419 | 20230110 | 441 | 20230111 | 1233 | 1942329 | 1912 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5736 | 38.6769 | -120.7481 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0012212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801973 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6355 | 20230110 | 445 | 20230110 | 1836 | 1944129 | 831 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 12465 | 39.1446 | -120.907 | Yes | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0012711 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802346 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223453239078 | 20230110 | 446 | 20230110 | 1842 | 1942375 | 836 | Transformer only | Vegetation | Tree - fell into line | 3 | 2508 | 38.7332 | -120.7904 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0012930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802496 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 31377 | 20230110 | 510 | 20230110 | 1212 | 1941723 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 16036 | 39.0323 | -121.0725 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012002 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801778 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | OTHER | WIRE DOWN LD SIDE 583890 TWD 223579337115 | 20230110 | 513 | 20230111 | 1536 | 1942622 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3024 | 38.6782 | -120.7459 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012871 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | No | 1802447 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20230110 | 518 | 20230110 | 1503 | 1942642 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10530 | 38.6321 | -120.9241 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012045 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801828 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20685 | 20230110 | 619 | 20230111 | 1358 | 1942987 | 1899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 15192 | 38.6587 | -120.756 | Yes | Strong Winds-Heavy Rain | Pole-Wood | Broken | 23-0012295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802050 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11707 | 20230110 | 659 | 20230110 | 1303 | 1941600 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7644 | 38.6924 | -120.9238 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011997 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801773 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222855258578 | 20230110 | 800 | 20230110 | 1218 | 1943465 | 258 | Transformer only | Vegetation | Tree - fell into line | 4 | 1032 | 39.2709 | -120.9922 | Yes | Strong Winds-Heavy Rain; | Conductor- Overhead | Together | 23-0012382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802111 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20367 | 20230110 | 808 | 20230110 | 1304 | 1943457 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2368 | 38.6948 | -120.7775 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0012017 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801798 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | RECLOSER | 50020 | 20230110 | 906 | 20230110 | 2036 | 1941494 | 690 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 90920 | 38.7361 | -121.171 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0012089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801862 | 0 | Non-EPSS | N | 2023 | N/A
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18873 | 20230110 | 959 | 20230110 | 1020 | 1944458 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 357 | 38.8161 | -120.9016 | Yes | Clear;32-90 F |  |  | 23-0012189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801952 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 7583 | 20230110 | 1003 | 20230111 | 1558 | 1944365 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5852 | 39.0876 | -121.0462 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802368 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY 1101 | 152101101 | FUSE | 7935 | 20230110 | 1018 | 20230113 | 1250 | 1946473 | 4472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 165464 | 39.6302 | -120.5447 | Yes | Overcast-Fog-Snow;Below 32 F | Insulator | Broken | 23-0012987 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802548 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 30755 | 20230110 | 1020 | 20230110 | 1347 | 1944453 | 207 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 207 | 38.9338 | -121.0984 | Yes | Strong Winds-Heavy Rain; | Fuse | Burned Open | 23-0012501 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802200 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | SWITCH | 1525 | 20230110 | 1027 | 20230110 | 1257 | 1944526 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3000 | 38.7435 | -120.6471 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801983 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1055 | 20230110 | 1111 | 20230111 | 1458 | 1945160 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 61679 | 38.652 | -120.6282 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802328 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222546552595 | 20230110 | 1115 | 20230111 | 1203 | 1944756 | 1488 | Transformer only | Vegetation | Tree - fell into line | 1 | 1488 | 39.1074 | -121.1037 | Yes | Rain;32-90 F | Service conductor | Broken | 23-0012748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802361 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12319 | 20230110 | 1143 | 20230110 | 1705 | 1944871 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5152 | 38.6221 | -120.7394 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012860 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802440 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | JUMPER | OJ @ SAPID# 100019109 | 20230110 | 1204 | 20230110 | 1646 | 1944953 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 564 | 39.0547 | -121.0486 | Yes | Strong Winds-Heavy Rain; | Conductor- Overhead | Normal | 23-0012435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1802153 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | 222599746384 | 20230110 | 1313 | 20230111 | 1932 | 1948786 | 1819 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5024 | 38.9367 | -121.0873 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013895 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1803257 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222762852509 | 20230110 | 1343 | 20230111 | 939 | 1945308 | 1196 | Transformer only | Vegetation | Tree - fell into line | 1 | 1196 | 39.1047 | -121.0279 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0012883 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802455 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223461236865 | 20230110 | 1444 | 20230111 | 1559 | 1945549 | 1515 | Transformer only | Vegetation | Tree - fell into line | 1 | 1515 | 38.6721 | -120.7883 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802357 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32689 | 20230110 | 1445 | 20230110 | 1509 | 1945659 | 24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 48 | 39.2227 | -121.0733 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012635 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802298 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | JUMPER | OJ 1 SPAN SS OF CGC #222621839042 | 20230110 | 1451 | 20230110 | 1705 | 1945575 | 134 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1206 | 38.7347 | -121.0821 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0012624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1802291 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221868748549 | 20230110 | 1511 | 20230113 | 1327 | 1945686 | 4216 | Transformer only | Vegetation | Tree - fell into line | 2 | 8432 | 38.9988 | -121.3434 | Yes | Overcast;32-90 F | Transformer | On Ground | 23-0012953 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802520 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 37461 | 20230110 | 1651 | 20230112 | 1943 | 1945475 | 3052 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12196 | 38.9519 | -121.2514 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012859 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802439 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223739734326 | 20230110 | 1652 | 20230110 | 1803 | 1945993 | 71 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 71 | 38.6015 | -120.6956 | Yes | Clear;32-90 F | Secondary | Normal | 23-0012819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1802405 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223571540510 | 20230110 | 1702 | 20230111 | 849 | 1946033 | 947 | Transformer only | 3rd Party | Other | 1 | 947 | 38.7729 | -120.7475 | Yes | Clear;32-90 F | Customer Equipment | Normal | 23-0013400 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802935 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 210168 | 20230110 | 1708 | 20230110 | 1716 | 1941582 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 872 | 38.8867 | -121.2371 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1802418 | 0 | EPSS Ckt | N | 2023 | A & B
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 6413 | 20230110 | 1924 | 20230111 | 955 | 1946380 | 871 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 51389 | 38.7102 | -120.7152 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802963 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1102 | 152151102 | FUSE | 38311 | 20230110 | 2014 | 20230111 | 1138 | 1946465 | 924 | Distribution Circuit | Animal | Bird found | 20 | 18480 | 38.897 | -121.433 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013569 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803041 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5321 | 20230110 | 2019 | 20230111 | 1135 | 1946475 | 916 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 16488 | 38.9425 | -121.1922 | Yes | Clear;32-90 F |  |  | 23-0013449 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802966 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 3735 | 20230110 | 2021 | 20230112 | 1131 | 1946474 | 2350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 10531 | 38.9372 | -121.1756 | Yes | Clear;32-90 F |  |  | 23-0013474 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1802984 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5993 | 20230110 | 2123 | 20230112 | 1830 | 1946547 | 2707 | Distribution Circuit | Environmental/External | Lightning | 26 | 22557 | 38.9242 | -121.1435 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Burned/flashed | 23-0013478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802987 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | OTHER | WIRE DOWN HWY 20 E/OF BOWMAN RD | 20230111 | 16 | 20230112 | 1229 | 1946783 | 2140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 137584 | 39.3051 | -120.6685 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013272 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802826 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7799 | 20230111 | 533 | 20230111 | 941 | 1946984 | 248 | Distribution Circuit | Animal | Bird found | 6 | 1488 | 38.9412 | -121.2288 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013448 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802965 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222370346565 | 20230111 | 645 | 20230112 | 1405 | 1947039 | 1880 | Transformer only | Environmental/External | Lightning | 3 | 5640 | 38.9425 | -121.1678 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802975 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20357 | 20230111 | 845 | 20230111 | 927 | 1947391 | 42 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 210 | 38.6784 | -120.7671 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013454 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802969 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | JUMPER | OJ 1 SS OF CGC #223669038180 | 20230111 | 858 | 20230111 | 1025 | 1947253 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 174 | 38.7085 | -120.7154 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0013415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1802943 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 30099 | 20230111 | 1007 | 20230111 | 1701 | 1948636 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2898 | 38.7668 | -121.1933 | No | Clear;32-90 F | Insulator | Broken | 23-0013854 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1803224 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | JUMPER | 2557 SS JUMPERS | 20230111 | 1021 | 20230111 | 1500 | 1946696 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 279 | 38.8015 | -120.1164 | No | Clear;32-90 F | Jumper | Burned/flashed | 23-0013485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1802991 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | WIRE DOWN | 20230111 | 1155 | 20230112 | 1915 | 1947857 | 1880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7481 | 39.0014 | -121.0552 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0013602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1803066 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 740738 | 20230111 | 1244 | 20230111 | 1300 | 1947985 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 214 | 3424 | 38.7139 | -120.6222 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1803095 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 10425 | 20230111 | 1405 | 20230111 | 1416 | 1948241 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 60 | 660 | 38.7047 | -120.7089 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0011879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1803152 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK 1102 | 152291102 | FUSE | 6705 | 20230111 | 1454 | 20230111 | 1558 | 1948579 | 64 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 1152 | 39.3083 | -120.5401 | No | Clear;32-90 F |  |  | 23-0013836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803214 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 8279 | 20230111 | 1524 | 20230111 | 1546 | 1948262 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 352 | 38.9396 | -121.1724 | No | Clear;32-90 F | Fuse | Normal | 23-0013811 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1803199 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 51742 | 20230111 | 1928 | 20230112 | 1414 | 1948991 | 1126 | Distribution Circuit | Equipment Failure/Involved | Underground | 119 | 32861 | 38.7292 | -121.082 | No | Overcast-Rain;32-90 F | Elbow | Failed/Faulted | 23-0013968 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1803319 | 0 | EPSS Ckt | N | 2023 | A AND GRD
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222653852676 | 20230111 | 2100 | 20230112 | 1126 | 1949100 | 866 | Transformer only | Vegetation | Tree - fell into line | 2 | 1732 | 39.1093 | -121.0662 | No | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0014271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1803613 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 34407 | 20230111 | 2313 | 20230112 | 1711 | 1949159 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12936 | 39.3251 | -120.372 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014469 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1803752 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20230112 | 11 | 20230113 | 1528 | 1949213 | 2338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 161778 | 39.6081 | -120.6068 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1803565 | 0 | EPSS Ckt | N | 2023 | SENSITIVE GRD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7965 | 20230112 | 12 | 20230113 | 1528 | 1949920 | 2356 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 7068 | 39.6516 | -120.6276 | No | Clear;32-90F |  |  | 23-0014412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1803713 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224409760555 | 20230112 | 505 | 20230112 | 921 | 1949337 | 256 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 1792 | 39.3187 | -120.4424 | No | Clear;32-90F |  |  | 23-0014322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1803647 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | FUSE | 9661 | 20230112 | 734 | 20230112 | 942 | 1949453 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 9856 | 38.7277 | -121.2258 | No | Clear;32-90F |  |  | 23-0014351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803666 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8003 | 20230112 | 738 | 20230113 | 1251 | 1949457 | 1753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3506 | 39.4456 | -120.8237 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804183 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 20230112 | 1133 | 20230112 | 1458 | 1949971 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 205 | 39.322 | -120.8533 | No | Clear;32-90F |  |  | 23-0014631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803810 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR 2106 | 152582106 | RECLOSER | 1686 | 20230112 | 1245 | 20230112 | 2343 | 1950142 | 658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1798 | 161160 | 38.8055 | -121.2049 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 23-0014613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1803804 | 0 | EPSS Ckt | N | 2023 | B- C GRD
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 13795 | 20230112 | 1544 | 20230112 | 2047 | 1950537 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 30300 | 38.7622 | -120.8606 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0014680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1803840 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222353846403 | 20230112 | 1840 | 20230113 | 1056 | 1950838 | 976 | Transformer only | Environmental/External | Lightning | 1 | 976 | 38.9379 | -121.1739 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0014863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1803977 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223579438313 | 20230112 | 2121 | 20230113 | 1456 | 1951009 | 1055 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2110 | 38.7125 | -120.7468 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0014945 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804057 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6919 | 20230113 | 918 | 20230114 | 955 | 1952505 | 1477 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 51695 | 38.8593 | -120.833 | No | Clear;32-90F | Insulator | Broken | 23-0015539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1804385 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 3141 | 20230113 | 1105 | 20230113 | 1322 | 1951741 | 137 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 274 | 38.8072 | -120.7003 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0015229 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1804235 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38015 | 20230113 | 1109 | 20230113 | 1141 | 1951747 | 32 | Distribution Circuit | Animal | Bird found | 5 | 160 | 38.8252 | -121.1589 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804261 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222695647578 | 20230113 | 1116 | 20230113 | 1714 | 1952046 | 358 | Transformer only | Environmental/External | Lightning | 1 | 358 | 38.9691 | -121.053 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0015419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804310 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222693347508 | 20230113 | 1116 | 20230113 | 1437 | 1952044 | 201 | Transformer only | Environmental/External | Lightning | 2 | 402 | 38.9672 | -121.0538 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0015430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804316 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222693047530 | 20230113 | 1116 | 20230113 | 1455 | 1952045 | 219 | Transformer only | Environmental/External | Lightning | 3 | 657 | 38.9678 | -121.0539 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0015437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804319 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223006033780 | 20230113 | 1133 | 20230113 | 1602 | 1951803 | 269 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 269 | 38.5891 | -120.9494 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0015335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804273 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7877 | 20230113 | 1211 | 20230113 | 1346 | 1951867 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 570 | 38.8967 | -121.4786 | No | Clear;32-90F |  |  | 23-0015295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804262 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 8349 | 20230113 | 1244 | 20230113 | 1435 | 1951913 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 7548 | 38.885 | -121.2977 | No | Clear;32-90F | Insulator | Broken | 23-0015332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1804272 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222382145767 | 20230113 | 1402 | 20230113 | 1549 | 1952067 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 107 | 38.9206 | -121.1618 | No | Clear;32-90F | Fuse | Arcing | 23-0015472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804340 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222693347508 | 20230113 | 1503 | 20230113 | 1911 | 1952147 | 248 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 496 | 38.9672 | -121.0538 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0015460 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804333 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5365 | 20230113 | 2132 | 20230114 | 1441 | 1952604 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 44910 | 38.8911 | -121.1255 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1804785 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31895 | 20230114 | 541 | 20230114 | 1020 | 1953606 | 279 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 558 | 39.3159 | -120.8962 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804848 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230114 | 717 | 20230114 | 931 | 1952977 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1876 | 38.7941 | -120.8199 | Yes | Clear;32-90F |  |  | 23-0015997 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804816 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2117 | 20230114 | 730 | 20230114 | 846 | 1953020 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 259 | 19684 | 38.6926 | -120.7923 | Yes | Clear;32-90F |  |  | 23-0015920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804754 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 6705 | 20230114 | 846 | 20230114 | 1340 | 1953405 | 294 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 5292 | 39.3083 | -120.5401 | Yes | Rain; |  |  | 23-0016216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804981 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32365 | 20230114 | 854 | 20230114 | 1149 | 1953462 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 350 | 38.8411 | -120.8152 | Yes | Rain; |  |  | 23-0016122 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804912 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20230114 | 911 | 20230118 | 1652 | 1953562 | 3379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 184 | 277448 | 39.3251 | -120.6429 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1804804 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 9225 | 20230114 | 911 | 20230114 | 2008 | 1954661 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 9412 | 39.3227 | -120.6364 | Yes | Rain;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0015978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805045 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 6703 | 20230114 | 911 | 20230115 | 1841 | 1954838 | 2010 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 22110 | 39.3202 | -120.6232 | Yes | Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1805091 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 5999 | 20230114 | 911 | 20230116 | 1508 | 1953522 | 3237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 16185 | 39.316 | -120.6138 | Yes | Snow; | Conductor- Overhead | Broken- wire on ground | 23-0016780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1805477 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 6707 | 20230114 | 911 | 20230118 | 1652 | 1959544 | 6221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 111978 | 39.3243 | -120.5629 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0017619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1806198 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222384540970 | 20230114 | 931 | 20230114 | 1600 | 1953667 | 389 | Transformer only | Environmental/External | Lightning | 1 | 389 | 38.7883 | -121.1642 | Yes | Rain;32-90 F | Transformer | Leaking | 23-0016082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804884 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8495 | 20230114 | 937 | 20230114 | 1130 | 1953688 | 113 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 4633 | 38.8917 | -121.0145 | Yes | Rain; | Conductor- Overhead | Normal | 23-0016084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804885 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20230114 | 955 | 20230114 | 2102 | 1953769 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 24801 | 38.8964 | -121.1202 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1804842 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 210663 | 20230114 | 1001 | 20230114 | 1718 | 1954798 | 437 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 40204 | 38.7968 | -120.147 | Yes | Rain;32-90 F |  |  | 23-0016356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805111 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222468344118 | 20230114 | 1026 | 20230114 | 1552 | 1953988 | 326 | Transformer only | Environmental/External | Lightning | 7 | 2282 | 38.8747 | -121.1339 | Yes | Rain;32-90 F | Transformer | Burned/flashed | 23-0016163 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1804943 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1102 | 153701102 | RECLOSER | 89506 | 20230114 | 1052 | 20230114 | 1704 | 1954036 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4836 | 38.8736 | -121.3236 | Yes | Rain; | Pole-Wood | Broken | 23-0016129 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1804918 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | PLACER | DRUM 1101 | 152321101 | RECLOSER | 1101/2 | 20230114 | 1059 | 20230115 | 1725 | 1954075 | 1483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 196080 | 39.2562 | -120.7669 | Yes | Rain; | Insulator | Broken | 23-0016116 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804908 | 0 | EPSS Ckt | N | 2023 | A+C
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8721 | 20230114 | 1106 | 20230114 | 1701 | 1954080 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13135 | 39.1301 | -121.0442 | Yes | Rain; | Conductor- Overhead | Normal | 23-0016199 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804970 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 20230114 | 1127 | 20230114 | 1240 | 1954141 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 39.322 | -120.8533 | Yes | Rain; |  |  | 23-0016195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804968 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20230114 | 1224 | 20230114 | 1656 | 1954297 | 272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4352 | 38.8734 | -121.238 | Yes | Rain;32-90 F |  |  | 23-0016307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805064 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | TRANSFORMER | 223001736278 | 20230114 | 1327 | 20230114 | 1452 | 1954425 | 85 | Transformer only | Vegetation | Tree - fell into line | 3 | 255 | 38.658 | -120.9498 | Yes | Rain;32-90 F | Transformer | Broken | 23-0016269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805028 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S 1 SPAN E/OF CGC 224073139176 | 20230114 | 1331 | 20230118 | 810 | 1959597 | 5439 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 21756 | 38.7323 | -120.5719 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017635 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1806204 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ @ CGC 224108539415 | 20230114 | 1331 | 20230118 | 808 | 1960106 | 5437 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 9 | 48933 | 38.7401 | -120.5608 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0017846 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806271 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2547 | 20230114 | 1331 | 20230118 | 1806 | 1959609 | 6035 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42245 | 38.8068 | -120.1372 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017648 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1806209 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 2500 | 20230114 | 1331 | 20230118 | 1825 | 1954448 | 5957 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4094 | 9631789 | 38.8234 | -120.0307 | Yes | Rain; | Conductor- Overhead | Broken- wire on ground | 23-0016229 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1804992 | 0 | EPSS Ckt | N | 2023 | A+GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223239236540 | 20230114 | 1335 | 20230115 | 1205 | 1954472 | 1350 | Transformer only | Animal | Squirrel | 1 | 1350 | 38.6643 | -120.8666 | Yes | Snow; | Fuse | Normal | 23-0016664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805399 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 20230114 | 1428 | 20230114 | 1517 | 1954304 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 1078 | 38.7956 | -120.8033 | Yes | Rain;32-90 F | Conductor- Overhead | Normal | 23-0016284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805040 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20711 | 20230114 | 1437 | 20230114 | 1942 | 1954595 | 305 | Distribution Circuit | Environmental/External | Lightning | 24 | 4560 | 38.6169 | -120.9542 | Yes | Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0016355 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805110 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18285 | 20230114 | 1438 | 20230114 | 1911 | 1954591 | 273 | Distribution Circuit | Environmental/External | Lightning | 66 | 7458 | 38.6388 | -120.9443 | Yes | Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0016326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805083 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5633 | 20230114 | 1453 | 20230114 | 1538 | 1954614 | 45 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 21 | 930 | 38.9612 | -121.0828 | Yes | Rain;32-90 F |  |  | 23-0016294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805049 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1443 | 20230114 | 1501 | 20230114 | 1840 | 1954633 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 19929 | 38.7978 | -120.8203 | Yes | Rain;32-90 F |  |  | 23-0016371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805125 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223154236630 | 20230114 | 1503 | 20230115 | 924 | 1954795 | 1101 | Transformer only | Environmental/External | Lightning | 2 | 2202 | 38.667 | -120.8962 | Yes | Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0016353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805109 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 222900033684 | 20230114 | 1503 | 20230115 | 1140 | 1954674 | 1237 | Transformer only | Environmental/External | Lightning | 1 | 1237 | 38.5869 | -120.987 | Yes | Snow;32-90 F | Transformer | Failed/Faulted | 23-0016598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805344 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 7991 | 20230114 | 1504 | 20230114 | 1929 | 1954640 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 27560 | 38.6679 | -120.894 | Yes | Rain;32-90 F |  |  | 23-0016347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1805103 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222911033645 | 20230114 | 1518 | 20230115 | 1022 | 1954664 | 1144 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 5720 | 38.5857 | -120.9831 | Yes | Snow;32-90 F | Transformer | Failed/Faulted | 23-0016583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805330 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 18599 | 20230114 | 1530 | 20230115 | 943 | 1954678 | 1093 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 4323 | 38.7095 | -120.8281 | Yes | Rain;32-90 F |  |  | 23-0016376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805127 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9533 | 20230114 | 1558 | 20230115 | 857 | 1954717 | 1019 | Distribution Circuit | Animal | Bird found | 10 | 3830 | 38.8679 | -121.4506 | Yes | Rain;32-90 F | Fuse | Failed/Faulted | 23-0016385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1805136 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | OTHER | WIRE DOWN SAP ID 100093792 | 20230114 | 1611 | 20230118 | 1630 | 1954744 | 5779 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 443251 | 39.632 | -120.5654 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805245 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | SWITCH | 5893 | 20230114 | 1639 | 20230115 | 1305 | 1954818 | 1226 | Distribution Circuit | 3rd Party | Other | 90 | 109980 | 38.8974 | -121.1804 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0016318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805085 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 4259 | 20230114 | 1839 | 20230117 | 1747 | 1956253 | 4268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 183524 | 39.3059 | -120.5204 | Yes | Snow; | Conductor- Overhead | Broken- wire on ground | 23-0016761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1805462 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 222979734820 | 20230114 | 1852 | 20230115 | 1347 | 1955073 | 1135 | Distribution Circuit | Environmental/External | Lightning | 2 | 1373 | 38.6178 | -120.9581 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805215 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223320540745 | 20230114 | 1922 | 20230115 | 1353 | 1955111 | 1111 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3333 | 38.7782 | -120.8354 | Yes | Snow;32-90 F | Transformer | Failed/Faulted | 23-0016631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805370 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2105 | 153612105 | OCB | 2105/2 | 20230114 | 1944 | 20230115 | 1352 | 1955137 | 1088 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4771 | 595022 | 38.6555 | -121.0603 | Yes | Rain;32-90 F | Crossarm- Wood | Burned/flashed | 23-0016391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805142 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | SWITCH | 945 | 20230114 | 1958 | 20230115 | 121 | 1955149 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 72352 | 39.22 | -121.1989 | Yes | Rain;32-90 F | Conductor- Overhead | Normal | 23-0016396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805146 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20230115 | 610 | 20230116 | 1413 | 1955516 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 234606 | 39.6081 | -120.6068 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0016529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805286 | 0 | EPSS Ckt | N | 2023 | B+GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | T9202 | 20230115 | 853 | 20230115 | 1103 | 1955637 | 130 | Transformer only | Unknown Cause | Patrol - not conducted | 19 | 2470 | 38.6758 | -120.8247 | No | Snow;32-90 F |  |  | 23-0016578 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1805325 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK SUB | 15229 | OTHER | TAMARACK | 20230115 | 901 | 20230115 | 911 | 1955558 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 556 | 5560 | 0 | 0 | No | Snow; |  |  | 23-0016587 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1805334 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 9817 | 20230115 | 1002 | 20230115 | 1227 | 1955778 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3770 | 39.223 | -121.091 | No | Snow; | Conductor- Overhead | Arcing | 23-0016610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805356 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK 1102 | 152481102 | FUSE | 3891 | 20230115 | 1051 | 20230115 | 1216 | 1955820 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2635 | 39.2197 | -120.9493 | No | Snow; |  |  | 23-0016665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805400 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223349938289 | 20230115 | 1113 | 20230115 | 1253 | 1955853 | 100 | Transformer only | Environmental/External | Lightning | 3 | 300 | 38.7122 | -120.827 | No | Snow; | Transformer (OH) | Failed/Faulted | 23-0016676 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805409 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 20230115 | 1218 | 20230115 | 1649 | 1955907 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 271 | 39.322 | -120.8533 | No | Snow; | Conductor- Overhead | Broken | 23-0016712 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805429 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5229 | 20230115 | 1241 | 20230115 | 1314 | 1955932 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 1320 | 38.913 | -121.2561 | No | Snow; | Service conductor | Normal | 23-0016673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805406 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21041 | 20230115 | 1255 | 20230116 | 2041 | 1955952 | 1906 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2061 | 38.63 | -120.9097 | No | Snow; | Transformer (OH) | Burned/flashed | 23-0016752 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805454 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 20230115 | 1259 | 20230118 | 1701 | 1955966 | 1567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1000 | 319094 | 39.4655 | -120.8444 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0016684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805412 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | NARROWS-2105 | 153132105 | SWITCH | 945 | 20230115 | 1352 | 20230115 | 1822 | 1956021 | 270 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 60480 | 39.22 | -121.1989 | No | Snow; | Conductor- Overhead | Normal | 23-0016695 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1805419 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20230115 | 1706 | 20230116 | 1448 | 1956228 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 116141 | 39.0014 | -121.0224 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0016756 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1805457 | 0 | EPSS Ckt | N | 2023 | A C GRD
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20230116 | 515 | 20230117 | 2121 | 1957999 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 1659 | 3526892 | 38.7934 | -120.6201 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017173 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805860 | 0 | EPSS Ckt | N | 2023 | A B C PH TIME OC
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7965 | 20230116 | 515 | 20230117 | 1725 | 1958778 | 2170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 60760 | 38.7533 | -120.6117 | Yes | Clear;32-90 F |  |  | 23-0017366 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806038 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 18423 | 20230116 | 515 | 20230117 | 2121 | 1960081 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 31278 | 38.7599 | -120.5815 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1806268 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20230116 | 616 | 20230116 | 1630 | 1956938 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 461 | 280272 | 38.6217 | -120.5868 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0016953 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805658 | 0 | EPSS Ckt | N | 2023 | A & B
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230116 | 830 | 20230116 | 1647 | 1957181 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 16673 | 38.8458 | -121.482 | Yes | Clear;32-90F | Other | Broken | 23-0017060 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805758 | 1 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20859 | 20230116 | 846 | 20230116 | 1534 | 1957374 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2040 | 38.765 | -120.7039 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0017147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805835 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20230116 | 918 | 20230117 | 1115 | 1957471 | 1557 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 16219 | 38.6945 | -120.6389 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0017322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805999 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 21211 | 20230116 | 940 | 20230117 | 1910 | 1960215 | 2010 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 10050 | 38.7645 | -120.5769 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0017874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806288 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221488041119 | 20230116 | 1000 | 20230116 | 1703 | 1957564 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 423 | 38.7943 | -121.4791 | Yes | Clear;32-90F | Service conductor | Broken | 23-0017176 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805864 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 11269 | 20230116 | 1016 | 20230118 | 1220 | 1960042 | 3004 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 129172 | 38.7607 | -120.574 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0017819 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806263 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRIP-SAVER | 6645 | 20230116 | 1017 | 20230117 | 1916 | 1958466 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 229564 | 38.7649 | -120.5894 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017173 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1805969 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18525 | 20230116 | 1026 | 20230116 | 1555 | 1957654 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1645 | 38.7541 | -120.6882 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017289 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805973 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7919 | 20230116 | 1042 | 20230117 | 1448 | 1959749 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 107904 | 38.7507 | -120.632 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017730 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806232 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 20230116 | 1057 | 20230116 | 2114 | 1957727 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 11723 | 38.7136 | -120.632 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0017271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805948 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 6705 | 20230116 | 1059 | 20230118 | 1207 | 1958073 | 2948 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 53064 | 39.3083 | -120.5401 | Yes | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0017190 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805873 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | RECLOSER | 927014 | 20230116 | 1122 | 20230118 | 1150 | 1960372 | 2908 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 895664 | 38.7532 | -120.5963 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0017173 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806326 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | TAMARACK-1102 | 152291102 | RECLOSER | 482896 | 20230116 | 1143 | 20230118 | 1207 | 1957755 | 2810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 135388 | 39.3139 | -120.4991 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0017160 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805848 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 20230116 | 1211 | 20230116 | 1403 | 1957998 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 896 | 38.9409 | -120.7298 | Yes | Clear;32-90F |  |  | 23-0017247 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805921 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 2051 | 20230116 | 1212 | 20230117 | 1640 | 1958425 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 72044 | 38.7456 | -120.6289 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0017279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805958 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230116 | 1218 | 20230117 | 1348 | 1958034 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 451944 | 38.7391 | -120.6681 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805866 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 20141 | 20230116 | 1220 | 20230118 | 1649 | 1960325 | 3149 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 91321 | 38.7601 | -120.5895 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1806306 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 12039 | 20230116 | 1236 | 20230118 | 1330 | 1959362 | 2871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 29670 | 38.759 | -120.5766 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0017552 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806171 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 20230116 | 1317 | 20230117 | 1112 | 1958141 | 1315 | Distribution Circuit | Environmental/External | Ice or snow | 59 | 77585 | 38.6204 | -120.6018 | Yes | Clear;32-90 F | Insulator | Broken | 23-0017358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806028 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 236062 | 20230116 | 1422 | 20230117 | 1624 | s1805963 | 1562 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 404558 | 38.7471 | -120.6442 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1805963 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20535 | 20230116 | 1431 | 20230117 | 1551 | 1958330 | 1520 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 83600 | 38.7338 | -120.6035 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017758 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806241 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224168335578 | 20230116 | 1711 | 20230117 | 1335 | 1958619 | 1224 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3672 | 38.6347 | -120.5411 | Yes | Clear;32-90 F | Transformer | Broken | 23-0017532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806162 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223495039480 | 20230117 | 718 | 20230117 | 1002 | 1959130 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 38.7433 | -120.7749 | No | Clear;32-90 F | Transformer (OH) |  | 23-0017557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806175 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | SWITCH | 239390 | 20230117 | 738 | 20230117 | 829 | 1959157 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1128 | 57528 | 38.7281 | -120.796 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0017478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806137 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7737 | 20230117 | 847 | 20230117 | 1107 | 1959268 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2660 | 38.9993 | -121.2622 | No | Clear;32-90 F |  |  | 23-0017601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806192 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | OCB | 1101/2 | 20230117 | 959 | 20230117 | 1352 | 1959256 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1370 | 45810 | 38.7444 | -121.1608 | No | Clear;32-90 F | Cutout- fuse holder | Arcing | 23-0017553 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806173 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK 1104 | 152481104 | FUSE | 69925 | 20230117 | 1246 | 20230117 | 1533 | 1959670 | 167 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5010 | 39.2629 | -121.0409 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017711 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806225 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | WIRE DOWN | 20230117 | 1324 | 20230117 | 1913 | 1959691 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 22619 | 38.7406 | -120.6558 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | No | 1806230 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223997338201 | 20230117 | 1520 | 20230117 | 1822 | 1959930 | 182 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 364 | 38.707 | -120.6003 | No | Clear;32-90 F | Transformer | Normal | 23-0017880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806292 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22119 | 20230117 | 1620 | 20230117 | 2136 | 1959973 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1896 | 38.7524 | -120.6108 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806270 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 67415 | 20230117 | 1630 | 20230117 | 1934 | 1960109 | 184 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2760 | 38.883 | -120.8795 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0017847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806272 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223946839928 | 20230117 | 1909 | 20230118 | 1155 | 1960469 | 1006 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4024 | 38.7547 | -120.6172 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0018217 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806547 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224068039843 | 20230117 | 1910 | 20230118 | 923 | 1960289 | 853 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3412 | 38.7516 | -120.5739 | No | Clear;32-90F | Fuse | Normal | 23-0018163 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806524 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224046038677 | 20230117 | 1944 | 20230118 | 1714 | 1960779 | 1290 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 5160 | 38.7197 | -120.5828 | No | Clear;32-90 F | Transformer | Broken | 23-0018303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806560 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7917 | 20230118 | 235 | 20230118 | 909 | 1960508 | 394 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 788 | 38.8458 | -121.4767 | No | Clear;32-90F |  |  | 23-0018139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806509 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20230118 | 527 | 20230118 | 943 | 1960503 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 795 | 203520 | 38.8695 | -121.02 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0018073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806487 | 0 | EPSS Ckt | N | 2023 | NO TARGETS
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 18429 | 20230118 | 700 | 20230118 | 1456 | 1960574 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3332 | 38.7515 | -120.5988 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0018294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806559 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 586723 | 20230118 | 716 | 20230118 | 908 | 1960529 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1344 | 38.9143 | -121.2099 | No | Clear;32-90F |  |  | 23-0018137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806508 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 9221 | 20230118 | 736 | 20230118 | 936 | 1960541 | 120 | Distribution Circuit | 3rd Party | Other | 25 | 3042 | 39.3014 | -120.6601 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806533 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224080539390 | 20230118 | 849 | 20230118 | 954 | 1960618 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 260 | 38.7394 | -120.5705 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0018206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806544 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224061040040 | 20230118 | 923 | 20230118 | 1106 | 1960665 | 103 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 309 | 38.7571 | -120.5768 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806558 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221488041119 | 20230118 | 1020 | 20230118 | 1146 | 1960793 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 38.7943 | -121.4791 | No | Clear;32-90F |  |  | 23-0018313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806562 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7925 | 20230118 | 1200 | 20230118 | 1248 | 1960930 | 48 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 96 | 39.6217 | -120.6131 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806566 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222487642073 | 20230118 | 1215 | 20230118 | 1315 | 1960950 | 60 | Transformer only | Equipment Failure/Involved | Underground | 1 | 60 | 38.8184 | -121.1281 | No | Clear;32-90F | Secondary | Broken | 23-0018331 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806569 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 40885 | 20230118 | 1232 | 20230118 | 1441 | 1960982 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 196 | 39.314 | -120.6393 | No | Clear;32-90F | Lightning Arrestor | Failed/Faulted | 23-0018361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806578 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 31923 | 20230118 | 1441 | 20230118 | 1701 | 1961123 | 140 | Distribution Circuit | Environmental/External | Ice or snow | 27 | 3780 | 39.622 | -120.6131 | No | Clear;32-90F | Insulator | Broken | 23-0018484 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806607 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE 1111 | 153081111 | TRANSFORMER | 223338138607 | 20230118 | 1504 | 20230118 | 1554 | 1960965 | 50 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 50 | 38.7211 | -120.8308 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0018502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806611 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | SWITCH | 197930 | 20230118 | 1717 | 20230118 | 1728 | 1961318 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 888 | 9768 | 39.0441 | -121.0583 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0018560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806634 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | SWITCH | 197930 | 20230118 | 1736 | 20230118 | 1830 | 1961324 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 888 | 47952 | 39.0441 | -121.0583 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0018560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806636 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | OTHER | WIRE DOWN 1 E/O 3427 | 20230118 | 1817 | 20230120 | 2011 | 1961847 | 2994 | Distribution Circuit | Environmental/External | Ice or snow | 147 | 172197 | 39.3227 | -120.6128 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0018842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1806784 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 887684 | 20230118 | 1916 | 20230119 | 1435 | 1961438 | 1159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 704 | 533562 | 38.7891 | -120.1684 | No | Clear;Below 32 F | Crossarm- Wood | Broken | 23-0018575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806644 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7963 | 20230118 | 2242 | 20230119 | 843 | 1961708 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 7813 | 38.7532 | -120.6133 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018699 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806738 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11659 | 20230119 | 111 | 20230119 | 851 | 1961741 | 460 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 5520 | 38.5702 | -120.7324 | No | Clear;32-90F |  |  | 23-0018719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806744 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY 1102 | 152201102 | FUSE | 8803 | 20230119 | 426 | 20230120 | 1516 | 1962198 | 2090 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 53724 | 39.5069 | -120.9932 | No | Clear;Below 32 F | Insulator | Broken | 23-0018907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806798 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 3349 | 20230119 | 651 | 20230119 | 1055 | 1962056 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2196 | 38.7751 | -120.4256 | No | Clear;32-90F |  |  | 23-0018826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806780 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 9225 | 20230119 | 1130 | 20230120 | 2009 | 1962631 | 1959 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 35262 | 39.3227 | -120.6364 | No | Clear;32-90F | Insulator | Broken | 23-0019029 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1806840 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 6729 | 20230119 | 1246 | 20230120 | 2009 | 1962629 | 1883 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 11298 | 39.3209 | -120.6266 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1806839 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7549 | 20230119 | 1546 | 20230119 | 1552 | 1962617 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 3 | 18 | 38.7801 | -121.4233 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806836 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224095339882 | 20230119 | 2049 | 20230120 | 641 | 1962799 | 592 | Transformer only | Company Initiated | Return Circuit Normal | 2 | 1184 | 38.7526 | -120.5644 | No | Clear;32-90 F | Transformer | Normal | 23-0019182 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806954 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 2 SPANS SS OF CGC 223425541680 | 20230119 | 2250 | 20230120 | 1403 | 1962868 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2006 | 38.8055 | -120.7997 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019190 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1806962 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7929 | 20230119 | 2324 | 20230119 | 2354 | 1962827 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 60 | 38.8465 | -121.4097 | No | Clear;32-90F |  |  | 23-0019183 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806955 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | TRANSFORMER | T2346 | 20230120 | 1013 | 20230120 | 1103 | 1963134 | 50 | Transformer only | Company Initiated | Coordination failure | 13 | 650 | 38.8147 | -121.2955 | No | Clear;32-90 F | Transformer | Normal | 23-0019346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807039 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6629 | 20230120 | 1033 | 20230120 | 1322 | 1963164 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4225 | 39.3122 | -120.4181 | No | Clear;32-90F | Lightning Arrestor | Failed/Faulted | 23-0019335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807034 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7671 | 20230120 | 1400 | 20230120 | 1509 | 1963420 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 2071 | 38.8956 | -121.4145 | No | Clear;32-90 F |  |  | 23-0019568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807076 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | TRANSFORMER | 222600443564 | 20230120 | 1404 | 20230120 | 1431 | 1963381 | 27 | Transformer only | Vegetation | Tree - fell into line | 2 | 54 | 38.8592 | -121.0876 | No | Clear;32-90 F | Service conductor | Broken | 23-0019501 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807065 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 3039 | 20230120 | 1421 | 20230120 | 1923 | 1963409 | 302 | Distribution Circuit | Animal | Squirrel | 13 | 3926 | 39.0425 | -121.0961 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0019555 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807074 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SECTIONALIZER | 2628 | 20230120 | 1617 | 20230121 | 1703 | 1963640 | 1486 | Distribution Circuit | Environmental/External | Ice or snow | 29 | 43094 | 39.6105 | -120.606 | No | Clear;Below 32 F | Insulator | Broken | 23-0019506 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807095 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222775559328 | 20230121 | 741 | 20230121 | 1311 | 1963820 | 330 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 660 | 39.2916 | -121.0203 | No | Clear;32-90F |  |  | 23-0019688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807164 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223616039475 | 20230121 | 743 | 20230121 | 1436 | 1963823 | 413 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 413 | 38.7437 | -120.733 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019697 | OH | Sus | 35422565 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807177 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222927032660 | 20230121 | 912 | 20230121 | 1818 | 1963886 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 623 | 38.559 | -120.9773 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0019709 | OH | Sus | 35422567 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807188 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | TRANSFORMER | 222626343805 | 20230121 | 1118 | 20230121 | 1948 | 1963990 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 565 | 38.8658 | -121.079 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0019742 | OH | Sus | 35422568 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807213 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL 1101 | 152471101 | RECLOSER | 583518 | 20230121 | 1651 | 20230121 | 1657 | 1964239 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 37 | 222 | 39.3256 | -121.1123 | No | Clear;32-90F |  |  | 23-0019767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807230 | 0 | EPSS Ckt | N | 2023 | A+C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19552 | 20230121 | 1806 | 20230121 | 1920 | 1964278 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 787 | 52518 | 38.7436 | -120.7818 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0019778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1807236 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | DEL MAR-2109 | 152582109 | FUSE | 37433 | 20230122 | 747 | 20230122 | 813 | 1964480 | 26 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 234 | 38.849 | -121.2316 | No | Clear;32-90F |  |  | 23-0019826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807282 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 2679 | 20230122 | 1227 | 20230123 | 133 | 1964721 | 786 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 7860 | 38.9153 | -121.4513 | No | Clear;32-90F | Pole-Wood | On Ground | 23-0019894 | OH | Sus | 31635022 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1807330 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | FUSE | 32167 | 20230122 | 1246 | 20230122 | 1315 | 1964732 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 435 | 38.7869 | -121.2588 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019877 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807318 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230122 | 1410 | 20230122 | 1709 | 1964788 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 7518 | 38.8458 | -121.482 | No | Clear;32-90F |  |  | 23-0019918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807351 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38015 | 20230122 | 1424 | 20230122 | 1842 | 1964821 | 258 | Distribution Circuit | Animal | Bird found | 5 | 1290 | 38.8252 | -121.1589 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807368 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2704 | 20230122 | 1509 | 20230122 | 2128 | 1964879 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 26596 | 38.8107 | -121.1649 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0019901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807338 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 20230122 | 1517 | 20230122 | 1747 | 1964895 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3900 | 38.7681 | -120.951 | No | Clear;32-90F |  |  | 23-0019929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807363 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11439 | 20230122 | 2002 | 20230123 | 933 | 1965028 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 49471 | 38.7331 | -120.789 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019969 | OH | Sus | 31634964 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1807402 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 20230122 | 2346 | 20230123 | 1412 | 1965281 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19052 | 38.7956 | -120.8033 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1807434 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 24189 | 20230123 | 132 | 20230123 | 435 | 1965280 | 183 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 1647 | 38.8025 | -120.7947 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807435 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223265139007 | 20230123 | 215 | 20230123 | 1228 | 1965173 | 613 | Transformer only | Vegetation | Tree - fell into line | 1 | 613 | 38.7322 | -120.8566 | No | Clear;32-90 F | Transformer | Broken | 23-0019988 | OH | Sus | 35422623 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807421 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 20749 | 20230123 | 420 | 20230123 | 1247 | 1965269 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7192 | 38.832 | -120.8169 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0020090 | OH | Sus | 31635030 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807531 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13717 | 20230123 | 856 | 20230123 | 1252 | 1965513 | 236 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 67 | 15812 | 38.6007 | -120.7101 | No | Clear;32-90F |  |  | 23-0020271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807605 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 33485 | 20230123 | 934 | 20230123 | 1324 | 1965600 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 460 | 38.8658 | -121.0803 | No | Clear;32-90F | Pole-Wood | Broken | 23-0020095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807535 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | VR814 | 20230123 | 1313 | 20230123 | 1538 | 1965950 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 909 | 131805 | 39.5586 | -120.8318 | No | Clear-Strong Winds;Below 32 F | Recloser | Malfunctioning | 23-0020279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1807607 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222695857012 | 20230123 | 1410 | 20230123 | 1805 | 1965952 | 235 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 940 | 39.2282 | -121.0492 | No | Clear;32-90F |  |  | 23-0020335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807621 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223112036582 | 20230123 | 1554 | 20230124 | 1014 | 1966124 | 1100 | Transformer only | Vegetation | Tree - fell into line | 3 | 3300 | 38.6659 | -120.911 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0020434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1807639 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222065846414 | 20230123 | 1632 | 20230123 | 1719 | 1966118 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 47 | 38.9388 | -121.2748 | No | Clear;32-90F | Connector or Splice (OH) | Arcing | 23-0020446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807646 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51484 | 20230123 | 1816 | 20230123 | 1923 | 1966278 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 806 | 54002 | 39.1909 | -120.9998 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0020451 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1807649 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 637069 | 20230123 | 2155 | 20230123 | 2352 | 1966341 | 117 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 351 | 38.7111 | -120.5988 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807675 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | SWITCH | 321 | 20230124 | 951 | 20230124 | 1652 | 1966840 | 421 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 2338 | 38.8211 | -121.307 | No | Clear;32-90F | Pole-Wood | Broken | 23-0020535 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807831 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223024040860 | 20230124 | 957 | 20230124 | 1219 | 1966853 | 142 | Transformer only | 3rd Party | Dig in- 3rd party | 2 | 284 | 38.7836 | -120.9408 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0020723 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807859 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 4931 | 20230124 | 1021 | 20230124 | 1143 | 1966874 | 82 | Distribution Circuit | Animal | Squirrel | 2 | 164 | 38.8148 | -121.2079 | No | Clear;32-90F | Pothead(Riser Termination) | Normal | 23-0020728 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807864 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 100000045210 | 20230124 | 1219 | 20230124 | 1433 | 1967012 | 134 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 134 | 39.3212 | -120.4428 | No | Clear;32-90F | Fuse | Normal | 23-0020877 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807909 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2015 | 20230124 | 1423 | 20230124 | 1704 | 1967141 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2254 | 38.5962 | -120.619 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0020867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807907 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223666041091 | 20230124 | 1725 | 20230125 | 1720 | 1967344 | 1435 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2870 | 38.7874 | -120.7154 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807964 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223274339211 | 20230124 | 2026 | 20230125 | 1527 | 1967409 | 1141 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2282 | 38.7374 | -120.8533 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807947 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | JUMPER | OJ 2 SP SS OG CGC 222671446133 | 20230124 | 2112 | 20230125 | 0 | 1967429 | 168 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 7 | 1176 | 38.9296 | -121.0616 | No | Clear;32-90F | Secondary | Broken | 23-0020978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807959 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7929 | 20230125 | 1236 | 20230125 | 1300 | 1967896 | 24 | Distribution Circuit | Animal | Bird found | 2 | 48 | 38.8465 | -121.4097 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0021257 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808144 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13717 | 20230125 | 1335 | 20230125 | 2155 | 1968097 | 500 | Distribution Circuit | Animal | Squirrel | 67 | 17030 | 38.6007 | -120.7101 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0021427 | OH | Sus | 31635572 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808185 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 374539 | 20230125 | 1522 | 20230126 | 150 | 1968229 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 628 | 38.8159 | -120.9163 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0021442 | OH | Sus | 31635644 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1808192 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3629 | 20230125 | 1524 | 20230125 | 1549 | 1968181 | 25 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 225 | 39.2129 | -121.0061 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0021366 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1808170 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230126 | 127 | 20230126 | 1635 | 1968437 | 864 | Distribution Circuit | Environmental/External | Ice or snow | 202 | 137094 | 39.2562 | -120.7669 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0021521 | OH | Sus | 31635651 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1808259 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | RECLOSER | 542272 | 20230126 | 1345 | 20230126 | 1655 | 1969008 | 190 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 21731 | 38.7539 | -120.5747 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0021853 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1808460 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | SWITCH | 18582SW | 20230127 | 903 | 20230127 | 1251 | s1808637 | 228 | Distribution Circuit | Equipment Failure/Involved | Underground | 76 | 5616 | 38.6904 | -121.0758 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0022106 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1808637 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222722647585 | 20230127 | 1134 | 20230127 | 1140 | 1969610 | 6 | Transformer only | Animal | Squirrel | 1 | 6 | 38.9693 | -121.0434 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0022288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1808670 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 32015 | 20230127 | 1228 | 20230127 | 1502 | 1969885 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 6776 | 38.9774 | -120.8865 | No | Clear;32-90 F |  |  | 23-0022469 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808706 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | OJS 4 POLES N/OF CGC 222798748141 | 20230127 | 1229 | 20230127 | 1640 | 1969888 | 251 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 502 | 38.9854 | -121.0169 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0022385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1808688 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 4229 | 20230128 | 1326 | 20230128 | 1500 | 1970544 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 658 | 39.3282 | -120.4128 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0022641 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1808833 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5867 | 20230128 | 1643 | 20230128 | 1848 | 1970638 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 3625 | 38.8852 | -120.9599 | No | Clear;32-90 F |  |  | 23-0022669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808857 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 9401 | 20230129 | 755 | 20230129 | 850 | 1970817 | 55 | Distribution Circuit | Animal | Other | 5 | 275 | 38.9241 | -121.2089 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0022713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808911 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223491036946 | 20230129 | 1331 | 20230129 | 1708 | 1970981 | 217 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 434 | 38.6747 | -120.7787 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0022741 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1808939 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222710954922 | 20230129 | 1729 | 20230130 | 408 | 1971092 | 639 | Distribution Circuit | 3rd Party | Vehicle | 980 | 268060 | 39.1709 | -121.0448 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0022754 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1808952 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 9445 | 20230129 | 1812 | 20230129 | 1946 | 1971118 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 470 | 38.8979 | -121.2288 | No | Clear;32-90 F |  |  | 23-0022758 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808955 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5633 | 20230129 | 1822 | 20230130 | 17 | 1971122 | 355 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 7340 | 38.9612 | -121.0828 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0022765 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1808963 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | JUMPER | OJ CENTER PHASE | 20230129 | 2113 | 20230129 | 2257 | 1971255 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1278 | 63969 | 39.2557 | -121.0142 | No | Clear;32-90 F | Jumper | Burned Open | 23-0022785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1808986 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRIP-SAVER | 18935 | 20230130 | 701 | 20230130 | 830 | 1971362 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 7476 | 38.6729 | -120.8939 | No | Clear;32-90 F |  |  | 23-0022841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809085 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 7989 | 20230130 | 854 | 20230130 | 950 | 1971625 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 2968 | 38.6663 | -120.8941 | No | Clear;32-90 F |  |  | 23-0022873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809143 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 4163 | 20230130 | 921 | 20230130 | 1156 | 1971650 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 3720 | 38.8381 | -120.851 | No | Clear;32-90 F |  |  | 23-0022970 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809189 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY 1101 | 152031101 | SWITCH | 2079 | 20230130 | 1032 | 20230130 | 1705 | 1971794 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 332 | 130476 | 39.1124 | -121.0835 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0022725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1809171 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2101 | 153132101 | FUSE | 4261 | 20230130 | 1048 | 20230130 | 1212 | 1971825 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1848 | 39.1642 | -121.1509 | No | Clear;32-90 F |  |  | 23-0022985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809201 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2101 | 153132101 | TRANSFORMER | 222301456593 | 20230130 | 1154 | 20230130 | 1518 | 1971914 | 204 | Transformer only | 3rd Party | Other | 6 | 1224 | 39.2183 | -121.1889 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0023023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1809212 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | R5397 | 20230130 | 1503 | 20230131 | 421 | 1972108 | 798 | Distribution Circuit | 3rd Party | Vehicle | 16 | 12768 | 38.9268 | -121.1944 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0023162 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1809256 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223282049250 | 20230131 | 300 | 20230131 | 1045 | 1972342 | 465 | Transformer only | Vegetation | Tree - fell into line | 2 | 930 | 39.0129 | -120.8449 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0023230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1809300 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7737 | 20230131 | 647 | 20230131 | 842 | 1972376 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2185 | 38.9993 | -121.2622 | No | Clear;32-90 F |  |  | 23-0023300 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809357 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7721 | 20230131 | 1351 | 20230131 | 1605 | 1972992 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 447 | 39.0138 | -121.327 | No | Clear;32-90 F |  |  | 23-0023628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1809522 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 20230131 | 1414 | 20230201 | 227 | 1973026 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 19933 | 38.7911 | -120.7022 | No | Clear;32-90 F | Secondary | Broken | 23-0023633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1809523 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | OCB | 2107/2 | 20230131 | 1528 | 20230201 | 721 | 1973089 | 953 | Distribution Circuit | Equipment Failure/Involved | Underground | 2138 | 142474 | 38.8222 | -121.306 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0023603 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | No | No | 1809518 | 0 | Non-EPSS | N | 2023 | PH TIME BU PH/GRD INST/TIME
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2567 | 20230201 | 702 | 20230201 | 1245 | 1973246 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 44590 | 38.7942 | -120.145 | No | Clear;32-90F | Conductor- Overhead | Arcing | 23-0023904 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1809763 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5211 | 20230201 | 813 | 20230201 | 931 | 1973507 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 7098 | 38.8401 | -121.1386 | No | Clear;32-90F |  |  | 23-0023816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1809705 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 861610 | 20230201 | 1751 | 20230201 | 1828 | 1974305 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1130 | 41810 | 39.0467 | -121.0715 | No | Clear;32-90 F | PT/CCVT | Failed/Faulted | 23-0000737 | OH | Sus | 35304231 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1809827 | 0 | EPSS Ckt | N | 2023 | B GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | T84184 | 20230202 | 912 | 20230202 | 1103 | 1974637 | 111 | Transformer only | Equipment Failure/Involved | Underground | 7 | 777 | 38.9026 | -121.2657 | No | Clear;32-90 F | Fuse | Burned Open | 23-0024410 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810041 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222861350833 | 20230202 | 2016 | 20230203 | 550 | 1975398 | 574 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2296 | 39.058 | -120.9934 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0024683 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810156 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225615542396 | 20230203 | 902 | 20230203 | 1253 | 1975775 | 231 | Transformer only | Environmental/External | Ice or snow | 1 | 231 | 38.814 | -120.0298 | No | Clear;32-90 F | Fuse | Normal | 23-0024991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810353 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | JUMPER | OJ 4475 DEL MONTE | 20230203 | 910 | 20230203 | 1220 | 1975792 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 190 | 38.882 | -121.2209 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0024809 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1810282 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6123 | 20230203 | 1537 | 20230203 | 1727 | 1976174 | 110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 8360 | 38.9793 | -121.0075 | No | Overcast;32-90 F | Woodpin | Broken | 23-0025087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1810379 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 9401 | 20230204 | 654 | 20230204 | 854 | 1976399 | 120 | Distribution Circuit | Animal | Other | 5 | 600 | 38.9241 | -121.2089 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0025175 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1810465 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | MTR#1007604839 | 20230204 | 1222 | 20230204 | 1323 | 1976629 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 183 | 39.1439 | -121.0636 | No | Clear;32-90 F |  |  | 23-0025215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1810524 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | WIRE DOWN | 20230204 | 2311 | 20230205 | 1305 | 1977158 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12114 | 39.3152 | -120.9645 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025316 | OH | Sus | 31636332 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | Yes | 1810620 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 57465 | 20230205 | 330 | 20230205 | 1149 | 1977145 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10978 | 39.3625 | -120.7904 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025335 | OH | Sus | 35424879 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1810640 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 91405 | 20230205 | 759 | 20230205 | 924 | 1977295 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 425 | 38.8824 | -121.1029 | No | Clear;32-90 F |  |  | 23-0025362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1810658 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 6703 | 20230205 | 956 | 20230205 | 1010 | 1977371 | 14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 224 | 39.3202 | -120.6232 | No | Overcast-Snow;Below 32 F |  |  | 23-0025375 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1810670 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223630741581 | 20230205 | 1530 | 20230205 | 1552 | 1977471 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 38.8011 | -120.7272 | No | Clear;32-90 F | Fuse | Broken | 23-0025424 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810713 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 9769 | 20230205 | 1956 | 20230206 | 1738 | 1977702 | 1302 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 13582 | 38.7392 | -121.0826 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0025493 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1810777 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223913939830 | 20230205 | 2049 | 20230206 | 1657 | 1977737 | 1208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1940 | 38.7522 | -120.6282 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0025611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810937 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223387937287 | 20230206 | 511 | 20230206 | 912 | 1977819 | 241 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 482 | 38.6842 | -120.814 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0025543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810819 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3229 | 20230206 | 931 | 20230207 | 416 | 1978004 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9000 | 39.0961 | -121.038 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025636 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1810962 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11659 | 20230206 | 1019 | 20230206 | 1119 | 1978145 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 720 | 38.5702 | -120.7324 | No | Clear;32-90 F | Insulator | Broken | 23-0025647 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1810965 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | FUSE | 34751 | 20230206 | 1100 | 20230206 | 1226 | 1977936 | 86 | Distribution Circuit | Animal | Other | 1 | 86 | 38.8562 | -121.2848 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0025674 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810976 | 1 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222906258253 | 20230206 | 1323 | 20230207 | 37 | 1978398 | 674 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 674 | 39.2614 | -120.9748 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0025802 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1811020 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 22745 | 20230206 | 1333 | 20230206 | 1557 | 1978420 | 144 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 288 | 38.6146 | -120.7028 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0025775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811009 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 11823 | 20230206 | 1336 | 20230206 | 1829 | 1978417 | 293 | Distribution Circuit | 3rd Party | Vehicle | 274 | 80282 | 38.7456 | -120.5647 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811011 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223026042370 | 20230206 | 1639 | 20230206 | 1938 | 1978565 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 38.8253 | -120.9389 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0025950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1811052 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | OTHER | T7904 TWD T7905 | 20230207 | 2225 | 20230208 | 154 | 1979610 | 209 | Distribution Circuit | Equipment Failure/Involved | Underground | 58 | 12122 | 38.6784 | -121.0494 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0026472 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811412 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223395837609 | 20230208 | 1726 | 20230208 | 1830 | 1980296 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 320 | 38.6934 | -120.8113 | No | Clear;32-90 F | Secondary | Arcing | 23-0026844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1811669 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3701 | 20230208 | 1809 | 20230208 | 1854 | 1980335 | 45 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 225 | 38.8719 | -120.8699 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0026843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811668 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 9769 | 20230209 | 1347 | 20230209 | 1358 | 1981094 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 5 | 55 | 38.7392 | -121.0826 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0026537 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811952 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230209 | 1609 | 20230210 | 130 | 1981204 | 561 | Distribution Circuit | Animal | Bird found | 1008 | 143528 | 38.6858 | -121.0119 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027268 | OH | Sus | 31636526 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1811972 | 0 | EPSS Ckt | N | 2023 | B & GRD
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 3273 | 20230210 | 920 | 20230210 | 958 | 1981670 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 532 | 38.8802 | -121.0771 | No | Clear;32-90F |  |  | 23-0027501 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812192 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6611 | 20230210 | 1050 | 20230210 | 1428 | 1981782 | 218 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 29 | 6322 | 39.3192 | -120.432 | No | Clear;32-90F |  |  | 23-0027640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1812260 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222792754953 | 20230210 | 1126 | 20230210 | 1645 | 1981797 | 319 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 319 | 39.1711 | -121.017 | No | Clear;32-90F |  |  | 23-0027624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812251 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5249 | 20230210 | 1216 | 20230210 | 1800 | 1981848 | 344 | Distribution Circuit | 3rd Party | Vehicle | 152 | 8631 | 38.8109 | -121.1269 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0027604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1812243 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | SWITCH | 1115 | 20230210 | 1636 | 20230210 | 2038 | 1982040 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2662 | 38.7653 | -120.8856 | No | Clear;32-90F | Pole-Wood | Broken | 23-0027681 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1812287 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 788327 | 20230210 | 2145 | 20230210 | 2300 | 1982151 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 150 | 38.7946 | -121.3782 | No | Clear;32-90F |  |  | 23-0027766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1812322 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 6837 | 20230211 | 935 | 20230211 | 1350 | 1982319 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 6155 | 38.9977 | -121.0232 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0027818 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1812401 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S @ 5360 PORTER RANCH RD | 20230211 | 1012 | 20230211 | 1520 | 1982350 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 616 | 38.8475 | -120.8123 | No | Clear;32-90F | Pole-Wood | Broken | 23-0027823 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1812409 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 21873 | 20230211 | 1700 | 20230211 | 1846 | 1982616 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 2718 | 38.7228 | -121.0138 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0027868 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812452 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222360439570 | 20230212 | 1152 | 20230212 | 1445 | 1982906 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 346 | 38.7501 | -121.1731 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0027926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812517 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1101 | 152461101 | TRANSFORMER | 222581144696 | 20230212 | 1204 | 20230212 | 1245 | 1982918 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 38.8903 | -121.094 | No | Clear;32-90F | Transformer (OH) |  | 23-0027931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812523 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223605637115 | 20230212 | 1453 | 20230212 | 2025 | 1982989 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 664 | 38.6794 | -120.7379 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0027948 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812546 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224632140515 | 20230213 | 1355 | 20230213 | 1849 | 1983765 | 294 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 294 | 38.768 | -120.3765 | No | Clear;32-90F | Cutout- fuse holder | Broken | 23-0028304 | OH | Sus | 31636714 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812873 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224722040416 | 20230213 | 1356 | 20230214 | 1125 | 1983768 | 1289 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2578 | 38.7644 | -120.3448 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0028345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812905 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222593061072 | 20230213 | 1508 | 20230213 | 1638 | 1983863 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 180 | 39.3409 | -121.0845 | No | Clear;32-90F |  |  | 23-0028307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812875 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 591351 | 20230213 | 2046 | 20230214 | 1209 | 1984220 | 923 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 12648 | 39.3222 | -120.3792 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0028391 | OH | Sus | 31636671 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812944 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | JUMPER | OJ @ CGC # 222832458326 | 20230214 | 1419 | 20230214 | 1850 | 1985124 | 271 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 271 | 39.2642 | -121.0006 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0028806 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813217 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9493 | 20230215 | 648 | 20230215 | 1045 | 1985672 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 807 | 39.1867 | -120.9467 | No | Clear;Below 32 F | Transformer (OH) | Leaking | 23-0028992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813332 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2669 | 20230215 | 1120 | 20230215 | 1353 | 1986083 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2295 | 38.7475 | -120.7978 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0029197 | OH | Sus | 31636910 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1813507 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12627 | 20230215 | 1135 | 20230216 | 52 | 1986098 | 797 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2391 | 38.7925 | -120.7023 | No | Clear;32-90 F | Insulator | Broken | 23-0029437 | OH | Sus | 31636888 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1813574 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223913038203 | 20230215 | 1401 | 20230215 | 1854 | 1986259 | 293 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 293 | 38.7066 | -120.6293 | No | Clear;32-90 F | Transformer | Malfunctioning | 23-0023443 | OH | Sus | 31611150 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1813546 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | SWITCH | 736 | 20230215 | 1918 | 20230215 | 1942 | 1986475 | 24 | Distribution Circuit | Company Initiated | Return Circuit Normal | 99 | 2376 | 38.934 | -121.0799 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0014952 | UG | Sus | 35401586 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1813584 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222748854350 | 20230215 | 2023 | 20230216 | 235 | 1986467 | 372 | Transformer only | Equipment Failure/Involved | Underground | 2 | 744 | 39.1556 | -121.0314 | No | Clear;32-90 F | Service conductor | Broken | 23-0029492 | UG | Sus | 31636864 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1813609 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | TRANSFORMER | T0539 | 20230215 | 2311 | 20230216 | 36 | 1986508 | 85 | Transformer only | Equipment Failure/Involved | Underground | 6 | 510 | 38.8161 | -121.2345 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0029503 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813620 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | PIKE CITY 1101 | 152201101 | FUSE | 6765 | 20230216 | 902 | 20230216 | 1258 | 1986745 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2832 | 39.4912 | -121.0862 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0029640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813736 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | FB 1 W/O 374539 | 20230216 | 1032 | 20230216 | 1316 | 1986842 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5904 | 38.8168 | -120.9174 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0029108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813744 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | TRANSFORMER | 222174141196 | 20230216 | 1520 | 20230216 | 2257 | 1987159 | 457 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 914 | 38.7951 | -121.2383 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0029880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1813787 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20230217 | 712 | 20230217 | 848 | 1987328 | 96 | Distribution Circuit | Animal | Bird found | 53 | 5088 | 38.8428 | -121.029 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0030015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1813868 | 0 | EPSS Ckt | N | 2023 | AC
SIERRA | PLACER | SUMMIT-1101 | 152591101 | SWITCH | 48632 | 20230217 | 1053 | 20230217 | 1104 | 1987655 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 336 | 3696 | 39.32 | -120.379 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0030124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813999 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL 1102 | 152181102 | FUSE | 6047 | 20230217 | 1457 | 20230217 | 1646 | 1987827 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 872 | 38.9807 | -120.9404 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814043 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222723052052 | 20230218 | 1110 | 20230218 | 1448 | 1988218 | 218 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 654 | 39.0922 | -121.0417 | No | Clear;32-90 F | Secondary | On Ground | 23-0030467 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1814198 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | OCB | 1107/2 | 20230219 | 858 | 20230219 | 905 | 1988551 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2881 | 20167 | 38.8448 | -121.1663 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0030527 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814274 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 2208 | 20230219 | 1425 | 20230219 | 2024 | 1988895 | 359 | Distribution Circuit | 3rd Party | Vehicle | 399 | 52173 | 39.1986 | -121.0634 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0030550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814303 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 3575 | 20230220 | 621 | 20230220 | 755 | 1989179 | 94 | Distribution Circuit | Animal | Squirrel | 2 | 188 | 38.9745 | -121.0262 | No | Clear;32-90 F | Fuse | Burned Open | 23-0030610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814364 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7639 | 20230220 | 1039 | 20230220 | 1506 | 1989375 | 267 | Distribution Circuit | Animal | Squirrel | 30 | 8010 | 39.197 | -121.1733 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0030700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814484 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 33511 | 20230220 | 1420 | 20230220 | 1430 | 1989520 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 13 | 39.0335 | -121.3418 | No | Clear;32-90 F |  |  | 23-0030696 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814482 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222861255858 | 20230221 | 942 | 20230221 | 1123 | 1990030 | 101 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 101 | 39.196 | -120.9917 | Yes | Clear;32-90 F |  |  | 23-0030961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1814736 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222649656693 | 20230221 | 1007 | 20230221 | 1359 | 1990067 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 928 | 39.2196 | -121.0659 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0030904 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814719 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7559 | 20230221 | 1013 | 20230221 | 1430 | 1990073 | 257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1028 | 38.8023 | -121.4251 | Yes | Clear;32-90 F |  |  | 23-0031192 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1814881 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 8023 | 20230221 | 1020 | 20230221 | 1522 | 1989761 | 302 | Distribution Circuit | Environmental/External | Lightning | 1 | 302 | 38.9031 | -120.8347 | Yes | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0030945 | OH | Sus | 45681032 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814729 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | FUSE | 34869 | 20230221 | 1138 | 20230221 | 1232 | 1990190 | 54 | Distribution Circuit | 3rd Party | Metallic Balloon | 78 | 4212 | 38.7977 | -121.2497 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814765 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 4873 | 20230221 | 1404 | 20230221 | 1619 | 1991239 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1350 | 39.0659 | -121.0127 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0031159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814854 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33631 | 20230221 | 1414 | 20230222 | 1148 | 1991825 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6470 | 39.2905 | -121.03 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031521 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1815149 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 875388 | 20230221 | 1425 | 20230222 | 1155 | 1991609 | 1290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 17286 | 39.2827 | -120.9454 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031217 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1814899 | 0 | EPSS Ckt | N | 2023 | A B INST TIME
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3689 | 20230221 | 1425 | 20230221 | 2007 | 1991502 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2394 | 39.261 | -121.1929 | Yes | Clear;32-90 F |  |  | 23-0031821 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815420 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2784 | 20230221 | 1435 | 20230222 | 1423 | 1991747 | 1428 | Distribution Circuit | Vegetation | Tree - fell into line | 1280 | 409896 | 39.2591 | -121.0187 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1814929 | 0 | EPSS Ckt | N | 2023 | C-GRD
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7131 | 20230221 | 1438 | 20230222 | 1111 | 1991764 | 1233 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 66582 | 39.2747 | -121.0477 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031448 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1815083 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 35743 | 20230221 | 1448 | 20230221 | 1631 | 1992749 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1751 | 39.0133 | -121.0315 | Yes | Clear;32-90 F |  |  | 23-0031394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815034 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3337 | 20230221 | 1448 | 20230221 | 1746 | 1991906 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2136 | 39.0994 | -121.0291 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031618 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815240 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 20791 | 20230221 | 1453 | 20230222 | 136 | 1991982 | 643 | Distribution Circuit | 3rd Party | Vehicle | 44 | 28292 | 38.7304 | -120.9223 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1815109 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20179 | 20230221 | 1456 | 20230221 | 1722 | 1992094 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 438 | 38.6313 | -120.8554 | Yes | Overcast;32-90 F |  |  | 23-0031565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815189 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 20230221 | 1516 | 20230221 | 1700 | 1992281 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2704 | 38.7681 | -120.951 | Yes | Clear;32-90 F |  |  | 23-0031601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815222 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 8015 | 20230221 | 1537 | 20230221 | 1728 | 1992703 | 111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 555 | 38.7587 | -120.6789 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031569 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815193 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222778557382 | 20230221 | 1537 | 20230221 | 1703 | 1992652 | 86 | Transformer only | 3rd Party | Vehicle | 2 | 172 | 39.238 | -121.0198 | Yes | Clear;32-90 F | Fuse | Normal | 23-0031581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815205 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20230221 | 1547 | 20230221 | 1553 | 1991905 | 6 | Distribution Circuit | Vegetation | Tree - branch fell on line | 611 | 3666 | 39.0014 | -121.0224 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815032 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 4109 | 20230221 | 1639 | 20230222 | 1410 | 1993310 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 32160 | 39.0837 | -121.1142 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1815423 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20230221 | 1721 | 20230222 | 1215 | 1993817 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 238 | 11325 | 38.9847 | -121.366 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815275 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20230221 | 1747 | 20230221 | 1757 | 1991961 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 422 | 4220 | 39.2034 | -121.0788 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815252 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 20230221 | 1748 | 20230222 | 843 | 1994222 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 23270 | 38.7681 | -120.951 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815365 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222861255858 | 20230221 | 1752 | 20230222 | 1055 | 1994325 | 1023 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1023 | 39.196 | -120.9917 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0031901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815499 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223519239461 | 20230221 | 1824 | 20230221 | 2021 | 1992480 | 117 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 351 | 38.7431 | -120.7676 | Yes | Clear;32-90 F |  |  | 23-0031801 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1815400 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20179 | 20230221 | 2315 | 20230222 | 16 | 1996224 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 183 | 38.6313 | -120.8554 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0031987 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815584 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 8329 | 20230222 | 601 | 20230222 | 816 | 1996434 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3375 | 38.8941 | -121.3402 | No | Clear;32-90 F |  |  | 23-0032106 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815688 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230222 | 602 | 20230222 | 1656 | 1996406 | 654 | Distribution Circuit | 3rd Party | Vehicle | 936 | 237600 | 38.7391 | -120.6681 | No | Clear;Below 32 F | Pole-Wood | Broken | 23-0032048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815649 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SECTIONALIZER | 2114 | 20230222 | 955 | 20230222 | 1115 | 1997122 | 80 | Distribution Circuit | Vegetation | Tree - branch fell on line | 505 | 40400 | 39.2601 | -120.944 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0032186 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1815777 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | JUMPER | OJ CGC 221502038970 | 20230222 | 1006 | 20230222 | 1510 | 1997172 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 608 | 38.7361 | -121.475 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0032196 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815769 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20230222 | 1334 | 20230222 | 1540 | 1997796 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2520 | 38.8769 | -121.017 | No | Clear;32-90 F |  |  | 23-0032475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1815921 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 10297 | 20230223 | 947 | 20230223 | 1110 | 1999150 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 498 | 38.7232 | -120.8332 | Yes | Clear;32-90 F |  |  | 23-0033044 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1816264 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5901 | 20230223 | 1513 | 20230224 | 1010 | 1999642 | 1137 | Distribution Circuit | 3rd Party | Vehicle | 45 | 8085 | 39.0467 | -120.7858 | Yes | Clear;Below 32 F | Pole-Wood | Broken | 23-0033287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1816372 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | BROKEN JUMPER | 20230223 | 2152 | 20230224 | 908 | 2000730 | 676 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 9138 | 38.925 | -121.4519 | Yes | Clear;32-90F | Jumper | Broken | 23-0033486 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1816518 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | OCB | 1101/2 | 20230224 | 127 | 20230225 | 1509 | 2001631 | 2262 | Distribution Circuit | Vegetation | Tree - fell into line | 1370 | 593987 | 38.7444 | -121.1608 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1816595 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 6502 | 20230224 | 337 | 20230224 | 603 | 2002241 | 146 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1700 | 247320 | 38.7126 | -121.0782 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0033612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816649 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | CATLETT-1101 | 153761101 | JUMPER | BURNT OJ LD SIDE OF 7513 | 20230224 | 350 | 20230224 | 1205 | 2004227 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8254 | 38.7363 | -121.4402 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Burned Open | 23-0033811 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1816823 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38443 | 20230224 | 407 | 20230224 | 1315 | 2002443 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1644 | 38.7963 | -121.1342 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033884 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1816884 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | FUSE | 30095 | 20230224 | 425 | 20230224 | 1323 | 2002501 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 58104 | 38.7671 | -121.154 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1816835 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230224 | 519 | 20230224 | 1338 | 2003069 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15469 | 39.2788 | -120.9795 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816800 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20230224 | 727 | 20230224 | 1217 | 2003780 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 63124 | 39.1336 | -121.0717 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1816786 | 0 | EPSS Ckt | N | 2023 | A B GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6455 | 20230224 | 849 | 20230224 | 1211 | 2004367 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 8888 | 39.1515 | -120.962 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0033962 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816941 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 164936 | 20230224 | 853 | 20230224 | 1415 | 2004392 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5152 | 38.9271 | -121.2141 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0033930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816919 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 7597 | 20230224 | 854 | 20230224 | 1124 | 2004401 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 3150 | 39.0663 | -120.9467 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0033995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816967 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | FB 2 S/O CGC# 221862748940 | 20230224 | 911 | 20230224 | 1105 | 2003838 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 228 | 39.007 | -121.3458 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0033762 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1816787 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 33955 | 20230224 | 914 | 20230224 | 1641 | 2004552 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5364 | 39.043 | -120.9483 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0034126 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817062 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33769 | 20230224 | 930 | 20230224 | 1338 | s1817088 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 13392 | 39.1578 | -121.0255 | Yes | Clear;32-90 F |  |  | 23-0034182 |  | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817088 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20230224 | 943 | 20230224 | 1449 | 2004823 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6263 | 39.1527 | -121.0381 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0034000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816972 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 35323 | 20230224 | 1054 | 20230224 | 1717 | 2004949 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | 39.096 | -121.0531 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0034037 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816998 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 7783 | 20230224 | 1107 | 20230224 | 1805 | 2005112 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 53504 | 39.0555 | -120.9649 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817251 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6199 | 20230224 | 1111 | 20230225 | 1804 | 2005131 | 1853 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 65921 | 39.0825 | -120.9565 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0034093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817037 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 33947 | 20230224 | 1115 | 20230225 | 1125 | 2005209 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1450 | 39.0329 | -120.951 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817936 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222910545063 | 20230224 | 1140 | 20230224 | 1146 | 2005254 | 6 | Transformer only | 3rd Party | Customer Equipment | 1 | 6 | 38.8994 | -120.9785 | Yes | Clear;32-90F | Other | Broken | 23-0034074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817022 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9483 | 20230224 | 1217 | 20230224 | 1807 | 2005329 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2100 | 39.1902 | -120.9675 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817080 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20230224 | 1230 | 20230224 | 1504 | 2005382 | 154 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 9086 | 39.1894 | -120.9612 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817170 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9373 | 20230224 | 1247 | 20230224 | 1504 | 2005507 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1141 | 38.9134 | -120.8373 | Yes | Overcast-Rain;32-90 F |  |  | 23-0034275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817164 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18745 | 20230224 | 1311 | 20230225 | 1018 | 2005669 | 1267 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3801 | 38.6551 | -120.7047 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Normal | 23-0034420 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817274 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20230224 | 1320 | 20230224 | 1622 | 2005637 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 22386 | 38.6701 | -120.7775 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817169 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8571 | 20230224 | 1336 | 20230224 | 1707 | 2005689 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1477 | 38.9018 | -120.8612 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817197 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7391 | 20230224 | 1343 | 20230224 | 1855 | 2005699 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3120 | 39.2598 | -120.9962 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817221 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | MTR#1007476329 | 20230224 | 1356 | 20230225 | 1107 | 2005729 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1270 | 38.6664 | -120.7471 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1817293 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 69880 | 20230224 | 1406 | 20230224 | 1517 | 2005768 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 1207 | 39.0808 | -120.9419 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817175 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 3345 | 20230224 | 1432 | 20230224 | 1824 | 2005848 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 696 | 38.8956 | -120.8591 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034378 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817246 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20230224 | 1452 | 20230224 | 1529 | 2005901 | 37 | Distribution Circuit | Vegetation | Other ground vegetation | 992 | 36704 | 39.4883 | -120.8571 | Yes | Clear;Below 32 F | Pole-Wood | Broken | 23-0034276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817165 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 1423 | 20230224 | 1528 | 20230224 | 1728 | 2006024 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 14880 | 38.7284 | -120.7602 | Yes | Clear;32-90 F |  |  | 23-0034380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817248 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20230224 | 1534 | 20230224 | 2105 | 2006036 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4634 | 38.8109 | -120.8052 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0034492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817341 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223690038605 | 20230224 | 1706 | 20230224 | 2031 | 2006343 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 410 | 38.7201 | -120.7084 | Yes | Clear;32-90 F | Insulator | Broken | 23-0034499 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817349 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 20230224 | 1707 | 20230225 | 1049 | 2006350 | 1062 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8496 | 38.9409 | -120.7298 | Yes | Clear;32-90F |  |  | 23-0035136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817999 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8947 | 20230224 | 1717 | 20230225 | 1338 | 2006396 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 30525 | 39.2127 | -121.0123 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817315 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223016555572 | 20230224 | 1747 | 20230225 | 1234 | 2006489 | 1126 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 6412 | 39.1879 | -120.9366 | Yes | Overcast-Snow;32-90 F |  |  | 23-0034529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817379 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222931555764 | 20230224 | 1909 | 20230224 | 2019 | 2006815 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 70 | 39.1932 | -120.967 | Yes | Clear;32-90 F |  |  | 23-0034566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1817421 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18473 | 20230224 | 1911 | 20230224 | 2029 | 2006821 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1482 | 38.7143 | -120.7126 | Yes | Clear;32-90 F | Insulator | Broken | 23-0034520 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817370 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 20230224 | 1926 | 20230225 | 1121 | 2006841 | 955 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 955 | 38.6344 | -120.6373 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817510 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224576659905 | 20230225 | 528 | 20230225 | 1621 | 2007680 | 653 | Transformer only | 3rd Party | Other | 5 | 3265 | 39.3004 | -120.3838 | Yes | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0035077 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817940 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225199441366 | 20230225 | 946 | 20230225 | 1011 | 2006778 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 50 | 38.7881 | -120.1753 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0035123 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817987 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18475 | 20230225 | 1220 | 20230225 | 1551 | 2008418 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 4140 | 38.7141 | -120.7126 | Yes | Clear;32-90F |  |  | 23-0035329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818174 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225199441366 | 20230225 | 1248 | 20230225 | 1420 | 2008455 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 184 | 38.7881 | -120.1753 | Yes | Clear;Below 32 F | Transformer (OH) | Failed/Faulted | 23-0035234 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818076 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 8315 | 20230226 | 1540 | 20230226 | 1836 | 2010319 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 528 | 39.5249 | -121.0168 | Yes | Clear;32-90F |  |  | 23-0035912 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818726 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8175 | 20230226 | 1711 | 20230226 | 2218 | 2010410 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3684 | 39.1125 | -121.1435 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818737 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4821 | 20230226 | 1713 | 20230309 | 1645 | 2010415 | 15812 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 189744 | 39.2427 | -121 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818742 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223472436943 | 20230226 | 1729 | 20230226 | 1854 | 2010462 | 85 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 85 | 38.6747 | -120.7847 | Yes | Clear;32-90F |  |  | 23-0035930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1818743 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8955 | 20230226 | 1846 | 20230227 | 1535 | 2010728 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14988 | 39.1898 | -120.9768 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035956 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818766 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20230226 | 1916 | 20230307 | 2016 | 2010805 | 11953 | Distribution Circuit | Vegetation | Tree - fell into line | 842 | 5727184 | 39.2129 | -121.0129 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1818748 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 35809 | 20230226 | 1916 | 20230304 | 1412 | 2019623 | 8336 | Distribution Circuit | Environmental/External | Ice or snow | 92 | 766912 | 39.2215 | -121.0052 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken | 23-0038672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820792 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7415 | 20230226 | 1916 | 20230309 | 952 | 2025945 | 15276 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 137484 | 39.2184 | -120.9671 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041369 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822696 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8941 | 20230226 | 1916 | 20230309 | 1428 | 2025956 | 15552 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 202176 | 39.2125 | -120.9765 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041375 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822702 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9063 | 20230226 | 1916 | 20230310 | 1455 | 2025966 | 17019 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 238266 | 39.2185 | -120.9648 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0041379 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822706 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3631 | 20230226 | 1916 | 20230308 | 1459 | 2025973 | 14143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 183859 | 39.2143 | -120.959 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041381 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822708 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3633 | 20230226 | 1916 | 20230309 | 1044 | 2025974 | 15328 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 275904 | 39.211 | -120.9576 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822709 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7469 | 20230226 | 1916 | 20230310 | 2103 | 2025978 | 17387 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 799802 | 39.2081 | -120.9493 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041383 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822710 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 6685 | 20230226 | 1916 | 20230311 | 1940 | 2031661 | 18744 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 1387056 | 39.216 | -120.9972 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043270 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1823855 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9321 | 20230226 | 1956 | 20230226 | 2200 | 2010846 | 124 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 7068 | 38.9257 | -120.793 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818809 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 33701 | 20230226 | 2010 | 20230227 | 948 | 2010861 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1636 | 39.2131 | -121.0174 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035952 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1818761 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20230226 | 2123 | 20230310 | 1623 | 2010957 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 1058994 | 39.4553 | -121.053 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1818836 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | JUMPER | OJ'S 1 SPAN SS OF 30629 | 20230226 | 2123 | 20230310 | 1300 | 2024966 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16777 | 39.4717 | -121.0849 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822435 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | JUMPER | OJ'S @ HARD TAP SS OF CGC 222577565960 | 20230226 | 2123 | 20230310 | 1300 | 2024969 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 100662 | 39.474 | -121.0853 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Normal | 23-0040877 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1822436 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6915 | 20230226 | 2127 | 20230227 | 1330 | 2010955 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4815 | 38.9299 | -120.7589 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819091 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9771 | 20230226 | 2129 | 20230305 | 1903 | 2023456 | 9934 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 466892 | 39.2022 | -121.0212 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1822002 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33823 | 20230226 | 2130 | 20230302 | 1528 | 2019154 | 5398 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 102562 | 39.1706 | -121.0443 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038474 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820664 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8257 | 20230226 | 2130 | 20230302 | 1048 | 2019162 | 5118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 56298 | 39.1808 | -121.0468 | Yes | Clear;32-90 F |  |  | 23-0038476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820666 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222766254416 | 20230226 | 2130 | 20230307 | 1453 | 2019718 | 12563 | Transformer only | Vegetation | Tree - fell into line | 1 | 12563 | 39.1571 | -121.0269 | Yes | Clear;32-90F | Service conductor | Broken | 23-0038719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820816 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222745154485 | 20230226 | 2130 | 20230310 | 1425 | 2020228 | 16855 | Transformer only | Environmental/External | Ice or snow | 1 | 16855 | 39.1593 | -121.0329 | Yes | Clear;32-90 F | Transformer | Broken | 23-0038966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820969 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9781 | 20230226 | 2130 | 20230310 | 1735 | 2022867 | 17045 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 51135 | 39.1825 | -121.0273 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0040073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | No | No | 1821817 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33727 | 20230226 | 2130 | 20230310 | 1610 | 2022868 | 16960 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 50880 | 39.1852 | -121.0276 | Yes | Clear;32-90 F |  |  | 23-0040074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821818 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33707 | 20230226 | 2130 | 20230310 | 1900 | 2023473 | 17130 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 34260 | 39.1993 | -121.0191 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822008 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ'S 15 SPANS N/OF 7039 | 20230226 | 2130 | 20230309 | 1140 | 2023475 | 15250 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 30500 | 39.2048 | -121.0202 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822010 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33713 | 20230226 | 2130 | 20230310 | 1650 | 2023670 | 17000 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 85000 | 39.1975 | -121.0341 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040330 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822060 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33799 | 20230226 | 2130 | 20230309 | 1540 | 2024088 | 15490 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 77450 | 39.1922 | -121.0065 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040460 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1822194 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7045 | 20230226 | 2130 | 20230309 | 1815 | 2024091 | 15645 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 62580 | 39.1931 | -121.009 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040461 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1822195 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33719 | 20230226 | 2130 | 20230309 | 1616 | 2024112 | 15526 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15526 | 39.194 | -121.0286 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040469 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822203 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33723 | 20230226 | 2130 | 20230305 | 2045 | 2024115 | 10035 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 30105 | 39.1933 | -121.0261 | Yes | Clear;32-90F |  |  | 23-0040470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822204 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33309 | 20230226 | 2130 | 20230306 | 1419 | 2024152 | 11089 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 33267 | 39.1886 | -120.9997 | Yes | Clear;32-90F |  |  | 23-0040502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822237 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 63513 | 20230226 | 2135 | 20230310 | 1651 | 2026718 | 16996 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 33992 | 39.2789 | -120.9376 | Yes | Clear;32-90F |  |  | 23-0036041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822927 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31949 | 20230226 | 2152 | 20230306 | 1654 | 2010980 | 11222 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33666 | 39.0088 | -120.8468 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0036184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818921 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 40061 | 20230226 | 2200 | 20230312 | 1309 | 2023883 | 19629 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 19629 | 39.3079 | -120.936 | Yes | Clear;32-90F | Customer Equipment | Failed/Faulted | 23-0040396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822132 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2140 | 20230226 | 2201 | 20230311 | 1846 | 2010985 | 18525 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 11056803 | 39.2895 | -120.9854 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0036035 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1818841 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9889 | 20230226 | 2201 | 20230312 | 1320 | 2032767 | 19639 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39278 | 39.2991 | -120.9693 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1824080 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | FB 1 SPAN W/OF 6573 | 20230226 | 2201 | 20230312 | 1546 | 2032771 | 19785 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 59355 | 39.3149 | -120.9851 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1824081 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20230226 | 2203 | 20230227 | 1013 | 2010986 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4368 | 38.9928 | -120.8828 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Burned/flashed | 23-0036034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1818840 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8639 | 20230226 | 2213 | 20230226 | 2339 | 2010994 | 86 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 631 | 39.145 | -120.9763 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818852 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20230226 | 2228 | 20230310 | 1651 | 2010964 | 16943 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 1040285 | 39.274 | -120.9698 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1818846 | 0 | EPSS Ckt | N | 2023 | AC GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31407 | 20230226 | 2228 | 20230311 | 1219 | 2030894 | 18111 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 181110 | 39.2779 | -120.9453 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1823705 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9795 | 20230226 | 2247 | 20230227 | 1110 | 2011023 | 743 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 40865 | 39.1904 | -120.9887 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036178 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818917 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7049 | 20230226 | 2252 | 20230227 | 133 | 2011019 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6440 | 39.191 | -121.0028 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036042 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1818847 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3629 | 20230226 | 2259 | 20230227 | 1001 | 2011027 | 662 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 5958 | 39.2129 | -121.0061 | Yes | Clear;32-90F |  |  | 23-0036202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818935 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5829 | 20230226 | 2308 | 20230227 | 1012 | 2011090 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 57104 | 38.9432 | -120.7202 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818959 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20230226 | 2342 | 20230227 | 1214 | 2011101 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 56772 | 39.275 | -121.021 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036049 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1818854 | 0 | EPSS Ckt | N | 2023 | AC GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33795 | 20230227 | 10 | 20230227 | 1406 | 2011109 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2508 | 39.1997 | -121.0106 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818897 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20230227 | 25 | 20230227 | 948 | 2011114 | 563 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 33217 | 39.1894 | -120.9612 | Yes | Clear;32-90F |  |  | 23-0036188 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818923 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1367 | 20230227 | 406 | 20230227 | 639 | 2011146 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 4437 | 38.7454 | -120.6316 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036068 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818871 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224084539806 | 20230227 | 553 | 20230227 | 727 | 2011168 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 94 | 38.7507 | -120.5682 | Yes | Clear;32-90F | Jumper | Bent or Twisted | 23-0036083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818877 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9553 | 20230227 | 635 | 20230306 | 1725 | 2011186 | 10730 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 225330 | 39.2613 | -120.9057 | Yes | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818904 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 8871 | 20230227 | 718 | 20230227 | 903 | 2011229 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1470 | 39.2789 | -121.086 | Yes | Clear;32-90F |  |  | 23-0036152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818907 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7329 | 20230227 | 721 | 20230311 | 1142 | 2011233 | 17541 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 245574 | 39.2352 | -120.9819 | Yes | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819078 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31751 | 20230227 | 1018 | 20230227 | 1252 | 2011756 | 154 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 308 | 39.2341 | -120.9848 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819053 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4899 | 20230227 | 1023 | 20230227 | 1800 | 2011780 | 457 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 15538 | 39.1993 | -121.187 | Yes | Clear;32-90 F |  |  | 23-0036698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819257 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20230227 | 1031 | 20230227 | 1210 | 2011804 | 99 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 2377 | 39.2095 | -120.827 | Yes | Clear;32-90F |  |  | 23-0036342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819017 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK 1101 | 152301101 | FUSE | 6375 | 20230227 | 1032 | 20230228 | 1238 | 2011781 | 1566 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 120 | 186419 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0036275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818972 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 80083 | 20230227 | 1039 | 20230302 | 1256 | 2011826 | 4457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 22285 | 39.2151 | -120.8091 | Yes | Clear;32-90F | Lightning Arrestor | Broken | 23-0038799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820864 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9371 | 20230227 | 1047 | 20230307 | 1921 | 2011891 | 12034 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 24068 | 38.9399 | -120.7368 | Yes | Clear;Below 32 F | Pole-Wood | Broken | 23-0036608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819182 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | WIRE DOWN ROAD PHASE | 20230227 | 1047 | 20230307 | 1950 | 2011901 | 12063 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4216 | 5663307 | 38.9368 | -120.7452 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | Yes | 1819191 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3377 | 20230227 | 1047 | 20230308 | 1441 | 2011856 | 13194 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 2295756 | 38.9439 | -120.7215 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038315 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820511 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 40519 | 20230227 | 1047 | 20230307 | 1827 | 2022418 | 11980 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 23960 | 38.9377 | -120.7431 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821729 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6901 | 20230227 | 1047 | 20230307 | 1921 | 2022908 | 12034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 180510 | 38.94 | -120.7288 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821827 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 20230227 | 1047 | 20230308 | 1959 | 2022910 | 13512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 108096 | 38.9409 | -120.7298 | Yes | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0040084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821828 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 57171 | 20230227 | 1047 | 20230307 | 1921 | 2024703 | 12034 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12034 | 38.9362 | -120.7472 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1822372 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222782056021 | 20230227 | 1050 | 20230227 | 1123 | 2011306 | 33 | Transformer only | Vegetation | Tree - fell into line | 6 | 198 | 39.2005 | -121.0192 | Yes | Clear;32-90F | Secondary | On Ground | 23-0036260 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1818966 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7585 | 20230227 | 1105 | 20230227 | 1529 | 2011918 | 264 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4488 | 38.7722 | -121.4512 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819044 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32341 | 20230227 | 1134 | 20230227 | 1318 | 2012074 | 104 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 208 | 38.9354 | -120.7485 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Normal | 23-0036454 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819080 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3625 | 20230227 | 1140 | 20230310 | 1331 | 2013377 | 15951 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 159510 | 39.211 | -121.0067 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819262 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 34175 | 20230227 | 1148 | 20230307 | 1132 | 2024720 | 11504 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 178784 | 39.2406 | -120.924 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822379 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2717 | 20230227 | 1148 | 20230308 | 1725 | 2026014 | 13297 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 5850680 | 39.2616 | -120.9247 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041388 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | Yes | 1822717 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 3679 | 20230227 | 1148 | 20230311 | 1608 | 2031439 | 17540 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 17540 | 39.2918 | -120.9527 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1823804 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8947 | 20230227 | 1149 | 20230308 | 1341 | 2025941 | 13072 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 326800 | 39.2127 | -121.0123 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822693 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230227 | 1149 | 20230311 | 1331 | 2012100 | 17210 | Distribution Circuit | Vegetation | Tree - fell into line | 1990 | 16642449 | 39.2417 | -121.0264 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1819015 | 0 | EPSS Ckt | N | 2023 | B & C GRD
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20230227 | 1150 | 20230309 | 1905 | 2012089 | 14835 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 474720 | 39.2132 | -121.0136 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036427 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819068 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18399 | 20230227 | 1155 | 20230227 | 1246 | 2012130 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 969 | 38.5933 | -120.6537 | Yes | Overcast-Snow;32-90 F |  |  | 23-0036429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819070 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ @ CGC 222826948203 | 20230227 | 1201 | 20230227 | 1710 | 2011916 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1545 | 38.9859 | -121.0059 | Yes | Clear;32-90F | Transformer (OH) | Leaking | 23-0036520 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819116 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6697 | 20230227 | 1203 | 20230305 | 2211 | 2012705 | 9248 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 258944 | 39.1942 | -120.9935 | Yes | Overcast-Fog;Below 32 F | Conductor- Overhead | Normal | 23-0036539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819129 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 5655 | 20230227 | 1204 | 20230227 | 1851 | s1819319 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 13024 | 38.7977 | -120.7123 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819319 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6331 | 20230227 | 1206 | 20230305 | 1834 | 2012202 | 9028 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 758352 | 39.1457 | -120.9054 | Yes | Overcast-Snow;32-90 F | Fuse | Failed/Faulted | 23-0036555 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819141 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8755 | 20230227 | 1209 | 20230309 | 1243 | 2012171 | 14434 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 577360 | 39.1913 | -120.9937 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040646 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1822338 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33805 | 20230227 | 1209 | 20230310 | 851 | 2025111 | 15642 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 187704 | 39.1987 | -120.9931 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0040923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822474 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3455 | 20230227 | 1212 | 20230307 | 1545 | 2021805 | 11733 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 293325 | 38.922 | -120.7775 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039661 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821428 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7153 | 20230227 | 1214 | 20230306 | 1755 | 2020049 | 10421 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 812838 | 39.2455 | -121.0448 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038853 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820893 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6313 | 20230227 | 1221 | 20230307 | 1432 | 2021818 | 11651 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 273766 | 39.1511 | -120.8999 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821435 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6359 | 20230227 | 1221 | 20230306 | 1635 | 2021820 | 10334 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 41336 | 39.1525 | -120.8937 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821436 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6361 | 20230227 | 1221 | 20230307 | 1535 | 2021822 | 11714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 35142 | 39.1567 | -120.8896 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039682 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821438 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33577 | 20230227 | 1221 | 20230307 | 1535 | 2021823 | 11714 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 35142 | 39.1691 | -120.893 | Yes | Clear;32-90F |  |  | 23-0039685 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1821440 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ @ HARD TAP SS OF CGC 223187054669 | 20230227 | 1221 | 20230307 | 1106 | 2023969 | 11445 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11445 | 39.1644 | -120.8772 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822156 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6309 | 20230227 | 1221 | 20230307 | 1650 | 2024644 | 11789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 153257 | 39.1712 | -120.8717 | Yes | Overcast-Snow;32-90 F | Crossarm- Wood | Broken | 23-0040696 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822356 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3629 | 20230227 | 1233 | 20230309 | 1906 | 2012667 | 14793 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 133137 | 39.2129 | -121.0061 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1819118 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3627 | 20230227 | 1233 | 20230309 | 1906 | 2026899 | 14793 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 147930 | 39.2141 | -121.0073 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1822962 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8945 | 20230227 | 1236 | 20230308 | 1649 | 2025935 | 13213 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 264260 | 39.2102 | -121.0041 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822690 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30861 | 20230227 | 1241 | 20230309 | 1319 | 2025933 | 14438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 115504 | 39.2052 | -120.9808 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822688 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8943 | 20230227 | 1241 | 20230308 | 1753 | 2025934 | 13272 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 185808 | 39.2038 | -120.9827 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822689 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8667 | 20230227 | 1245 | 20230310 | 1634 | 2024142 | 16069 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 867726 | 39.184 | -120.9994 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0040474 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822209 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 58023 | 20230227 | 1247 | 20230309 | 1845 | 2026739 | 14758 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14758 | 39.2867 | -121.0039 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822935 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 35501 | 20230227 | 1248 | 20230310 | 1223 | 2026741 | 15815 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 15815 | 39.2878 | -121.0018 | Yes | Clear;32-90F |  |  | 23-0036414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822936 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 4697 | 20230227 | 1248 | 20230309 | 1256 | 2026747 | 14408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 86448 | 39.2898 | -120.9991 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822940 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30869 | 20230227 | 1249 | 20230309 | 1334 | 2025942 | 14445 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 28890 | 39.2086 | -120.9986 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041366 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822694 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7041 | 20230227 | 1249 | 20230309 | 1113 | 2013106 | 14304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 243168 | 39.1983 | -121.0221 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819206 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20230227 | 1300 | 20230227 | 1905 | 2012309 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 34675 | 38.9858 | -121.022 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036618 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819190 | 0 | EPSS Ckt | N | 2023 | A & C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7065 | 20230227 | 1302 | 20230309 | 1618 | 2025078 | 14596 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 744396 | 39.1869 | -120.9556 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040910 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822461 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33255 | 20230227 | 1302 | 20230307 | 1905 | 2025643 | 11883 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11883 | 39.1876 | -120.9582 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041214 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822633 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | SWITCH | 1975 | 20230227 | 1303 | 20230310 | 1956 | 2025931 | 16253 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 796397 | 39.2099 | -120.9358 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041355 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822685 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7161 | 20230227 | 1303 | 20230310 | 2102 | 2025943 | 16319 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 16319 | 39.2085 | -120.9979 | Yes | Clear;32-90F |  |  | 23-0041367 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822695 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 33781 | 20230227 | 1303 | 20230309 | 1000 | 2025950 | 14217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 28434 | 39.2056 | -120.9807 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822697 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 33763 | 20230227 | 1303 | 20230310 | 1440 | 2025952 | 15937 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 95622 | 39.2096 | -120.9783 | Yes | Clear;32-90F |  |  | 23-0041373 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822700 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7261 | 20230227 | 1303 | 20230309 | 1445 | 2025954 | 14502 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 464064 | 39.2117 | -120.9761 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822701 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8939 | 20230227 | 1303 | 20230308 | 1405 | 2025957 | 13022 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 65110 | 39.2144 | -120.9754 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822703 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4839 | 20230227 | 1303 | 20230310 | 1628 | 2025958 | 16045 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 48135 | 39.2188 | -120.9729 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0041377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822704 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 9741 | 20230227 | 1306 | 20230227 | 1717 | 2012384 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 32379 | 39.1038 | -121.0843 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036534 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819124 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 20230227 | 1310 | 20230307 | 1755 | 2025759 | 11805 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 318735 | 39.1757 | -120.9295 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041280 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822651 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7385 | 20230227 | 1311 | 20230227 | 1622 | 2012380 | 191 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 13179 | 39.2623 | -121.0131 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036501 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819105 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7105 | 20230227 | 1319 | 20230305 | 1148 | 2012520 | 8549 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 1483405 | 39.2847 | -121.0584 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0036572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819156 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 9533 | 20230227 | 1323 | 20230228 | 1222 | 2012432 | 1379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 20685 | 38.9992 | -120.997 | Yes | Clear;32-90 F |  |  | 23-0037304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819730 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 654283 | 20230227 | 1325 | 20230308 | 1143 | 2025092 | 12858 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 102864 | 39.2138 | -121.0141 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0040918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822469 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7055 | 20230227 | 1326 | 20230308 | 1809 | 2024154 | 13243 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 291346 | 39.1909 | -120.9915 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040520 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822255 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20230227 | 1326 | 20230309 | 1740 | 2024165 | 14654 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 820624 | 39.1731 | -120.9738 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822264 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8957 | 20230227 | 1326 | 20230308 | 1810 | 2025645 | 13244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 238392 | 39.1885 | -120.9532 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0041215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822634 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30529 | 20230227 | 1329 | 20230228 | 2115 | 2012456 | 1906 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9530 | 39.0722 | -121.0559 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0037178 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819651 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9155 | 20230227 | 1332 | 20230309 | 918 | 2012468 | 14146 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 170566 | 39.2132 | -121.014 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819202 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5583 | 20230227 | 1335 | 20230307 | 1828 | 2020283 | 11813 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 259886 | 38.9355 | -120.7431 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820986 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20230227 | 1340 | 20230307 | 2008 | 2012453 | 11762 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2185 | 14248234 | 39.1911 | -120.9965 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0036477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819092 | 0 | EPSS Ckt | N | 2023 | B & C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20230227 | 1340 | 20230310 | 1716 | 2021969 | 16056 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 867024 | 39.1908 | -120.9934 | Yes | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039776 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821539 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9795 | 20230227 | 1340 | 20230311 | 1556 | 2024155 | 17416 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 957880 | 39.1904 | -120.9887 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040521 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822256 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20230227 | 1340 | 20230311 | 922 | 2024158 | 17022 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 204264 | 39.1679 | -120.9656 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | On Ground | 23-0040524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822259 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8789 | 20230227 | 1340 | 20230307 | 1511 | 2025070 | 11611 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 325108 | 39.1878 | -120.9258 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822457 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33257 | 20230227 | 1340 | 20230307 | 1423 | 2025072 | 11563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11563 | 39.1899 | -120.966 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0040908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822459 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9481 | 20230227 | 1340 | 20230308 | 1631 | 2025632 | 13131 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 157572 | 39.1909 | -120.97 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0041209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822630 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33315 | 20230227 | 1340 | 20230307 | 1423 | 2025636 | 11563 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 23126 | 39.192 | -120.9747 | Yes | Clear;32-90F |  |  | 23-0041210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822631 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 694875 | 20230227 | 1340 | 20230307 | 1423 | 2025647 | 11563 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 34689 | 39.1877 | -120.9512 | Yes | Clear;32-90F |  |  | 23-0041216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822635 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7063 | 20230227 | 1340 | 20230307 | 1507 | 2025648 | 11607 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 1346412 | 39.1877 | -120.9501 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0041218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822636 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9075 | 20230227 | 1340 | 20230310 | 1519 | 2026958 | 15939 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 812889 | 39.1859 | -120.9722 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041821 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1822968 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9075 | 20230227 | 1340 | 20230310 | 1519 | 2026958 | 15939 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 812889 | 39.1859 | -120.9722 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041821 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1822968 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33281 | 20230227 | 1340 | 20230311 | 921 | 2031950 | 17021 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 799987 | 39.1678 | -120.9663 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1823927 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7057 | 20230227 | 1342 | 20230310 | 1359 | 2024164 | 15857 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 539138 | 39.1912 | -120.9774 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822263 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20230227 | 1345 | 20230308 | 1513 | 2025638 | 13048 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 769832 | 39.1894 | -120.9612 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822632 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9793 | 20230227 | 1348 | 20230310 | 1500 | 2024156 | 15912 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 397800 | 39.1905 | -120.984 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822257 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | SWITCH | 774186 | 20230227 | 1348 | 20230227 | 2003 | 2012573 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 1238 | 175580 | 38.7259 | -120.7943 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1819094 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9483 | 20230227 | 1349 | 20230309 | 1809 | 2025071 | 14660 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87960 | 39.1902 | -120.9675 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822458 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6757 | 20230227 | 1349 | 20230308 | 2038 | 2025075 | 13369 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 227273 | 39.1882 | -120.9617 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822460 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 224226671425 | 20230227 | 1350 | 20230301 | 1713 | 2012576 | 3083 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 9249 | 39.617 | -120.4983 | Yes | Clear;32-90F |  |  | 23-0036483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819093 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 7571 | 20230227 | 1350 | 20230306 | 1320 | 2016263 | 10050 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 301500 | 38.9985 | -120.8694 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1819946 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 20230227 | 1350 | 20230307 | 1513 | 2018311 | 11603 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 475723 | 39.0098 | -120.8455 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820413 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31939 | 20230227 | 1350 | 20230306 | 1800 | 2018316 | 10330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 20660 | 39.0067 | -120.8524 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820415 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31937 | 20230227 | 1350 | 20230307 | 1854 | 2018320 | 11824 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 889769 | 39.0066 | -120.8531 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038187 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820417 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31933 | 20230227 | 1350 | 20230304 | 1427 | 2018435 | 7237 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 65133 | 39.0058 | -120.8554 | Yes | Clear;32-90 F |  |  | 23-0038246 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820468 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 3771 | 20230227 | 1350 | 20230303 | 1916 | 2018934 | 6086 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 91290 | 38.9979 | -120.8752 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038408 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820606 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 3043 | 20230227 | 1350 | 20230303 | 1535 | 2020372 | 5865 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 152490 | 38.9988 | -120.8904 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821017 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 32023 | 20230227 | 1350 | 20230304 | 1123 | 2021780 | 7053 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 141060 | 38.982 | -120.8747 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Together | 23-0039647 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1821421 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20230227 | 1351 | 20230304 | 1821 | 2012585 | 7392 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1390 | 6975265 | 39.0162 | -120.8351 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Together | 23-0036491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1819099 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | OTHER | 2503 | 20230227 | 1351 | 20230227 | 1836 | 2012586 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 882 | 49266 | 38.7235 | -120.7969 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036530 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | Yes | 1819122 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33299 | 20230227 | 1354 | 20230310 | 1520 | 2024779 | 15926 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 382224 | 39.1705 | -120.9927 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822395 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12623 | 20230227 | 1356 | 20230228 | 1249 | 2014316 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28833 | 38.7856 | -120.6992 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819607 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9353 | 20230227 | 1402 | 20230306 | 1155 | 2012780 | 9953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 43087 | 38.9015 | -120.9035 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0039979 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1821735 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 20230227 | 1411 | 20230227 | 1711 | 2012638 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3420 | 38.7136 | -120.632 | Yes |  | Conductor- Overhead | Normal | 23-0036684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819246 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7575 | 20230227 | 1412 | 20230303 | 2123 | 2016091 | 6191 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 105247 | 39.237 | -121.0063 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819915 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7715 | 20230227 | 1413 | 20230311 | 1319 | 2030898 | 17226 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 155034 | 39.2724 | -120.9688 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043036 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1823707 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31651 | 20230227 | 1413 | 20230311 | 1434 | 2031441 | 17301 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 51903 | 39.2917 | -120.9518 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0043211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1823805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 67415 | 20230227 | 1413 | 20230228 | 1627 | 2012645 | 1574 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 23610 | 38.883 | -120.8795 | Yes | Clear;32-90 F |  |  | 23-0037569 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819916 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 230743 | 20230227 | 1419 | 20230303 | 2123 | 2021831 | 6184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 142232 | 39.2403 | -121.005 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0039691 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821446 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31815 | 20230227 | 1433 | 20230310 | 1909 | 2021384 | 16116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 48348 | 39.2616 | -120.9897 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0039492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821320 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31809 | 20230227 | 1433 | 20230309 | 829 | 2026006 | 14036 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 28072 | 39.252 | -120.9971 | Yes | Clear;32-90F |  |  | 23-0041386 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822715 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20899 | 20230227 | 1436 | 20230227 | 1558 | 2012703 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1558 | 38.6003 | -120.7136 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0036560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819143 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 63545 | 20230227 | 1442 | 20230309 | 1806 | 2020109 | 14604 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29208 | 39.3638 | -120.795 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0038889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820919 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8051 | 20230227 | 1442 | 20230310 | 1707 | 2020113 | 15985 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 63940 | 39.3575 | -120.8018 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0038891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820920 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | TRANSFORMER | 223405061940 | 20230227 | 1442 | 20230313 | 636 | 2020176 | 19674 | Transformer only | Environmental/External | Ice or snow | 1 | 19674 | 39.3609 | -120.7964 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0038957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820964 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222835855575 | 20230227 | 1444 | 20230306 | 1419 | 2012653 | 10055 | Transformer only | Vegetation | Tree - fell into line | 1 | 10055 | 39.1885 | -121.0006 | Yes | Clear;32-90F | Service conductor | Bent or Twisted | 23-0036566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819149 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31807 | 20230227 | 1449 | 20230309 | 1137 | 2026004 | 14208 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 284160 | 39.2519 | -120.9973 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822714 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7313 | 20230227 | 1500 | 20230309 | 2048 | 2012761 | 14748 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 235968 | 39.2331 | -120.9878 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036635 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819207 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ'S @ FLYING BELLS 5 SPANS LD SIDE OF 7313 | 20230227 | 1500 | 20230310 | 1245 | 2029409 | 15705 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 2073060 | 39.2314 | -120.9916 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0036635 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1823387 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22029 | 20230227 | 1508 | 20230227 | 1825 | 2012789 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1576 | 38.7993 | -120.7168 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819265 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31935 | 20230227 | 1509 | 20230307 | 1715 | 2018431 | 11646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 46584 | 39.0063 | -120.8543 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038244 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820467 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13817 | 20230227 | 1512 | 20230228 | 1009 | 2012820 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 28425 | 38.6215 | -120.5877 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819299 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9809 | 20230227 | 1515 | 20230310 | 1241 | 2023684 | 15686 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 298034 | 39.1984 | -121.0317 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822063 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20230227 | 1515 | 20230228 | 1643 | 2012826 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 21392 | 38.8109 | -120.8052 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036736 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819296 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7043 | 20230227 | 1516 | 20230306 | 1811 | 2013277 | 10255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 133315 | 39.1984 | -121.0255 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0036676 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819240 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3605 | 20230227 | 1516 | 20230307 | 1618 | 2025088 | 11582 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 138984 | 39.1952 | -121.0237 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040916 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822467 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 30745 | 20230227 | 1518 | 20230228 | 1142 | 2012834 | 1224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 45719 | 39.0433 | -120.9863 | Yes | Clear;32-90F |  |  | 23-0037222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819677 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18473 | 20230227 | 1519 | 20230228 | 1523 | 2012841 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 30324 | 38.7143 | -120.7126 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0037336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819748 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 7781 | 20230227 | 1520 | 20230305 | 1552 | 2022788 | 8672 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 329536 | 39.0183 | -120.8485 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040066 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821809 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3603 | 20230227 | 1524 | 20230307 | 1457 | 2025083 | 11493 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 103437 | 39.1953 | -121.0238 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822465 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7755 | 20230227 | 1555 | 20230301 | 1407 | 2012463 | 2772 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 47124 | 39.0778 | -121.0865 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1819195 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7307 | 20230227 | 1600 | 20230304 | 1652 | 2013986 | 7252 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 580160 | 39.2394 | -120.9972 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken | 23-0039686 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821441 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9709 | 20230227 | 1606 | 20230302 | 1123 | 2019143 | 4037 | Distribution Circuit | Vegetation | Tree - fell into line | 263 | 1061731 | 39.1493 | -121.0347 | Yes | Overcast-Fog-Snow;32-90 F | Service conductor | Broken | 23-0038466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820658 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9709 | 20230227 | 1606 | 20230302 | 1123 | 2019143 | 4037 | Distribution Circuit | Vegetation | Tree - fell into line | 263 | 1061731 | 39.1493 | -121.0347 | Yes | Overcast-Fog-Snow;32-90 F | Service conductor | Broken | 23-0038466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820658 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20230227 | 1606 | 20230302 | 1206 | 2019146 | 4080 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 22 | 89760 | 39.1527 | -121.0381 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820661 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20230227 | 1606 | 20230302 | 1206 | 2019146 | 4080 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 22 | 89760 | 39.1527 | -121.0381 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820661 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 4637 | 20230227 | 1606 | 20230302 | 1518 | 2019152 | 4272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 200784 | 39.168 | -121.0464 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820663 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 4637 | 20230227 | 1606 | 20230302 | 1518 | 2019152 | 4272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 200784 | 39.168 | -121.0464 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820663 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 4639 | 20230227 | 1606 | 20230302 | 1231 | 2019158 | 4105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 562385 | 39.173 | -121.0452 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820665 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 4639 | 20230227 | 1606 | 20230302 | 1231 | 2019158 | 4105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 562385 | 39.173 | -121.0452 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820665 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33737 | 20230227 | 1606 | 20230303 | 1212 | 2020481 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 176832 | 39.1744 | -121.0296 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0039048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821040 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33737 | 20230227 | 1606 | 20230303 | 1212 | 2020481 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 176832 | 39.1744 | -121.0296 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0039048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821040 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9789 | 20230227 | 1606 | 20230308 | 915 | 2021704 | 12549 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 326274 | 39.212 | -121.0191 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039614 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821397 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3953 | 20230227 | 1606 | 20230307 | 1807 | 2022877 | 11641 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 384153 | 39.1909 | -121.0268 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0040076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821820 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3953 | 20230227 | 1606 | 20230307 | 1807 | 2022877 | 11641 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 384153 | 39.1909 | -121.0268 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0040076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821820 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33765 | 20230227 | 1606 | 20230309 | 1723 | 2024086 | 14477 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 390879 | 39.2028 | -121.0111 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822193 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33765 | 20230227 | 1606 | 20230309 | 1723 | 2024086 | 14477 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 390879 | 39.2028 | -121.0111 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822193 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7049 | 20230227 | 1606 | 20230309 | 1711 | 2024098 | 14465 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 578600 | 39.191 | -121.0028 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040467 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822201 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7049 | 20230227 | 1606 | 20230309 | 1711 | 2024098 | 14465 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 578600 | 39.191 | -121.0028 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040467 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822201 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 7667 | 20230227 | 1606 | 20230302 | 1235 | 2019626 | 4109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 246540 | 39.1549 | -121.0394 | Yes | Clear-Drizzle;32-90 F |  |  | 23-0038764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820845 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 31243 | 20230227 | 1607 | 20230308 | 1700 | 2024151 | 13013 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 39039 | 39.1882 | -120.9995 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822233 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9723 | 20230227 | 1610 | 20230302 | 1219 | 2019167 | 4089 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 445701 | 39.1803 | -121.0471 | Yes | Overcast-Rain;32-90 F |  |  | 23-0038480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820669 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9723 | 20230227 | 1610 | 20230302 | 1219 | 2019167 | 4089 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 109 | 445701 | 39.1803 | -121.0471 | Yes | Overcast-Rain;32-90 F |  |  | 23-0038480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820669 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9381 | 20230227 | 1610 | 20230306 | 1431 | 2015504 | 9981 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 149715 | 38.9255 | -120.8002 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1819778 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6905 | 20230227 | 1610 | 20230307 | 1424 | 2015540 | 11414 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11414 | 38.9255 | -120.8011 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037378 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819786 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9321 | 20230227 | 1610 | 20230306 | 1802 | 2015682 | 10192 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 580944 | 38.9257 | -120.793 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1819825 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9319 | 20230227 | 1610 | 20230306 | 1058 | 2018598 | 9768 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 214896 | 38.9233 | -120.8061 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820505 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3915 | 20230227 | 1610 | 20230305 | 1746 | 2018603 | 8736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 297024 | 38.918 | -120.815 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820507 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9349 | 20230227 | 1610 | 20230307 | 1828 | 2020289 | 11658 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 291450 | 38.9354 | -120.7471 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038987 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820987 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 41091 | 20230227 | 1610 | 20230305 | 1853 | 2022416 | 8803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 246484 | 38.9245 | -120.812 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039972 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821728 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31095 | 20230227 | 1610 | 20230306 | 1753 | 2022891 | 10183 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 61098 | 38.9261 | -120.7781 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821825 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9703 | 20230227 | 1615 | 20230310 | 1307 | 2020500 | 15652 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 939120 | 39.1681 | -121.0295 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0039053 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821044 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6363 | 20230227 | 1616 | 20230306 | 1809 | 2024696 | 10193 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 336369 | 39.1654 | -120.8745 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040723 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822369 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ'S 1 SPAN E/OF CGC 223242854376 | 20230227 | 1617 | 20230307 | 1538 | 2025020 | 11481 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 23490 | 39.1542 | -120.8567 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0040894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1822450 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7095 | 20230227 | 1619 | 20230309 | 1835 | 2022864 | 14536 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 654120 | 39.1802 | -121.028 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821816 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33307 | 20230227 | 1619 | 20230306 | 1419 | 2024149 | 9960 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 109560 | 39.1872 | -120.9997 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0040485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822220 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18789 | 20230227 | 1634 | 20230227 | 1957 | 2012195 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 4263 | 38.6816 | -120.7192 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Normal | 23-0036641 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819212 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31097 | 20230227 | 1635 | 20230307 | 1828 | 2021204 | 11633 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 116330 | 38.9332 | -120.753 | Yes | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0039426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1821282 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8433 | 20230227 | 1641 | 20230303 | 1924 | 2019839 | 5923 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 59230 | 39.218 | -121.0176 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038777 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820853 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9885 | 20230227 | 1641 | 20230308 | 1850 | 2021773 | 13089 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 52356 | 39.2178 | -121.0225 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0039645 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1821419 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30163 | 20230227 | 1641 | 20230309 | 1633 | 2021781 | 14392 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 43176 | 39.215 | -121.0203 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039648 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821422 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 33701 | 20230227 | 1641 | 20230306 | 1920 | 2021782 | 10239 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 20478 | 39.2131 | -121.0174 | Yes | Clear;32-90F |  |  | 23-0039649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821423 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9375 | 20230227 | 1653 | 20230303 | 2151 | 2015923 | 6058 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 157508 | 38.8463 | -120.7949 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0037494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819867 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9315 | 20230227 | 1653 | 20230302 | 1826 | 2018980 | 4413 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 105912 | 38.9114 | -120.8246 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038421 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820621 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | LD SIDE CGC 223349545405 | 20230227 | 1653 | 20230303 | 1232 | 2020463 | 5499 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 110316 | 38.9067 | -120.8237 | Yes | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0039040 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821031 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 20230227 | 1653 | 20230303 | 2151 | 2021563 | 6058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 121160 | 38.8528 | -120.789 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821349 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5591 | 20230227 | 1653 | 20230308 | 1654 | 2021569 | 12961 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 240117 | 38.8608 | -120.7883 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821351 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 1 S/O 5591 | 20230227 | 1653 | 20230308 | 1555 | 2021957 | 12902 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 289113 | 38.8605 | -120.7884 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821490 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 30875 | 20230227 | 1653 | 20230306 | 1655 | 2020078 | 10082 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 110902 | 39.1482 | -120.9083 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1820909 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6349 | 20230227 | 1655 | 20230305 | 1757 | 2013189 | 8702 | Distribution Circuit | Vegetation | Tree - grew into line | 129 | 1122558 | 39.1348 | -120.9227 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038234 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820460 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJS AT SAP ID 101393359 | 20230227 | 1656 | 20230227 | 2149 | 2013226 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2051 | 38.5423 | -120.7051 | Yes | Clear;Below 32 F | Conductor- Overhead | Burned/flashed | 23-0036673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819236 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20841 | 20230227 | 1700 | 20230227 | 1732 | 2012745 | 32 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 448 | 38.748 | -120.6416 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819264 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223524938552 | 20230227 | 1713 | 20230228 | 1730 | 2013224 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1995 | 38.7184 | -120.7647 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0036933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819477 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2015 | 20230227 | 1722 | 20230301 | 1836 | 2015894 | 2954 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 41356 | 38.5962 | -120.619 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037486 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819859 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 6623 | 20230227 | 1728 | 20230227 | 2120 | 2013300 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 3248 | 38.6876 | -120.638 | Yes |  | Conductor- Overhead | Normal | 23-0036928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819472 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1467 | 20230227 | 1754 | 20230228 | 1830 | 2013363 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13144 | 38.7047 | -120.7076 | Yes |  | Pole-Wood | Broken | 23-0036778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819320 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20230227 | 1809 | 20230228 | 1140 | 2013507 | 1051 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 43091 | 38.7404 | -120.6542 | Yes | Clear;32-90 F |  |  | 23-0037316 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819737 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ TWD CGC 222843057238 | 20230227 | 1818 | 20230305 | 1655 | 2022745 | 8557 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34228 | 39.234 | -120.9971 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken | 23-0040051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821794 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJS 1 SPAN SS/OF MTR 1009644023 | 20230227 | 1819 | 20230309 | 1445 | 2026999 | 14186 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14186 | 39.2362 | -120.9575 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0041333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822974 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 31765 | 20230227 | 1823 | 20230308 | 1639 | 2025869 | 12856 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 269976 | 39.2388 | -120.9608 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822671 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7853 | 20230227 | 1824 | 20230307 | 1336 | 2013536 | 11232 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 134784 | 39.2419 | -120.9628 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039990 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821746 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 8301 | 20230227 | 1839 | 20230227 | 1936 | 2013554 | 57 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 5928 | 39.213 | -121.0601 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0036753 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819307 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20230227 | 1844 | 20230301 | 1858 | 2013567 | 2894 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 69491 | 39.2095 | -120.827 | Yes | Clear;32-90 F | Lightning Arrestor | Broken | 23-0038443 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820637 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6355 | 20230227 | 1845 | 20230305 | 1805 | 2023967 | 8600 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 129000 | 39.1446 | -120.907 | Yes | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822154 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6365 | 20230227 | 1845 | 20230306 | 1719 | 2024702 | 9994 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 239856 | 39.1734 | -120.8591 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822371 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20230227 | 1846 | 20230306 | 1449 | 2013838 | 9843 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 2000519 | 39.1444 | -120.908 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0036731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819321 | 0 | EPSS Ckt | N | 2023 | SENS GRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5891 | 20230227 | 1849 | 20230228 | 1835 | 2013573 | 1426 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 27094 | 38.8911 | -120.8621 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819801 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20021 | 20230227 | 1855 | 20230228 | 1837 | 2015987 | 1422 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 9954 | 38.5897 | -120.605 | Yes | Clear;Below 32 F |  |  | 23-0037523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819882 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1351 | 20230227 | 1855 | 20230306 | 1416 | 2018969 | 9801 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 523646 | 38.5954 | -120.6169 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820617 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7385 | 20230227 | 1909 | 20230305 | 1827 | 2013640 | 8598 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 87726 | 39.2623 | -121.0131 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0036826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819369 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223837533500 | 20230227 | 2005 | 20230228 | 1504 | 2013753 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1139 | 38.5782 | -120.6586 | Yes | Clear;Below 32 F | Transformer (OH) | Broken- wire on ground | 23-0037156 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819633 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20230227 | 2028 | 20230306 | 1328 | 2013793 | 9660 | Distribution Circuit | Vegetation | Tree - fell into line | 1291 | 1993303 | 38.7617 | -120.5592 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0036774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819318 | 0 | EPSS Ckt | N | 2023 | A+GRD
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9721 | 20230227 | 2044 | 20230311 | 1606 | 2013834 | 17002 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 391046 | 39.1845 | -121.0471 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821058 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2653 | 20230227 | 2116 | 20230228 | 905 | 2014104 | 709 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 269 | 190721 | 38.6877 | -120.6388 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0037151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819628 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | JUMPER | OJ TWD MTR# 1007744961 | 20230227 | 2130 | 20230308 | 1654 | 2025925 | 12684 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 88788 | 39.2468 | -121.0308 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0041353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822684 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20230227 | 2247 | 20230311 | 1034 | 2013966 | 15701 | Distribution Circuit | Vegetation | Tree - fell into line | 634 | 2433519 | 39.5596 | -120.8241 | Yes |  | Pole-Wood | Broken- wire on ground | 23-0037025 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819564 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OTHER | WIRE DOWN @ CGC 222673659169 | 20230227 | 2248 | 20230305 | 1720 | 2013990 | 8312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1144 | 4071513 | 39.2875 | -121.0574 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037035 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1819569 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7131 | 20230227 | 2339 | 20230307 | 1643 | 2018163 | 11104 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 444160 | 39.2747 | -121.0477 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038103 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820360 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 9261 | 20230227 | 2339 | 20230306 | 1302 | 2024002 | 9443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 207746 | 39.2862 | -121.0551 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0040435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822166 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | JUMPER | TEMP C/OUT S/O MTR# 1006924602 | 20230227 | 2339 | 20230308 | 1521 | 2025921 | 12462 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 174468 | 39.2748 | -121.0409 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822683 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6907 | 20230227 | 2349 | 20230306 | 1753 | 2022916 | 9724 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 38896 | 38.9249 | -120.7875 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040085 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821830 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6913 | 20230227 | 2349 | 20230306 | 1754 | 2024544 | 9725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9725 | 38.9294 | -120.7663 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822342 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223442746067 | 20230227 | 2349 | 20230308 | 1518 | 2025015 | 12449 | Transformer only | Vegetation | Tree - fell into line | 1 | 12449 | 38.9253 | -120.7909 | Yes | Overcast-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 23-0040903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1822456 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223442746067 | 20230227 | 2349 | 20230308 | 1518 | 2025015 | 12449 | Transformer only | Vegetation | Tree - fell into line | 1 | 12449 | 38.9253 | -120.7909 | Yes | Overcast-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 23-0040903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1822456 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 97086 | 20230228 | 12 | 20230228 | 1310 | 2012648 | 778 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 349 | 266924 | 38.7652 | -120.7045 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037038 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819572 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 4115 | 20230228 | 26 | 20230307 | 1509 | 2014063 | 10963 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 100988 | 38.8659 | -120.822 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819895 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3957 | 20230228 | 722 | 20230306 | 1536 | 2022876 | 9134 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 164412 | 39.1854 | -121.0277 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040075 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821819 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 20230228 | 738 | 20230228 | 1250 | 2014990 | 312 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 62 | 19429 | 38.7959 | -120.7508 | Yes | Clear;32-90 F |  |  | 23-0037301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819728 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20230228 | 745 | 20230310 | 1704 | 2014302 | 14959 | Distribution Circuit | Environmental/External | Ice or snow | 157 | 1306904 | 39.4655 | -120.8443 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken | 23-0037093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819603 | 0 | EPSS Ckt | N | 2023 | A & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20511 | 20230228 | 815 | 20230228 | 1335 | 2014495 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 960 | 38.684 | -120.6587 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0037137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819623 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 34125 | 20230228 | 840 | 20230306 | 1629 | 2016102 | 9109 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9109 | 39.2683 | -121.0065 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037570 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1819917 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33147 | 20230228 | 840 | 20230306 | 1519 | 2022837 | 9039 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18078 | 39.2687 | -121.0068 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821813 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1507 | 20230228 | 843 | 20230228 | 1252 | 2014383 | 249 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 6474 | 38.7412 | -120.7227 | Yes | Clear;32-90 F |  |  | 23-0037406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819815 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20230228 | 931 | 20230228 | 951 | 2014662 | 20 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 178 | 3560 | 38.7138 | -120.6231 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819653 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7337 | 20230228 | 937 | 20230306 | 1651 | 2022463 | 9074 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 462774 | 39.2404 | -120.9894 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0039988 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821744 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9205 | 20230228 | 938 | 20230310 | 227 | 2022469 | 13969 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 502884 | 39.2457 | -120.9581 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821748 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1471 | 20230228 | 940 | 20230228 | 1208 | 2014700 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 4588 | 38.7418 | -120.6624 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0037340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819753 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7357 | 20230228 | 941 | 20230307 | 1600 | 2022466 | 10459 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 324595 | 39.2401 | -120.9818 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039989 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821745 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222302539821 | 20230228 | 946 | 20230228 | 1610 | 2014748 | 384 | Transformer only | Vegetation | Tree - fell into line | 1 | 384 | 38.7571 | -121.1936 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0037293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819720 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31959 | 20230228 | 953 | 20230302 | 1711 | 2018975 | 3318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 16590 | 39.0192 | -120.8225 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820619 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5901 | 20230228 | 953 | 20230303 | 1330 | 2020207 | 4537 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 90740 | 39.0467 | -120.7858 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820959 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30157 | 20230228 | 953 | 20230305 | 1620 | 2021370 | 7587 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 189675 | 39.0574 | -120.8005 | Yes | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821318 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30895 | 20230228 | 953 | 20230306 | 1644 | 2023998 | 9051 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 298683 | 39.0197 | -120.8247 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822164 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5929 | 20230228 | 955 | 20230304 | 1724 | 2018920 | 6209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 173852 | 39.0223 | -120.8097 | Yes | Overcast-Fog-Snow;Below 32 F | Other | Broken- wire on ground | 23-0038403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820600 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5925 | 20230228 | 955 | 20230302 | 1830 | 2020209 | 3395 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 16975 | 39.0331 | -120.797 | Yes | Clear;32-90 F |  |  | 23-0038954 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820961 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 313 | 20230228 | 955 | 20230305 | 1613 | 2020407 | 7578 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 22734 | 39.0563 | -120.7656 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0039031 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1821025 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6257 | 20230228 | 955 | 20230306 | 1616 | 2023958 | 9021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9021 | 39.0667 | -120.7695 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040420 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822153 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6001 | 20230228 | 955 | 20230306 | 1238 | 2021852 | 8803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 466559 | 39.0189 | -120.8614 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0039699 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821453 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1451 | 20230228 | 957 | 20230228 | 1608 | 2014988 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 16324 | 38.7595 | -120.7202 | Yes | Clear;32-90 F |  |  | 23-0037351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819760 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20953 | 20230228 | 959 | 20230228 | 1159 | 2014739 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 360 | 38.6247 | -120.57 | Yes | Clear;32-90 F |  |  | 23-0037288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819716 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2017 | 20230228 | 1010 | 20230301 | 1837 | 2014799 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 109032 | 38.6008 | -120.6417 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819865 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30899 | 20230228 | 1025 | 20230305 | 1608 | 2018911 | 7543 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 196118 | 39.0205 | -120.8136 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038400 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820597 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 5737 | 20230228 | 1053 | 20230306 | 1917 | 2015630 | 9144 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 36576 | 39.2594 | -121.0273 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0037401 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1819810 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33107 | 20230228 | 1053 | 20230307 | 1514 | 2018461 | 10341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 93069 | 39.2456 | -121.0203 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038256 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820474 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | JUMPER | OJ'S 1 SPAN SS OF CGC # 222807957651 | 20230228 | 1053 | 20230307 | 1150 | 2018789 | 10137 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 30411 | 39.2462 | -121.0097 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0038364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820553 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | JUMPER | OJ'S HIGH SIDE OF 36511 | 20230228 | 1053 | 20230307 | 1348 | 2018802 | 10255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 20510 | 39.2496 | -121.0246 | Yes | Overcast-Fog-Snow;Below 32 F | Cutout- fuse holder | Broken | 23-0038367 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820555 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 847033 | 20230228 | 1100 | 20230310 | 1709 | 2022753 | 14769 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 251073 | 39.2766 | -121.0247 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0040054 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821797 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7951 | 20230228 | 1134 | 20230306 | 1333 | 2021664 | 8759 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 43795 | 39.5716 | -120.823 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0039597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821376 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | JUMPER | OJ'S 1 SPAN SS OF 32475 | 20230228 | 1134 | 20230306 | 1319 | 2023838 | 8745 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34980 | 39.5705 | -120.8228 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822110 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 66267 | 20230228 | 1151 | 20230305 | 1744 | 2018952 | 7553 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 52871 | 39.0192 | -120.8257 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820611 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6003 | 20230228 | 1151 | 20230306 | 1352 | 2021853 | 8761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 8761 | 39.02 | -120.848 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0039700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821454 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6023 | 20230228 | 1151 | 20230305 | 1508 | 2021854 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 59176 | 38.9929 | -120.9242 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039701 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821455 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 7339 | 20230228 | 1151 | 20230306 | 1130 | 2022765 | 8619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 17238 | 39.0186 | -120.8773 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0040058 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821802 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5911 | 20230228 | 1154 | 20230302 | 1856 | 2018933 | 3302 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 112268 | 39.0213 | -120.8139 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820604 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 3977 | 20230228 | 1154 | 20230304 | 1914 | 2022766 | 6200 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 20 | 124000 | 39.0186 | -120.8843 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0040059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821803 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5923 | 20230228 | 1155 | 20230305 | 1827 | 2018966 | 7592 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 706056 | 39.0201 | -120.8181 | Yes | Overcast-Fog-Snow;Below 32 F | Pole - Tower- steel | Broken- wire on ground | 23-0038416 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820616 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 30261 | 20230228 | 1158 | 20230305 | 1725 | 2021857 | 7527 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 338715 | 38.986 | -120.9067 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821456 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 3479 | 20230228 | 1200 | 20230303 | 1459 | 2020148 | 4499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 98978 | 39.5606 | -120.8287 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0038919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820934 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 32469 | 20230228 | 1200 | 20230306 | 1319 | 2021666 | 8719 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17438 | 39.5713 | -120.8232 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0039598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821377 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9957 | 20230228 | 1208 | 20230228 | 1504 | 2015213 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 12320 | 38.5762 | -120.6628 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken | 23-0037337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819750 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8225 | 20230228 | 1216 | 20230310 | 1128 | 2024634 | 14352 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 489872 | 39.4541 | -121.0327 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822354 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 20230228 | 1216 | 20230309 | 1723 | 2024635 | 13267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 132670 | 39.4564 | -121.0375 | Yes | Overcast-Fog-Snow;32-90 F | Cutout- fuse holder | Broken | 23-0040694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822355 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12947 | 20230228 | 1217 | 20230228 | 1423 | 2015383 | 126 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 12474 | 38.7516 | -120.6928 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819816 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21407 | 20230228 | 1217 | 20230306 | 1510 | 2015386 | 8813 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 105756 | 38.7116 | -120.6263 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken | 23-0037574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819918 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9235 | 20230228 | 1217 | 20230306 | 1357 | 2015406 | 8740 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 390769 | 38.9217 | -120.8957 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039964 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821718 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 32449 | 20230228 | 1218 | 20230310 | 1906 | 2020076 | 14808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 592320 | 39.5403 | -120.8846 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Deteriorated | 23-0038872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820907 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | OCB | 1101/2 | 20230228 | 1220 | 20230309 | 1645 | 2017699 | 13225 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 2769836 | 39.4382 | -120.9964 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820265 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 920859 | 20230228 | 1223 | 20230307 | 1352 | 2018231 | 10169 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 40676 | 39.3663 | -121.0374 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0038415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820614 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6343 | 20230228 | 1235 | 20230305 | 1726 | 2018406 | 7491 | Distribution Circuit | Company Initiated | Personnel- company | 11 | 82401 | 39.1277 | -120.939 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038231 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820457 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12221 | 20230228 | 1244 | 20230228 | 1351 | 2015587 | 67 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 2613 | 38.7476 | -120.6412 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0037390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819797 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 20230228 | 1245 | 20230306 | 1550 | 2015672 | 8825 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 347669 | 38.7941 | -120.7143 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1819822 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18543 | 20230228 | 1258 | 20230303 | 1836 | 2015639 | 4658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 74528 | 38.7517 | -120.6921 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819847 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12629 | 20230228 | 1303 | 20230305 | 1630 | 2015651 | 7407 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 185175 | 38.7928 | -120.7012 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819928 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20230228 | 1303 | 20230306 | 1609 | 2015734 | 8826 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 322336 | 39.3823 | -121.0478 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038299 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820501 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12627 | 20230228 | 1304 | 20230305 | 1616 | 2015654 | 7392 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22176 | 38.7925 | -120.7023 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0037580 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819922 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 9695 | 20230228 | 1307 | 20230228 | 1410 | 2015659 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 630 | 38.7408 | -120.6916 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819853 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33739 | 20230228 | 1310 | 20230310 | 1610 | 2020486 | 14580 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 116640 | 39.1716 | -121.0295 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821041 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 20230228 | 1315 | 20230228 | 1557 | 2015675 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 10088 | 38.7959 | -120.7508 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819900 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 5655 | 20230228 | 1323 | 20230305 | 1540 | 2018447 | 7337 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 234784 | 38.7977 | -120.7123 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038249 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820471 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33319 | 20230228 | 1323 | 20230306 | 1602 | 2018413 | 8799 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 70392 | 39.1339 | -120.9411 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038237 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820462 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20637 | 20230228 | 1329 | 20230305 | 1625 | 2015711 | 7376 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 81136 | 38.8 | -120.7004 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0037585 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819925 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 3647 | 20230228 | 1331 | 20230304 | 1501 | 2020053 | 5850 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 52650 | 39.2465 | -121.0375 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0038856 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820896 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6347 | 20230228 | 1331 | 20230306 | 1524 | 2018407 | 8753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 166307 | 39.135 | -120.9242 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038233 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820459 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 74973 | 20230228 | 1338 | 20230308 | 1420 | 2015745 | 11562 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28932 | 39.2249 | -121.1717 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038424 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820624 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | JUMPER | WIRE DOWN 1 SPAN E/OF 33943 | 20230228 | 1349 | 20230228 | 1631 | 2015773 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 14940 | 39.0222 | -120.9558 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | Yes | 1819837 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | RECLOSER | 1070 | 20230228 | 1351 | 20230301 | 1846 | 2015806 | 1735 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 423430 | 39.0212 | -121.0599 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1819843 | 0 | EPSS Ckt | N | 2023 | A B GRD
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6917 | 20230228 | 1353 | 20230228 | 1712 | 2015873 | 199 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 4179 | 38.8721 | -120.8333 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0037602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819939 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223935937618 | 20230228 | 1357 | 20230228 | 1458 | 2015820 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 183 | 38.6919 | -120.6219 | Yes | Clear;32-90 F |  |  | 23-0037462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819845 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20230228 | 1358 | 20230228 | 1636 | 2015812 | 158 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 6478 | 38.7404 | -120.6542 | Yes | Partly Cloudy-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037561 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819909 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223327956367 | 20230228 | 1425 | 20230305 | 1637 | 2015866 | 7332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 14664 | 39.2085 | -120.8267 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0038920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820937 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 22603 | 20230228 | 1437 | 20230228 | 1811 | 2015912 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 428 | 38.7422 | -121.0605 | Yes | Clear;32-90 F |  |  | 23-0037660 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819998 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7147 | 20230228 | 1459 | 20230303 | 1355 | 2017097 | 4256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 114912 | 39.2454 | -121.0566 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 23-0039419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821278 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 4885 | 20230228 | 1511 | 20230303 | 1257 | 2016265 | 4097 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1278 | 1535156 | 39.22 | -121.0605 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819948 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 5485 | 20230228 | 1517 | 20230303 | 1258 | 2016014 | 4181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 405557 | 39.1755 | -121.0947 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1820945 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK 1102 | 152301102 | FUSE | 6411 | 20230228 | 1530 | 20230228 | 1725 | 2013586 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 11040 | 39.2096 | -120.8014 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819907 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 22821 | 20230228 | 1539 | 20230302 | 1148 | 2016446 | 2649 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7947 | 38.6247 | -120.5712 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820003 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1507 | 20230228 | 1542 | 20230301 | 2132 | 2016057 | 1790 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 46540 | 38.7412 | -120.7227 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819954 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223363856553 | 20230228 | 1609 | 20230305 | 1838 | 2016134 | 7349 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 29396 | 39.2134 | -120.8139 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0038850 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820890 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 4935 | 20230228 | 1616 | 20230302 | 1858 | 2016159 | 3042 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 97291 | 39.1227 | -121.053 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038585 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820748 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | FUSE | 20249 | 20230228 | 1617 | 20230228 | 1747 | 2016160 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1620 | 38.6557 | -120.9739 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0037637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819974 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 20230228 | 1620 | 20230305 | 1854 | 2016167 | 7354 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 85019 | 39.2024 | -120.8369 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1819949 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 8973 | 20230228 | 1622 | 20230302 | 1511 | 2016172 | 2809 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 22472 | 39.1654 | -121.0808 | Yes | Clear;32-90F |  |  | 23-0038867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820903 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230228 | 1641 | 20230304 | 902 | 2016226 | 5301 | Distribution Circuit | Vegetation | Tree - fell into line | 2121 | 904643 | 39.0997 | -121.05 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819947 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222696254113 | 20230228 | 1641 | 20230308 | 1719 | 2016330 | 11558 | Transformer only | Vegetation | Tree - fell into line | 4 | 46232 | 39.1484 | -121.0502 | Yes | Overcast-Snow;32-90 F | Service conductor | Broken- wire on ground | 23-0037626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819963 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 35867 | 20230228 | 1643 | 20230304 | 1151 | 2019945 | 5468 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 76552 | 38.9119 | -120.8623 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820873 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12842 | 20230228 | 1657 | 20230228 | 1852 | 2014997 | 64 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 60260 | 38.7536 | -120.6799 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819952 | 0 | EPSS Ckt | N | 2023 | B+C
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 585766 | 20230228 | 1659 | 20230302 | 1506 | 2016289 | 2767 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 588961 | 39.0992 | -120.95 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 23-0037385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1819953 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | JUMPER | WIRE DOWN 1 LD SIDE OF CGC#222988552273 | 20230228 | 1659 | 20230305 | 1355 | 2018399 | 7016 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14003 | 39.0974 | -120.9483 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1820450 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 59345 | 20230228 | 1702 | 20230302 | 1457 | 2016304 | 2755 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 217645 | 39.0995 | -120.9506 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0037385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1820915 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6381 | 20230228 | 1704 | 20230228 | 1915 | 2016295 | 131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 3930 | 39.0923 | -120.9499 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0037692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820025 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 69880 | 20230228 | 1707 | 20230304 | 1025 | 2016335 | 5358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 91086 | 39.0808 | -120.9419 | Yes | Clear;32-90 F |  |  | 23-0039934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1821693 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 8707 | 20230228 | 1710 | 20230302 | 1218 | 2016317 | 2588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 82816 | 39.0409 | -120.94 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0038767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820846 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20230228 | 1710 | 20230302 | 1457 | 2016324 | 2747 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 445014 | 38.8995 | -120.8545 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819962 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 6593 | 20230228 | 1710 | 20230305 | 1520 | 2018904 | 7090 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 85110 | 38.9136 | -120.8387 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038398 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820594 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9373 | 20230228 | 1710 | 20230302 | 1656 | 2020067 | 2866 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 71650 | 38.9134 | -120.8373 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0038868 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820904 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9393 | 20230228 | 1710 | 20230305 | 1518 | 2020126 | 7088 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 85056 | 38.9086 | -120.8486 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821063 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 6255 | 20230228 | 1710 | 20230303 | 1652 | 2020562 | 4302 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 77436 | 38.9115 | -120.8539 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0039075 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821064 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33317 | 20230228 | 1711 | 20230306 | 1721 | 2023974 | 8650 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 86500 | 39.1341 | -120.9408 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822159 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 9861 | 20230228 | 1722 | 20230304 | 1252 | 2017292 | 5490 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 76860 | 39.2453 | -121.0378 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820196 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 35861 | 20230228 | 1723 | 20230303 | 1652 | 2019929 | 4289 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 90069 | 38.9081 | -120.8563 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Normal | 23-0038813 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820872 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 11933 | 20230228 | 1743 | 20230304 | 1625 | 2016362 | 5682 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 270238 | 38.6952 | -120.6095 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820172 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6411 | 20230228 | 1750 | 20230301 | 1114 | 2016386 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 100224 | 39.2096 | -120.8014 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819986 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 649463 | 20230228 | 1751 | 20230304 | 944 | 2019465 | 5273 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5273 | 38.7146 | -120.606 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0038604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820759 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | JUMPER | OJ'S FEEDING CGC 222965052436 | 20230228 | 1813 | 20230305 | 1308 | 2016452 | 6895 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 34475 | 39.101 | -120.9563 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0040297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822035 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223332556465 | 20230228 | 1826 | 20230302 | 1702 | 2016307 | 2796 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2796 | 39.2102 | -120.825 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0038983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820984 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | TRANSFORMER | 222913835974 | 20230228 | 1850 | 20230301 | 1625 | 2016484 | 1295 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1295 | 38.6495 | -120.9802 | Yes | Clear;32-90 F |  |  | 23-0038046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 20230228 | 1851 | 20230305 | 1435 | 2016799 | 6944 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 302432 | 39.2024 | -120.8369 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1820328 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8573 | 20230228 | 1859 | 20230303 | 1625 | 2016499 | 4166 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 133356 | 38.902 | -120.8586 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820085 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5891 | 20230228 | 1903 | 20230301 | 1433 | 2016498 | 1170 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 22230 | 38.8911 | -120.8621 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0037679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820016 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6375 | 20230228 | 1926 | 20230302 | 1110 | 2016768 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 171056 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038049 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820322 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 32581 | 20230228 | 1928 | 20230303 | 2024 | 2017553 | 4376 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26256 | 39.211 | -121.0567 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820478 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 8015 | 20230228 | 1930 | 20230304 | 1746 | 2017784 | 5656 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 28280 | 38.7587 | -120.6789 | Yes | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0037958 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820276 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 7281 | 20230228 | 1946 | 20230302 | 836 | 2016759 | 2210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 86 | 190060 | 39.2169 | -121.0516 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038600 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820758 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20619 | 20230228 | 1949 | 20230304 | 1952 | 2019689 | 5763 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 103734 | 38.7219 | -120.6608 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820807 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224070235845 | 20230228 | 1949 | 20230305 | 1657 | 2021311 | 7028 | Transformer only | Equipment Failure/Involved | Electrical Overload | 16 | 9293 | 38.6419 | -120.5754 | Yes | Clear;32-90 F | Transformer | Broken | 23-0039466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1821307 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223924238369 | 20230228 | 1949 | 20230307 | 1439 | 2024851 | 9770 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 9770 | 38.7112 | -120.6259 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer | Broken | 23-0040825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822414 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1433 | 20230228 | 1952 | 20230302 | 1115 | 2019259 | 2363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 11815 | 38.7502 | -120.7568 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038536 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820719 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20849 | 20230228 | 1952 | 20230306 | 1200 | 2018251 | 8168 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 98016 | 38.7509 | -120.6914 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820386 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 9123 | 20230228 | 1952 | 20230303 | 1836 | 2018682 | 4244 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29708 | 38.7569 | -120.693 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820527 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12947 | 20230228 | 1952 | 20230303 | 1845 | 2018806 | 4253 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 106325 | 38.7516 | -120.6928 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820558 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18579 | 20230228 | 1952 | 20230303 | 1247 | 2018887 | 3895 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27265 | 38.7393 | -120.6685 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820588 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20635 | 20230228 | 1952 | 20230305 | 1615 | 2021588 | 6983 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 55864 | 38.797 | -120.7001 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821360 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18545 | 20230228 | 1952 | 20230304 | 930 | 2021813 | 5138 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 113036 | 38.7535 | -120.6976 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0039674 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821434 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20230228 | 1953 | 20230304 | 1838 | 2017050 | 5685 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 773748 | 38.7138 | -120.6231 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820089 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32285 | 20230228 | 1953 | 20230302 | 848 | 2016622 | 2215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 59805 | 39.2286 | -121.0968 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820379 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 9847 | 20230228 | 1954 | 20230304 | 1414 | 2018820 | 5420 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 439020 | 38.7542 | -120.6596 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820565 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 20641 | 20230228 | 1954 | 20230305 | 1615 | 2021095 | 6981 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 167544 | 38.8009 | -120.6955 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039366 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821244 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13817 | 20230228 | 1954 | 20230302 | 1148 | 2018928 | 2394 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 59850 | 38.6215 | -120.5877 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0038405 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820603 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32287 | 20230228 | 1954 | 20230307 | 1649 | 2016631 | 9895 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 98950 | 39.2277 | -121.0967 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820377 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRIP-SAVER | 3907 | 20230228 | 1954 | 20230302 | 1842 | 2016633 | 2808 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 398736 | 39.2223 | -121.0816 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038659 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820786 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18547 | 20230228 | 1955 | 20230303 | 1852 | 2018497 | 4257 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 221364 | 38.7546 | -120.6998 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820484 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 20230228 | 1955 | 20230305 | 1649 | 2019571 | 7014 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 453930 | 38.7911 | -120.7022 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820779 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12633 | 20230228 | 1955 | 20230305 | 1743 | 2021753 | 7068 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 106020 | 38.8036 | -120.699 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821411 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 20230228 | 1955 | 20230304 | 1838 | 2018204 | 5683 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 107977 | 38.7136 | -120.632 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820374 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 6641 | 20230228 | 1957 | 20230302 | 1826 | 2019025 | 2789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 47413 | 38.7454 | -120.6779 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0038434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820633 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ LINE & BUCK S/S CGC 223834436887 | 20230228 | 2000 | 20230301 | 2045 | 2018905 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1485 | 38.6712 | -120.6568 | Yes | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1820595 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10497 | 20230228 | 2014 | 20230303 | 1035 | 2018675 | 3741 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 44919 | 38.7319 | -120.6758 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820524 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32639 | 20230228 | 2031 | 20230308 | 1122 | 2018827 | 10971 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 43884 | 39.236 | -121.0601 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820848 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18917 | 20230228 | 2056 | 20230304 | 1952 | 2022187 | 5696 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 28480 | 38.7225 | -120.6428 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken | 23-0039897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821658 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL SUB | 15366 | OTHER | APPLE HILL | 20230228 | 2103 | 20230306 | 1510 | 2017066 | 8287 | Distribution Circuit | Vegetation | Tree - fell into line | 4296 | 3743866 | 0 | 0 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0037791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1820119 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18453 | 20230228 | 2103 | 20230302 | 1633 | 2019214 | 2610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 28710 | 38.7412 | -120.6977 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820695 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 20230228 | 2103 | 20230302 | 1805 | 2017080 | 2702 | Distribution Circuit | Environmental/External | Ice or snow | 1895 | 3682342 | 38.7393 | -120.6773 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820160 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22073 | 20230228 | 2103 | 20230303 | 942 | 2018867 | 3639 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 90975 | 38.7381 | -120.6736 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038389 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820579 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22075 | 20230228 | 2103 | 20230303 | 911 | 2018869 | 3608 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 54120 | 38.7384 | -120.673 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820581 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18577 | 20230228 | 2103 | 20230303 | 1001 | 2018974 | 3658 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 91450 | 38.74 | -120.6708 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820618 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 9843 | 20230228 | 2103 | 20230303 | 1131 | 2019970 | 3748 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 119936 | 38.7532 | -120.6499 | Yes | Overcast-Fog-Snow;32-90 F | Insulator | Broken | 23-0038833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820879 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9519 | 20230228 | 2103 | 20230304 | 1952 | 2018194 | 5689 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 699747 | 38.7148 | -120.6676 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820371 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13245 | 20230228 | 2103 | 20230302 | 1340 | 2018268 | 2437 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 60925 | 38.701 | -120.6688 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038169 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820400 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 20230228 | 2103 | 20230301 | 2045 | s1820438 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 21330 | 38.6765 | -120.6617 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820438 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12169 | 20230228 | 2103 | 20230303 | 1243 | 2018387 | 3820 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 57300 | 38.6445 | -120.5662 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820443 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 20230228 | 2103 | 20230304 | 1017 | 2017070 | 5114 | Distribution Circuit | Vegetation | Tree - fell into line | 2723 | 6847351 | 38.7934 | -120.62 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 23-0036774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820125 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20230228 | 2103 | 20230302 | 1645 | 2017072 | 2622 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1638 | 4281199 | 38.7934 | -120.6201 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820131 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | JUMPER | OJS @ CGC 224006940584 | 20230228 | 2103 | 20230303 | 1035 | 2020147 | 3692 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 33228 | 38.7722 | -120.5954 | Yes | Clear;32-90 F | Insulator | Broken | 23-0038918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820933 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 4595 | 20230228 | 2108 | 20230305 | 1605 | 2020302 | 6897 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 255189 | 38.6981 | -120.6039 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820994 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20230228 | 2108 | 20230303 | 1239 | 2017028 | 3811 | Distribution Circuit | Vegetation | Tree - fell into line | 592 | 959771 | 39.0443 | -120.9859 | Yes | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820102 | 0 | EPSS Ckt | N | 2023 | GRD
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1471 | 20230228 | 2110 | 20230304 | 1518 | 2018807 | 5408 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 167648 | 38.7418 | -120.6624 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820559 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7263 | 20230228 | 2134 | 20230228 | 2322 | 2017204 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 8640 | 39.2147 | -121.0803 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0037857 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820185 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6327 | 20230228 | 2138 | 20230305 | 1946 | 2017085 | 7088 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 141760 | 39.1143 | -120.9531 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1821663 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4955 | 20230228 | 2145 | 20230304 | 1715 | 2017089 | 5490 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 65880 | 38.8781 | -120.8937 | Yes | Clear;32-90 F |  |  | 23-0040049 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1821793 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5889 | 20230228 | 2147 | 20230306 | 1042 | 2017078 | 7975 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 75713 | 38.8776 | -120.8667 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821759 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | JUMPER | OJ W/OF 222685057690 | 20230228 | 2148 | 20230305 | 1618 | 2021421 | 6870 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 233580 | 39.2463 | -121.0532 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken | 23-0039507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821330 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 20230228 | 2154 | 20230303 | 1303 | 2017101 | 3789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22734 | 39.3753 | -121.0378 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0039548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1821348 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY 1102 | 152031102 | FUSE | 7507 | 20230228 | 2206 | 20230303 | 1943 | 2017113 | 4177 | Distribution Circuit | Equipment Failure/Involved | Underground | 96 | 204299 | 39.2183 | -121.0638 | Yes | Overcast-Fog-Snow;32-90 F | Transformer (UG) | Failed/Faulted | 23-0039066 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1821056 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 44383 | 20230228 | 2208 | 20230303 | 937 | 2017141 | 3569 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3569 | 38.899 | -120.9148 | Yes | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820173 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 779861 | 20230228 | 2305 | 20230303 | 1154 | 2021190 | 3649 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 102172 | 39.2633 | -121.0493 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0039421 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821280 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRIP-SAVER | 7181 | 20230228 | 2316 | 20230302 | 1651 | 2020051 | 2495 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 109780 | 39.2455 | -121.0444 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038855 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820895 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 32747 | 20230228 | 2356 | 20230302 | 1621 | 2017274 | 2425 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 373450 | 39.1426 | -121.0613 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1820503 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 96011 | 20230301 | 134 | 20230303 | 1603 | 2017471 | 3749 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 167575 | 38.8989 | -120.8591 | No | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1821059 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222649956742 | 20230301 | 555 | 20230309 | 926 | 2017594 | 11731 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 93848 | 39.2209 | -121.0658 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0038779 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820855 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1037 | 20230301 | 620 | 20230301 | 1118 | 2017630 | 298 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 57216 | 38.7018 | -120.8451 | No | Partly Cloudy;Below 32 F |  |  | 23-0038083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820346 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8067 | 20230301 | 637 | 20230303 | 1235 | 2017650 | 3238 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 29142 | 38.8732 | -120.8739 | No | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0039384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1821249 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7463 | 20230301 | 1000 | 20230310 | 1513 | 2024161 | 13273 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 185822 | 39.1647 | -120.9696 | No | Clear;Below 32 F |  |  | 23-0040526 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822261 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3773 | 20230301 | 1026 | 20230306 | 1800 | 2018606 | 7654 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 15308 | 38.8839 | -120.83 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0038308 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1820508 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9303 | 20230301 | 1026 | 20230302 | 1914 | 2018613 | 1968 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 17039 | 38.9074 | -120.836 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0038313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820510 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31145 | 20230301 | 1026 | 20230302 | 1540 | 2018871 | 1754 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8770 | 38.8524 | -120.836 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820582 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 8583 | 20230301 | 1026 | 20230305 | 1207 | 2019179 | 5861 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 52749 | 38.8979 | -120.8296 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0038486 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820672 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223317145434 | 20230301 | 1026 | 20230303 | 1151 | 2020535 | 2965 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2965 | 38.9082 | -120.8351 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0039063 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821053 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 33759 | 20230301 | 1118 | 20230301 | 1307 | 2018157 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 654 | 39.1453 | -121.0447 | No | Clear;32-90 F |  |  | 23-0038215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820440 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6451 | 20230301 | 1142 | 20230301 | 1401 | 2018193 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 556 | 39.2127 | -120.7812 | No | Clear;32-90F |  |  | 23-0038119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820370 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 7353 | 20230301 | 1520 | 20230301 | 1620 | 2018623 | 60 | Distribution Circuit | Environmental/External | Ice or snow | 12 | 720 | 39.2125 | -120.8167 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820514 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | SHADY GLEN-1102 | 152431102 | FUSE | 7173 | 20230301 | 1533 | 20230301 | 1614 | 2018604 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 902 | 39.1587 | -120.9693 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1820532 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | SWITCH | 489767 | 20230301 | 1623 | 20230301 | 1640 | 2018979 | 17 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 408 | 39.373 | -120.9951 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0038420 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1820620 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2015 | 20230301 | 1846 | 20230307 | 1350 | 2019037 | 8344 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 107088 | 38.5962 | -120.619 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038460 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1820648 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20230301 | 2001 | 20230302 | 1133 | 2019153 | 932 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 22379 | 39.2095 | -120.827 | No | Clear;32-90F |  |  | 23-0038757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820839 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1521 | 20230301 | 2016 | 20230303 | 1510 | 2019174 | 2574 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 105534 | 38.741 | -120.6619 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038489 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820674 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20230301 | 2024 | 20230304 | 1746 | 2019177 | 4162 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 113403 | 38.7404 | -120.6542 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1821274 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7919 | 20230301 | 2029 | 20230303 | 1658 | 2019182 | 2669 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 170816 | 38.7507 | -120.632 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0039072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821061 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223807439397 | 20230301 | 2110 | 20230303 | 1041 | 2019217 | 2251 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 11255 | 38.7406 | -120.6661 | No | Clear;32-90 F |  |  | 23-0039391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821253 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 18381 | 20230301 | 2124 | 20230302 | 1053 | 2019232 | 809 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 27 | 22091 | 38.7347 | -120.7846 | No | Clear;32-90 F |  |  | 23-0038678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820795 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30813 | 20230301 | 2142 | 20230303 | 1313 | 2019244 | 2371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 21339 | 38.8876 | -120.8304 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820968 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 20230301 | 2151 | 20230304 | 1057 | 2019252 | 3666 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 40326 | 38.8791 | -120.8335 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039016 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821011 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 63823 | 20230301 | 2259 | 20230302 | 1854 | s1820928 | 1195 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 55432 | 38.859 | -120.8472 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1820928 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | T3076 | 20230302 | 30 | 20230307 | 1650 | 2019312 | 8180 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 24540 | 39.2696 | -121.0243 | No | Clear;32-90F | Fuse | Burned Open | 23-0041340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822677 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223793639402 | 20230302 | 740 | 20230303 | 1106 | 2019410 | 1646 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 6584 | 38.7407 | -120.6714 | No | Clear;32-90F |  |  | 23-0039407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821264 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 20230302 | 823 | 20230302 | 1603 | 2019450 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9200 | 38.7853 | -120.6077 | No | Clear;32-90F | Conductor- Overhead | On Ground | 23-0038879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1820910 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 23279 | 20230302 | 835 | 20230302 | 1727 | 2019972 | 532 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 2128 | 38.6779 | -121.0259 | No | Clear;32-90 F |  |  | 23-0038985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820985 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31339 | 20230302 | 924 | 20230304 | 1757 | 2019544 | 3393 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 10179 | 38.895 | -120.9936 | No | Clear;32-90 F |  |  | 23-0040061 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 99087 | 20230302 | 944 | 20230302 | 1653 | 2019661 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 429 | 39.1914 | -120.8315 | No | Clear;32-90F | Lightning Arrestor | Broken | 23-0038688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820802 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ'S SS OF CGC 222853162904 | 20230302 | 957 | 20230307 | 1649 | 2019584 | 7612 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 30448 | 39.3896 | -120.9918 | No | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0039562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821358 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8047 | 20230302 | 1050 | 20230302 | 1540 | 2019665 | 290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3190 | 39.1556 | -121.0393 | No | Clear;32-90 F |  |  | 23-0038921 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1820938 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 31573 | 20230302 | 1115 | 20230303 | 1018 | 2019713 | 1383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4149 | 38.8106 | -121.1916 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0038717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1820815 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 20230302 | 1207 | 20230303 | 1657 | 2019784 | 1730 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 102070 | 38.6204 | -120.6018 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039012 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1821008 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13817 | 20230302 | 1210 | 20230302 | 1439 | 2019793 | 149 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 3725 | 38.6215 | -120.5877 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0038847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820888 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3815 | 20230302 | 1221 | 20230308 | 1143 | 2019808 | 8602 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 60214 | 38.915 | -120.8277 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0038778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1820854 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9991 | 20230302 | 1227 | 20230305 | 1811 | 2019815 | 4664 | Distribution Circuit | Vegetation | Tree - bark fell into line | 20 | 93280 | 38.9124 | -120.8292 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0040304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822041 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20953 | 20230302 | 1232 | 20230305 | 1249 | 2019821 | 4337 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13011 | 38.6247 | -120.57 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1821254 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | TRANSFORMER | 222935050163 | 20230302 | 1300 | 20230305 | 1535 | 2018207 | 4475 | Transformer only | Environmental/External | Ice or snow | 3 | 13425 | 39.0392 | -120.968 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0038820 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1820875 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5681 | 20230302 | 1400 | 20230305 | 1200 | 2021085 | 4200 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8400 | 39.0095 | -120.8449 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0040332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822062 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 31185 | 20230302 | 1415 | 20230302 | 1932 | 2019987 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 951 | 39.1897 | -120.85 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0039073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821062 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7179 | 20230302 | 1427 | 20230302 | 1746 | 2020032 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 11144 | 39.2418 | -121.0544 | No | Overcast-Fog-Snow;Below 32 F | Service conductor | Broken- wire on ground | 23-0038849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1820889 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20230302 | 1611 | 20230303 | 1510 | 2020454 | 1379 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 25754 | 38.7533 | -120.6117 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821037 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222743057631 | 20230302 | 1630 | 20230303 | 1733 | 2020225 | 1503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3006 | 39.2448 | -121.0327 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0038978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820979 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 5357 | 20230302 | 1631 | 20230308 | 1937 | 2020934 | 8826 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 150042 | 39.3711 | -120.996 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0039566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821361 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12617 | 20230302 | 1722 | 20230304 | 1924 | 2020306 | 3002 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 54036 | 38.8068 | -120.7467 | No | Clear;32-90F | Pole-Wood | Broken | 23-0039611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821394 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224092939774 | 20230302 | 1733 | 20230303 | 1224 | 2020323 | 1131 | Transformer only | Environmental/External | Ice or snow | 2 | 2262 | 38.7496 | -120.5655 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0039459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821303 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222735562820 | 20230302 | 1744 | 20230307 | 1119 | 2020343 | 6815 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6815 | 39.3879 | -121.0329 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0039446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821294 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6735 | 20230302 | 1856 | 20230303 | 1147 | 2020503 | 1011 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 208 | 210393 | 39.3118 | -120.3859 | No | Clear;32-90 F |  |  | 23-0039430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821285 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3935 | 20230302 | 1927 | 20230305 | 1428 | 2020547 | 4021 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 48252 | 39.1521 | -121.0255 | No | Partly Cloudy;32-90 F |  |  | 23-0040379 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822105 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 114670 | 20230302 | 1932 | 20230307 | 1749 | 2025913 | 7097 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 40 | 283880 | 39.1707 | -121.0508 | No | Partly Cloudy;32-90 F |  |  | 23-0041349 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822681 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9395 | 20230302 | 2025 | 20230305 | 1917 | 2020594 | 4252 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 42520 | 38.9124 | -120.836 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1821800 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 20230303 | 623 | 20230304 | 1519 | 2020768 | 1976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 123047 | 38.7959 | -120.7508 | No | Overcast;32-90 F | Insulator | Burned/flashed | 23-0039823 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821590 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230303 | 717 | 20230303 | 1340 | 2021298 | 383 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1040 | 393168 | 38.7391 | -120.6681 | No | Overcast;32-90 F |  |  | 23-0037831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821317 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222987352275 | 20230303 | 732 | 20230304 | 1429 | 2020780 | 1857 | Transformer only | Vegetation | Tree - fell into line | 3 | 5571 | 39.0974 | -120.9488 | No | Clear;32-90 F | Transformer | Normal | 23-0039916 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821672 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 20230303 | 1015 | 20230303 | 1050 | 2021571 | 35 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 210 | 39.3753 | -121.0378 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821353 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 37335 | 20230303 | 1037 | 20230303 | 1202 | 2020891 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 595 | 39.1743 | -120.8299 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0039278 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821200 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223165648250 | 20230303 | 1109 | 20230306 | 1548 | 2021167 | 4599 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 4599 | 38.9862 | -120.8875 | No | Clear;32-90F |  |  | 23-0040855 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822421 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 35453 | 20230303 | 1147 | 20230303 | 1207 | 2021236 | 20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 20 | 39.2395 | -121.0488 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821288 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20230303 | 1155 | 20230307 | 1744 | 2019272 | 6109 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42763 | 38.7521 | -120.6282 | No | Clear;Below 32 F | Conductor- Overhead | Broken | 23-0039445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821293 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222756454934 | 20230303 | 1203 | 20230310 | 1735 | 2021253 | 10412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22587 | 39.1708 | -121.0289 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040398 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822134 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31943 | 20230303 | 1232 | 20230303 | 1926 | 2021305 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 414 | 39.0078 | -120.8484 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821347 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6737 | 20230303 | 1241 | 20230303 | 1350 | 2021330 | 69 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 173 | 11937 | 39.3043 | -120.3887 | No | Clear;32-90F |  |  | 23-0039502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821328 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6341 | 20230303 | 1244 | 20230303 | 1625 | 2021336 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 12597 | 39.125 | -120.9435 | No | Partly Cloudy;32-90 F |  |  | 23-0039588 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821371 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ'S LD SD 222841062833 | 20230303 | 1303 | 20230307 | 1538 | 2021581 | 5915 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5915 | 39.3881 | -120.9964 | No | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0039558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821355 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 33737 | 20230303 | 1309 | 20230310 | 1533 | 2021366 | 10224 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 327168 | 39.1744 | -121.0296 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823113 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20230303 | 1355 | 20230303 | 1730 | 2021541 | 215 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 4515 | 39.0543 | -120.7583 | No | Clear;32-90F |  |  | 23-0039596 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821375 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30813 | 20230303 | 1413 | 20230303 | 1431 | 2021476 | 18 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 162 | 38.8876 | -120.8304 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0041195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822626 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31947 | 20230303 | 1418 | 20230306 | 1737 | 2022394 | 4519 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 49709 | 39.0083 | -120.8475 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0040361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822086 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224559060000 | 20230303 | 1537 | 20230303 | 1750 | 2021618 | 133 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 399 | 39.3031 | -120.3899 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0039632 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821410 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJ TWD CGC 223844739625 | 20230303 | 1651 | 20230304 | 1130 | 2021684 | 1119 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1119 | 38.7471 | -120.6521 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039607 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821388 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | WIRE DOWN | 20230303 | 1855 | 20230305 | 1505 | 2021827 | 2650 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2650 | 39.1368 | -120.9214 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039960 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1821715 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | SWITCH | 12639 | 20230303 | 1920 | 20230304 | 1924 | 2021837 | 1444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 187720 | 38.7892 | -120.7073 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0039692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821447 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223702039930 | 20230303 | 1921 | 20230304 | 1005 | 2021851 | 884 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 3536 | 38.7557 | -120.7029 | No | Clear;32-90 F |  |  | 23-0039918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821675 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223952037797 | 20230303 | 1950 | 20230304 | 911 | 2021873 | 801 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 801 | 38.6957 | -120.6163 | No | Clear;32-90F | Fuse | Normal | 23-0039901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821659 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223704339930 | 20230303 | 2015 | 20230304 | 1008 | 2021921 | 833 | Transformer only | Vegetation | Tree - fell into line | 1 | 833 | 38.7557 | -120.7023 | No | Clear;32-90 F | Service conductor | Normal | 23-0039922 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821679 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 97873 | 20230304 | 329 | 20230304 | 1002 | s1821670 | 393 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1965 | 39.2977 | -120.3788 | No | Clear;32-90 F |  |  | 23-0039914 |  | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821670 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31941 | 20230304 | 647 | 20230306 | 1328 | 2022086 | 3281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 9843 | 39.0071 | -120.8514 | No | Clear;32-90F |  |  | 23-0040765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1822388 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223168547708 | 20230304 | 648 | 20230305 | 1918 | 2022087 | 2190 | Transformer only | Vegetation | Tree - fell into line | 2 | 4380 | 38.9716 | -120.8862 | No | Clear;32-90 F | Transformer | Broken | 23-0039885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821648 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223882837452 | 20230304 | 812 | 20230304 | 1000 | 2022144 | 108 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 216 | 38.687 | -120.6404 | No | Clear;32-90 F |  |  | 23-0039920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821677 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223699539970 | 20230304 | 1007 | 20230304 | 1302 | 2022227 | 175 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 350 | 38.7565 | -120.704 | No | Clear;32-90 F | Fuse | Normal | 23-0039919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821676 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223715239713 | 20230304 | 1033 | 20230304 | 1752 | 2022255 | 439 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 439 | 38.7493 | -120.6985 | No | Clear;32-90 F |  |  | 23-0039974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821730 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 32655 | 20230304 | 1033 | 20230306 | 1133 | 2022271 | 2940 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5880 | 39.2814 | -121.0576 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1821692 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223164848857 | 20230304 | 1049 | 20230306 | 1731 | 2022269 | 3282 | Transformer only | Vegetation | Tree - fell into line | 1 | 3282 | 39.0027 | -120.8879 | No | Clear;32-90 F | Transformer | Broken | 23-0039977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821733 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222685062240 | 20230304 | 1133 | 20230304 | 1148 | 2021744 | 15 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 45 | 39.3724 | -121.0507 | No | Clear;32-90 F |  |  | 23-0039951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821706 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222818657427 | 20230304 | 1228 | 20230309 | 1517 | 2027044 | 7369 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 22107 | 39.2395 | -121.0057 | No | Clear;32-90F |  |  | 23-0042275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823161 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 344014 | 20230304 | 1246 | 20230306 | 813 | 2022427 | 2607 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 2607 | 39.3293 | -120.3467 | No | Clear;32-90F |  |  | 23-0040572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1822287 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 100000033821 | 20230304 | 1336 | 20230309 | 1131 | 2027045 | 7075 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 14150 | 39.2397 | -121.0052 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0042097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823105 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | JUMPER | 465074 | 20230304 | 1339 | 20230304 | 1951 | 2022501 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 13943 | 38.8911 | -121.0981 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1821756 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223271949053 | 20230304 | 1514 | 20230306 | 1349 | 2022591 | 2795 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 2795 | 39.0076 | -120.8495 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0040787 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822393 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 13777 | 20230304 | 1830 | 20230304 | 1957 | 2022828 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1593 | 38.7292 | -121.092 | No | Clear;32-90 F |  |  | 23-0040078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821822 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223857739620 | 20230304 | 1859 | 20230305 | 1738 | 2022851 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 8372 | 38.7463 | -120.6483 | No | Overcast-Fog;Below 32 F | Jumper | Broken | 23-0040253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1822001 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 223892938296 | 20230304 | 1940 | 20230306 | 1032 | 2023912 | 2332 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 2332 | 38.7095 | -120.6389 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822143 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 7091 | 20230304 | 2010 | 20230308 | 1121 | 2022936 | 5231 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 554486 | 39.1884 | -121.0272 | No | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1822578 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223876138504 | 20230304 | 2111 | 20230305 | 1029 | 2022957 | 798 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1596 | 38.7165 | -120.6428 | No |  | Transformer | Broken- wire on ground | 23-0040293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822032 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3643 | 20230305 | 314 | 20230305 | 745 | 2023161 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 2981 | 38.7363 | -121.196 | No | Clear;32-90 F |  |  | 23-0040237 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821985 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20230305 | 640 | 20230305 | 1444 | 2023319 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 102364 | 38.8995 | -120.8545 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821975 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20230305 | 645 | 20230305 | 1137 | 2023334 | 292 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 134 | 39128 | 39.0914 | -121.0565 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0040276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822014 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | MTR#1004689915 | 20230305 | 910 | 20230307 | 1130 | 2023488 | 3020 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 6040 | 38.8535 | -120.8569 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0040584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822294 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 3115 | 20230305 | 921 | 20230305 | 1031 | 2023495 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 350 | 39.1197 | -121.1475 | No | Clear;32-90F |  |  | 23-0040295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822033 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22029 | 20230305 | 1052 | 20230305 | 1100 | 2023626 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 64 | 38.7993 | -120.7168 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822044 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30801 | 20230305 | 1245 | 20230305 | 1517 | 2023732 | 152 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 304 | 38.9081 | -120.8469 | No | Clear;32-90F | Conductor- Overhead | Bent or Twisted | 23-0040381 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822107 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223413646075 | 20230305 | 1252 | 20230305 | 1611 | 2023739 | 199 | Transformer only | Vegetation | Tree - fell into line | 1 | 199 | 38.9254 | -120.8015 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0040417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822150 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | TRANSFORMER | 222690055725 | 20230305 | 1409 | 20230310 | 1429 | 2023902 | 7220 | Transformer only | Environmental/External | Ice or snow | 1 | 7220 | 39.1927 | -121.0514 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0040403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822137 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30897 | 20230305 | 1521 | 20230306 | 1415 | 2023897 | 1374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 41220 | 39.0196 | -120.8203 | No | Overcast-Snow;32-90 F | Crossarm- Wood | Broken | 23-0040401 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822136 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223322144784 | 20230305 | 1646 | 20230306 | 1009 | 2023966 | 1043 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2086 | 38.8906 | -120.8336 | No | Clear;32-90 F | Transformer | Burned Open | 23-0040610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822319 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | TRANSFORMER | 222750055920 | 20230305 | 1705 | 20230309 | 1457 | 2023981 | 5632 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 16896 | 39.1983 | -121.0307 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0040472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822207 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | 33713 HIGH SIDE JUMPERS | 20230305 | 1723 | 20230310 | 1650 | 2023992 | 7167 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7167 | 39.1983 | -121.0342 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041962 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823064 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3841 | 20230305 | 1822 | 20230306 | 802 | 2024035 | 820 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 68060 | 39.1277 | -120.9168 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0040523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822258 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8955 | 20230305 | 1846 | 20230310 | 1159 | 2024162 | 6793 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 81516 | 39.1898 | -120.9768 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken | 23-0040527 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822262 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20230305 | 1904 | 20230311 | 920 | 2026575 | 8056 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 56392 | 39.5206 | -120.9976 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1822889 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33725 | 20230305 | 2000 | 20230307 | 1730 | 2024147 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8190 | 39.1932 | -121.0255 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1822212 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7047 | 20230305 | 2233 | 20230308 | 1752 | 2024179 | 4039 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52507 | 39.1911 | -121.0022 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1822289 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222845955649 | 20230305 | 2305 | 20230306 | 1254 | 2024185 | 829 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 5803 | 39.1904 | -120.997 | No | Clear;32-90 F |  |  | 23-0040733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822375 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5847 | 20230306 | 649 | 20230306 | 1315 | 2024247 | 386 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 386 | 38.8454 | -120.7943 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0040736 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822376 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 31249 | 20230306 | 839 | 20230311 | 1544 | 2024181 | 7625 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 53687 | 39.1913 | -120.9959 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822303 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 100000040277 | 20230306 | 917 | 20230306 | 1044 | 2024225 | 87 | Transformer only | Vegetation | Tree - fell into line | 1 | 87 | 38.7143 | -120.6164 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0040619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822323 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30293 | 20230306 | 922 | 20230307 | 2220 | 2025311 | 2218 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 6654 | 39.2191 | -121.0106 | No | Overcast-Snow;Below 32 F |  |  | 23-0041435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822765 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ'S 1 SPAN SS OF CGC #222804556020 | 20230306 | 943 | 20230309 | 1915 | 2024580 | 4892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4892 | 39.2007 | -121.011 | No | Clear;32-90F | Pole-Wood | Broken | 23-0040665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822345 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 344014 | 20230306 | 1205 | 20230306 | 1211 | 2024656 | 6 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 6 | 39.3293 | -120.3467 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0040701 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822359 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222837056826 | 20230306 | 1529 | 20230311 | 1508 | 2032619 | 7179 | Transformer only | Environmental/External | Ice or snow | 4 | 28716 | 39.2228 | -120.9997 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 23-0043502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824048 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8951 | 20230306 | 1558 | 20230306 | 1809 | 2024939 | 131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 917 | 39.1794 | -120.976 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0040862 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822427 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | WIRE DOWN | 20230306 | 1646 | 20230308 | 1658 | 2024978 | 2892 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2892 | 39.3812 | -121.0594 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1822614 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 3133 | 20230306 | 1702 | 20230307 | 1624 | 2024988 | 1402 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4206 | 39.2896 | -121.0462 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041228 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1822638 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222662158929 | 20230306 | 1836 | 20230307 | 1754 | 2025060 | 1398 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2796 | 39.2807 | -121.0607 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822462 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223314945346 | 20230306 | 1904 | 20230306 | 1943 | 2025094 | 39 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 78 | 38.9058 | -120.8362 | No | Clear;32-90F | Secondary | Broken | 23-0040919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822470 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 591351 | 20230306 | 1949 | 20230306 | 2211 | 2025121 | 142 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 83 | 11786 | 39.3222 | -120.3792 | No | Clear;32-90F |  |  | 23-0040991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822531 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 8191 | 20230306 | 2041 | 20230310 | 1700 | 2025143 | 5539 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 293567 | 39.2059 | -121.0385 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1823093 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222837558852 | 20230307 | 1213 | 20230310 | 1823 | 2025579 | 4690 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 4690 | 39.2783 | -120.999 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822647 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 8307 | 20230307 | 1445 | 20230311 | 920 | 2026581 | 5435 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 59785 | 39.5203 | -120.9971 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822891 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 31605 | 20230307 | 1613 | 20230307 | 1747 | 2025842 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 99 | 9279 | 38.9817 | -121.0247 | No | Clear;32-90F |  |  | 23-0041350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822682 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 31605 | 20230307 | 1928 | 20230308 | 1020 | 2026011 | 892 | Distribution Circuit | Equipment Failure/Involved | Underground | 150 | 99142 | 38.9817 | -121.0247 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 23-0041487 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822810 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4817 | 20230307 | 2033 | 20230311 | 1812 | 2026356 | 5619 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 258474 | 39.2099 | -120.9363 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823059 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7397 | 20230307 | 2105 | 20230308 | 1030 | 2026208 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 36225 | 39.2604 | -120.9764 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0041569 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822856 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222672556762 | 20230307 | 2225 | 20230308 | 940 | 2026084 | 675 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 7425 | 39.2214 | -121.0578 | No | Clear;32-90F | Fuse | Broken | 23-0041597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822873 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 30393 | 20230307 | 2241 | 20230308 | 840 | 2026087 | 599 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 599 | 39.0117 | -121.0337 | No | Clear;32-90F |  |  | 23-0041531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822828 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3099 | 20230308 | 604 | 20230308 | 2306 | 2026232 | 1022 | Distribution Circuit | 3rd Party | Vehicle | 9 | 9198 | 39.134 | -120.9401 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0041474 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822801 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 20230308 | 721 | 20230311 | 920 | 2026284 | 4439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 35504 | 39.4382 | -120.9965 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1822812 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 20230308 | 859 | 20230310 | 1605 | 2026386 | 3306 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 42978 | 39.2097 | -120.9435 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822975 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ TWD CGC 222782056021 | 20230308 | 909 | 20230309 | 1645 | 2027221 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11376 | 39.2005 | -121.02 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1823060 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | T3046 | 20230308 | 916 | 20230308 | 1058 | 2026416 | 102 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 306 | 39.2184 | -121.0108 | No | Clear;32-90F |  |  | 23-0041633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822894 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 30745 | 20230308 | 918 | 20230308 | 1448 | 2026434 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 18480 | 39.0433 | -120.9863 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041607 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1822878 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222429855513 | 20230308 | 1048 | 20230308 | 1345 | 2026612 | 177 | Transformer only | Animal | Squirrel | 1 | 177 | 39.189 | -121.1436 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0041737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822937 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | JUMPER | 7165 HI SIDE JUMPERS | 20230308 | 1056 | 20230308 | 1721 | 2026586 | 385 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 10780 | 39.2322 | -121.0732 | No | Clear;32-90F | Pole-Wood | Broken | 23-0041631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822893 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 34483 | 20230308 | 1151 | 20230308 | 1430 | 2026643 | 159 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 159 | 39.2432 | -121.0108 | No | Overcast-Snow;32-90 F | Jumper | Normal | 23-0041664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1822913 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33717 | 20230308 | 1500 | 20230309 | 1259 | 2027311 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1522 | 39.194 | -121.0301 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041997 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1823075 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 31841 | 20230309 | 316 | 20230309 | 1042 | 2027161 | 446 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 3122 | 39.2711 | -120.9968 | Yes | Clear;32-90F |  |  | 23-0042039 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823087 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 30509 | 20230309 | 1048 | 20230310 | 1530 | 2027399 | 1722 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36162 | 39.2045 | -121.0382 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042052 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823094 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 34949 | 20230309 | 1108 | 20230310 | 1830 | 2027420 | 1882 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3764 | 39.1959 | -121.0109 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823099 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 9841 | 20230309 | 1142 | 20230309 | 1628 | 2027451 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 8294 | 39.2585 | -121.0206 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0042099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823106 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222866562360 | 20230309 | 1252 | 20230311 | 834 | 2027397 | 2622 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 5244 | 39.3747 | -120.9867 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0042225 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823150 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33267 | 20230309 | 1257 | 20230309 | 1817 | 2027539 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 640 | 39.1822 | -120.9716 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823119 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 20230309 | 1259 | 20230312 | 1515 | 2028295 | 4456 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 120312 | 39.1757 | -120.9295 | Yes | Overcast;32-90 F |  |  | 23-0043746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824263 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJS TWDS CGC 222820455929 | 20230309 | 1300 | 20230311 | 1715 | 2027890 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9405 | 39.1989 | -121.0059 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0042349 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823195 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8479 | 20230309 | 1402 | 20230309 | 1425 | 2027682 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 1196 | 38.9916 | -121.0154 | Yes | Clear;32-90F | Woodpin | Broken | 23-0042182 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823138 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20230309 | 1637 | 20230309 | 1829 | 2028124 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 19936 | 38.7138 | -120.6231 | Yes | Partly Cloudy-Fog-Rain;32-90 F | Insulator | Broken | 23-0042242 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823190 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7071 | 20230309 | 1702 | 20230311 | 921 | 2031359 | 2419 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 12095 | 39.1668 | -120.9708 | Yes | Clear;32-90F |  |  | 23-0043233 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1823822 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7601 | 20230309 | 1711 | 20230311 | 1440 | 2028301 | 2729 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 40935 | 39.1991 | -121.0034 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043052 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823712 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6487 | 20230309 | 1715 | 20230310 | 1712 | 2028304 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2874 | 39.1792 | -120.9998 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823214 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8953 | 20230309 | 1834 | 20230310 | 1230 | 2028590 | 1076 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6456 | 39.1869 | -120.9724 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0042987 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823687 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39051 | 20230309 | 2002 | 20230309 | 2133 | 2029183 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 6188 | 39.0263 | -121.0589 | Yes | Overcast-Rain;32-90 F |  |  | 23-0042568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823386 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | WIRE DOWN | 20230309 | 2102 | 20230311 | 1024 | 2030062 | 2242 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11906 | 39.2707 | -120.9921 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1823653 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | FUSE | 34517 | 20230309 | 2107 | 20230310 | 1247 | 2029381 | 940 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 47000 | 38.7472 | -121.2163 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0042621 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823433 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222273943682 | 20230309 | 2233 | 20230310 | 806 | 2029601 | 573 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1146 | 38.8639 | -121.2038 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0042805 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823593 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222601856505 | 20230309 | 2315 | 20230310 | 1130 | 2029687 | 735 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 735 | 39.2147 | -121.0828 | Yes | Clear;32-90F |  |  | 23-0042633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823444 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | SWITCH | 61602 | 20230309 | 2323 | 20230309 | 2331 | 2029681 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 957 | 7656 | 39.2254 | -121.0789 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0042631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823442 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 30097 | 20230309 | 2334 | 20230310 | 1045 | 2029696 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14762 | 38.7524 | -121.2068 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823464 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20367 | 20230310 | 122 | 20230310 | 1141 | 2029865 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4952 | 38.6948 | -120.7775 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043006 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823695 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 5679 | 20230310 | 204 | 20230310 | 910 | 2029910 | 426 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 12354 | 38.985 | -121.1355 | No | Clear;32-90F |  |  | 23-0042803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823591 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 20230310 | 238 | 20230310 | 406 | 2029954 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2495 | 219560 | 38.7393 | -120.6773 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1823513 | 0 | EPSS Ckt | N | 2023 | ABC TIME
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7147 | 20230310 | 316 | 20230310 | 1405 | 2029996 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 31867 | 39.2454 | -121.0566 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042870 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823631 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5405 | 20230310 | 319 | 20230310 | 834 | 2030008 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 23669 | 38.9096 | -121.0882 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 23-0042788 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823583 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | WIRE DOWN LD SIDE OF 31849 | 20230310 | 338 | 20230310 | 1213 | 2030075 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 5702 | 39.2733 | -120.9779 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | Yes | 1823615 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3337 | 20230310 | 348 | 20230310 | 905 | 2030027 | 317 | Distribution Circuit | Vegetation | Tree - bark fell into line | 12 | 3804 | 39.0994 | -121.0291 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823609 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230310 | 348 | 20230310 | 1140 | 2030026 | 472 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 6608 | 38.7941 | -120.8199 | No | Clear;32-90F |  |  | 23-0043026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823700 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 889106 | 20230310 | 408 | 20230310 | 434 | 2030071 | 26 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 34 | 884 | 38.8035 | -120.046 | No | Overcast-Heavy Rain;32-90 F |  |  | 23-0042737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823551 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20230310 | 435 | 20230310 | 1642 | 2030074 | 727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 705 | 64371 | 38.773 | -120.2933 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0042740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1823554 | 0 | EPSS Ckt | N | 2023 | ABC GRD
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | OCB | 2105/2 | 20230310 | 654 | 20230310 | 826 | 2030230 | 92 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4800 | 96617 | 38.6555 | -121.0603 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0042768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823573 | 0 | EPSS Ckt | N | 2023 | PRI PH TIME OC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222886658557 | 20230310 | 719 | 20230310 | 1407 | 2030310 | 408 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1224 | 39.27 | -120.9809 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0043135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823749 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 30085 | 20230310 | 738 | 20230310 | 852 | 2030344 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 74 | 38.7963 | -121.1547 | No | Clear;32-90F |  |  | 23-0042855 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823618 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7069 | 20230310 | 841 | 20230310 | 1910 | 2030454 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4403 | 39.1772 | -120.9767 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823842 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6693 | 20230310 | 946 | 20230310 | 1721 | 2030641 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 22750 | 39.2001 | -121.0107 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0042955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823675 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222391440894 | 20230310 | 1114 | 20230310 | 1408 | 2030505 | 174 | Transformer only | Vegetation | Tree - fell into line | 1 | 174 | 38.7862 | -121.1619 | No | Clear;32-90 F | Transformer | Bent or Twisted | 23-0042997 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823691 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222887458560 | 20230310 | 1245 | 20230310 | 1420 | 2030993 | 95 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 95 | 39.2703 | -120.9806 | No | Clear;32-90F |  |  | 23-0043143 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823757 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223582046540 | 20230310 | 1410 | 20230310 | 1506 | 2031131 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 38.9388 | -120.7404 | No | Clear;32-90F | Fuse | Normal | 23-0043170 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823771 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 8879 | 20230310 | 1536 | 20230310 | 1641 | 2031288 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 780 | 39.2721 | -121.005 | No | Clear;32-90F |  |  | 23-0043204 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823797 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ SS CGC 222845955429 | 20230310 | 1700 | 20230311 | 1700 | 2031432 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10080 | 39.1841 | -120.9971 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1823802 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222866956948 | 20230310 | 1719 | 20230311 | 1133 | 2031487 | 1094 | Transformer only | Vegetation | Tree - fell into line | 2 | 2188 | 39.2257 | -120.989 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0043228 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823818 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 30757 | 20230310 | 1721 | 20230311 | 1112 | 2031472 | 1071 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 10710 | 39.2897 | -120.9153 | No | Partly Cloudy;32-90 F |  |  | 23-0043429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823993 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE 2110 | 153612110 | FUSE | 11077 | 20230310 | 1732 | 20230310 | 1843 | 2031485 | 71 | Distribution Circuit | Animal | Bird found | 24 | 1704 | 38.7044 | -121.1039 | No | Clear;32-90F | Fuse | Burned Open | 23-0043250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823837 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 992864 | 20230310 | 1745 | 20230310 | 1753 | 2031502 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 631 | 5048 | 38.8042 | -120.1031 | No | Overcast-Drizzle;32-90 F | Recloser | Normal | 23-0042740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823821 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20230310 | 1758 | 20230310 | 2025 | 2031508 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2058 | 38.7941 | -120.8199 | No | Overcast;32-90 F |  |  | 23-0043253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823840 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9553 | 20230310 | 1810 | 20230310 | 1833 | 2031548 | 23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 483 | 39.2613 | -120.9057 | No | Partly Cloudy;32-90 F |  |  | 23-0043244 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823833 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | SMARTVILLE 1101 | 153791101 | TRIP-SAVER | 34069 | 20230310 | 1845 | 20230310 | 2006 | 2031562 | 81 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 171 | 13851 | 39.2028 | -121.2764 | No | Clear;32-90F |  |  | 23-0043264 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823850 | 0 | EPSS Ckt | N | 2023 | A-B
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ'S SS OF CGC 222878955610 | 20230310 | 2000 | 20230311 | 1422 | 2031932 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2365 | 39.1889 | -120.9842 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1823923 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 20230310 | 2338 | 20230312 | 1551 | 2031764 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 293315 | 39.3638 | -120.7923 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823988 | 0 | Non-EPSS | N | 2023 | SGF
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6641 | 20230311 | 241 | 20230311 | 921 | 2031844 | 400 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 126 | 50425 | 39.2996 | -120.3786 | No | Clear;32-90 F |  |  | 23-0043374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823951 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | OTHER | SO-ND460269 | 20230311 | 509 | 20230311 | 1125 | 2032325 | 376 | Transformer only | Company Initiated | Return Circuit Normal | 1 | 376 | 39.228 | -121.0468 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0041235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1823992 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 30415 | 20230311 | 510 | 20230311 | 1126 | 2031883 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 12041 | 39.2299 | -121.0445 | No | Clear;32-90F | Pole-Wood | Broken | 23-0041235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823916 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222870834634 | 20230311 | 626 | 20230311 | 900 | 2031915 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 154 | 38.6145 | -120.9976 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0043376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823952 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15275 | 20230311 | 633 | 20230311 | 840 | 2031921 | 127 | Distribution Circuit | Animal | Bird found | 28 | 3556 | 38.9265 | -121.3165 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043357 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823937 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 30453 | 20230311 | 807 | 20230311 | 841 | 2031991 | 34 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 442 | 38.889 | -121.1225 | No | Clear;32-90F |  |  | 23-0043373 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823950 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | TRANSFORMER | 222195544930 | 20230311 | 813 | 20230311 | 1249 | 2031996 | 276 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 276 | 38.8975 | -121.2299 | No | Clear;32-90 F | Transformer | Broken | 23-0043397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823964 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 31243 | 20230311 | 931 | 20230311 | 1705 | 2032119 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1362 | 39.1882 | -120.9995 | No | Clear;32-90F | Pole-Wood | Broken | 23-0043382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823956 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | 2 SP EAST OF CGC 223417445943 | 20230311 | 1023 | 20230311 | 1133 | 2032213 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 420 | 38.9217 | -120.7984 | No | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0043407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823972 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20230311 | 1035 | 20230311 | 1651 | 2032239 | 376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 2632 | 39.5206 | -120.9976 | No | Clear;32-90F |  |  | 23-0043496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1824042 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 6527 | 20230311 | 1059 | 20230311 | 1839 | 2032158 | 460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 17348 | 39.2401 | -121.1879 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0043418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823984 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7329 | 20230311 | 1157 | 20230311 | 1344 | 2032362 | 107 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 1498 | 39.2352 | -120.9819 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823999 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20230311 | 1639 | 20230311 | 2027 | 2032692 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 89364 | 39.0014 | -121.0224 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1824064 | 0 | EPSS Ckt | N | 2023 | A-B-C
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6369 | 20230311 | 1818 | 20230312 | 1048 | 2032813 | 990 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2970 | 39.2167 | -120.8238 | No | Clear;32-90F | Crossarm- Steel | Broken | 23-0043550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824089 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30263 | 20230311 | 1918 | 20230312 | 1546 | 2032850 | 1228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 41752 | 39.2154 | -120.9321 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 23-0043604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824144 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJS 1 SPAN LD SIDE OF 795556 | 20230311 | 2111 | 20230312 | 1057 | 2032918 | 826 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 34692 | 39.313 | -120.9823 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0043665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824199 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222597051445 | 20230311 | 2318 | 20230312 | 1843 | 2032960 | 1165 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1165 | 39.0753 | -121.0866 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0043680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1824211 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20230312 | 718 | 20230312 | 904 | 2033078 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 13992 | 38.8063 | -120.925 | No | Clear;32-90F |  |  | 23-0043657 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824192 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20230312 | 720 | 20230312 | 814 | 2033069 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 2214 | 38.6888 | -120.9245 | No | Clear;32-90F |  |  | 23-0043643 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824179 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10919 | 20230312 | 754 | 20230312 | 1208 | 2033095 | 254 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 508 | 38.6969 | -120.8257 | No | Clear;32-90F | Circuit Breaker | Failed/Faulted | 23-0043677 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824208 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 30657 | 20230312 | 855 | 20230312 | 1501 | 2033129 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6222 | 38.8993 | -121.0951 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1824205 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10919 | 20230312 | 934 | 20230312 | 1458 | 2033340 | 324 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 648 | 38.6969 | -120.8257 | No | Clear;32-90F | Circuit Breaker | Failed/Faulted | 23-0043751 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824267 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 22943 | 20230312 | 1250 | 20230312 | 1938 | 2033298 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4080 | 38.8061 | -120.9079 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0043741 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1824258 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30251 | 20230312 | 1543 | 20230312 | 1850 | 2033426 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2618 | 39.1686 | -120.9373 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0043768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824282 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | SWITCH | 1013 | 20230312 | 1547 | 20230312 | 1843 | 2033425 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 1598 | 61518 | 39.0729 | -121.0868 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0043754 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824270 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222686057677 | 20230312 | 1626 | 20230313 | 1009 | 2033455 | 1063 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 3615 | 39.2464 | -121.0526 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043776 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824289 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20230312 | 1750 | 20230313 | 1352 | 2033527 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 710 | 852778 | 38.9732 | -121.0141 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1824287 | 0 | EPSS Ckt | N | 2023 | A-B-C
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRIP-SAVER | 7559 | 20230312 | 1841 | 20230312 | 2005 | 2033573 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 69 | 5796 | 39.0202 | -121.0625 | No | Clear;32-90F |  |  | 23-0043805 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1824319 | 0 | EPSS Ckt | N | 2023 | OPEN
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 5215 | 20230312 | 1941 | 20230312 | 2102 | 2033670 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 215 | 17415 | 39.2088 | -121.2511 | No | Clear;32-90F |  |  | 23-0043813 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824326 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 591351 | 20230312 | 2127 | 20230313 | 924 | 2033879 | 717 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 39694 | 39.3222 | -120.3792 | No | Clear;32-90F |  |  | 23-0044001 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824480 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20230313 | 42 | 20230313 | 1301 | 2033863 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 30299 | 38.6888 | -120.9245 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1824447 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20230313 | 352 | 20230313 | 400 | 2033897 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 511 | 4088 | 39.0351 | -121.0957 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0043934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824449 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 34911 | 20230313 | 612 | 20230313 | 1503 | 2033961 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5310 | 39.0043 | -121.0306 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1824467 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33269 | 20230313 | 952 | 20230313 | 1249 | 2034241 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 177 | 39.1799 | -120.9758 | No | Clear;32-90F | Pole-Wood | Broken | 23-0044034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824498 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223449243043 | 20230313 | 1011 | 20230313 | 1123 | 2034272 | 72 | Transformer only | Environmental/External | Lightning | 1 | 72 | 38.8417 | -120.7897 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0044100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824519 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5707 | 20230313 | 1109 | 20230313 | 1629 | 2034347 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 640 | 39.0256 | -121.0995 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1824543 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJS 1 SS OF CGC#222886557174 | 20230313 | 1213 | 20230313 | 1316 | 2034442 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 126 | 39.2324 | -120.9819 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0044126 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824528 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222771255407 | 20230313 | 1232 | 20230313 | 1834 | 2034463 | 362 | Transformer only | Vegetation | Tree - fell into line | 1 | 362 | 39.1838 | -121.0234 | No | Clear;32-90 F | Service conductor | Broken- wire on object | 23-0044277 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824585 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7933 | 20230313 | 1234 | 20230314 | 1130 | 2034469 | 1376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8256 | 39.6886 | -120.6461 | No | Clear;32-90F | Insulator | Broken | 23-0044139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824535 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222923055845 | 20230313 | 1407 | 20230314 | 1920 | 2034592 | 1753 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1753 | 39.1955 | -120.9698 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0044274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1824583 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222887559505 | 20230313 | 1538 | 20230314 | 1227 | 2034792 | 1249 | Transformer only | Vegetation | Tree - fell into line | 1 | 1249 | 39.2958 | -120.9805 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0044322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824607 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20379 | 20230313 | 2006 | 20230313 | 2140 | 2035053 | 94 | Distribution Circuit | Environmental/External | Lightning | 11 | 1034 | 38.6904 | -120.7587 | No | Clear;32-90F | Fuse | Burned Open | 23-0044417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824684 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | 1 SPAN EAST OF CGC # 222721055541 | 20230314 | 951 | 20230314 | 1120 | 2035429 | 89 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 2 | 178 | 39.1875 | -121.0403 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0044592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824780 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222895560140 | 20230314 | 953 | 20230314 | 1043 | 2035318 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 39.3129 | -120.9775 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0044554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824760 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 19910 | 20230314 | 1003 | 20230314 | 1137 | 2035716 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 39856 | 38.6313 | -120.8542 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0044658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824813 | 0 | EPSS Ckt | N | 2023 | BC
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222858656442 | 20230314 | 1010 | 20230314 | 1946 | 2035741 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 576 | 39.2124 | -120.9923 | Yes | Clear;32-90F | Metering Equipment | Failed/Faulted | 23-0044661 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824815 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | TRANSFORMER | 222835867632 | 20230314 | 1027 | 20230314 | 1102 | 2035230 | 35 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 70 | 39.5196 | -120.9959 | Yes | Clear;32-90 F |  |  | 23-0044698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1824845 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11491 | 20230314 | 1041 | 20230315 | 1621 | 2036029 | 1780 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 154860 | 38.6367 | -120.7207 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825299 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20563 | 20230314 | 1051 | 20230314 | 1202 | 2036153 | 71 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 1562 | 38.5986 | -120.9836 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0044951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825036 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 894 | 20230314 | 1103 | 20230314 | 1420 | 2041789 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 919 | 39.3115 | -120.9719 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0044582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1825363 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223234437265 | 20230314 | 1103 | 20230314 | 1513 | 2036419 | 250 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1250 | 38.6843 | -120.8679 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825447 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222680739271 | 20230314 | 1115 | 20230314 | 1820 | 2036634 | 425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 850 | 38.7422 | -121.061 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0045406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825390 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | RECLOSER | 19642 | 20230314 | 1120 | 20230314 | 1302 | 2036764 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 847 | 86394 | 38.6832 | -121.0684 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0044804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824924 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 8145 | 20230314 | 1129 | 20230314 | 1458 | 2037159 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 39710 | 38.6977 | -120.9365 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0045110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1825166 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20230314 | 1132 | 20230314 | 1921 | 2037179 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 108875 | 38.7121 | -120.9501 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1824952 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 5679 | 20230314 | 1137 | 20230314 | 1417 | 2037268 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 4640 | 38.985 | -121.1355 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0045107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825163 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 20577 | 20230314 | 1144 | 20230314 | 1245 | 2037529 | 61 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 244 | 38.7394 | -120.8547 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825140 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21295 | 20230314 | 1145 | 20230314 | 2013 | 2038083 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | 38.6429 | -120.6988 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1825026 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22347 | 20230314 | 1145 | 20230315 | 1605 | 2037567 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 30600 | 38.6466 | -120.9189 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825545 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5837 | 20230314 | 1208 | 20230314 | 1644 | 2038155 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2208 | 38.8578 | -120.8381 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045246 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1825271 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 20555 | 20230314 | 1209 | 20230315 | 1924 | 2041896 | 1875 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18750 | 38.7558 | -120.856 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1825336 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20230314 | 1210 | 20230314 | 1248 | 2038157 | 38 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 4332 | 39.275 | -121.021 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0044974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825057 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 90970 | 20230314 | 1214 | 20230314 | 1624 | 2038412 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 54914 | 38.8253 | -121.1698 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0044980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825062 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 20230314 | 1216 | 20230315 | 1907 | 2038331 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9255 | 38.5951 | -120.8115 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825482 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | OCB | 1112/2 | 20230314 | 1222 | 20230314 | 1952 | 2038658 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 2114 | 253772 | 38.7313 | -120.7839 | Yes | Overcast-Fog-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045011 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825087 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21979 | 20230314 | 1234 | 20230314 | 1440 | 2038997 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 630 | 38.7175 | -120.8799 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825217 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 89063 | 20230314 | 1240 | 20230315 | 1345 | 2039178 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3010 | 38.9448 | -121.2378 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825639 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9353 | 20230314 | 1247 | 20230315 | 1241 | 2039356 | 1434 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18642 | 38.9015 | -120.9035 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045357 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1825346 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 3879 | 20230314 | 1259 | 20230317 | 1340 | 2039940 | 4361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 30527 | 39.3206 | -120.3375 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0047018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826565 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 8275 | 20230314 | 1326 | 20230314 | 1419 | 2040561 | 53 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 742 | 38.9239 | -121.1195 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825310 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | FUSE | 22985 | 20230314 | 1345 | 20230314 | 1539 | 2040953 | 114 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 1596 | 38.6997 | -121.1096 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825457 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5419 | 20230314 | 1348 | 20230314 | 1521 | 2041187 | 93 | Distribution Circuit | Animal | Bird found | 40 | 3720 | 38.8975 | -121.2426 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825412 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 30453 | 20230314 | 1350 | 20230314 | 1831 | 2041105 | 281 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 3653 | 38.889 | -121.1225 | Yes | Clear;32-90 F |  |  | 23-0045714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825651 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 51794 | 20230314 | 1401 | 20230315 | 1854 | 2041735 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 2707 | 792668 | 39.0439 | -121.0501 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Steel | Broken- wire on ground | 23-0045281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1825297 | 0 | EPSS Ckt | N | 2023 | AC GRD
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20230314 | 1405 | 20230316 | 1141 | 2041765 | 2736 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 10096 | 39.3823 | -121.0478 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825410 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18517 | 20230314 | 1410 | 20230315 | 1021 | 2041834 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16051 | 38.7227 | -121.0466 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045594 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825546 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3911 | 20230314 | 1419 | 20230315 | 1801 | 2042006 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8310 | 39.3625 | -121.1125 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825574 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 9413 | 20230314 | 1424 | 20230315 | 1457 | 2042082 | 1473 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 52015 | 38.8989 | -121.2185 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1825463 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 889106 | 20230314 | 1430 | 20230316 | 1145 | 2042174 | 2715 | Distribution Circuit | Environmental/External | Ice or snow | 39 | 78231 | 38.8035 | -120.046 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825326 | 0 | EPSS Ckt | N | 2023 | B-C
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32621 | 20230314 | 1431 | 20230314 | 1609 | 2042251 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 18326 | 39.2311 | -121.0586 | Yes | Clear;32-90 F |  |  | 23-0045520 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825483 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4233 | 20230314 | 1444 | 20230314 | 1820 | 2042452 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 12312 | 39.2448 | -121.2159 | Yes | Clear;32-90 F |  |  | 23-0045707 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825645 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 17361 | 20230314 | 1456 | 20230315 | 1310 | 2042522 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 10948 | 39.0051 | -121.34 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825607 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20230314 | 1522 | 20230315 | 1853 | 2042750 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 203073 | 38.6701 | -120.7775 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825519 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 31377 | 20230314 | 1544 | 20230315 | 2010 | 2042952 | 1706 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 64708 | 39.0323 | -121.0725 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825693 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5747 | 20230314 | 1549 | 20230315 | 1515 | 2043006 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18278 | 38.957 | -121.0486 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825701 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 39927 | 20230314 | 1552 | 20230314 | 2110 | 2043088 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 4730 | 38.9027 | -121.0753 | Yes | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0045647 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825589 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5419 | 20230314 | 1555 | 20230315 | 1117 | 2043067 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 5335 | 38.8975 | -121.2426 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825615 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33161 | 20230314 | 1600 | 20230315 | 1458 | 2043150 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8268 | 39.2673 | -121.0214 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825564 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4717 | 20230314 | 1616 | 20230315 | 1737 | 2043189 | 1521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 80613 | 39.1676 | -121.1419 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045643 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1825586 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18873 | 20230314 | 1623 | 20230315 | 1755 | 2043253 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 32172 | 38.8161 | -120.9016 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825652 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20230314 | 1631 | 20230314 | 1637 | 2043406 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 83 | 498 | 39.4883 | -120.8571 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0045612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825560 | 0 | EPSS Ckt | N | 2023 | A+B
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30163 | 20230314 | 1645 | 20230314 | 2115 | 2043444 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 810 | 39.215 | -121.0203 | Yes | Clear;32-90 F |  |  | 23-0045872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825796 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7329 | 20230314 | 1712 | 20230315 | 1850 | 2043690 | 1538 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 21532 | 39.2352 | -120.9819 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0045921 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825844 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 20230314 | 1714 | 20230315 | 1811 | 2043753 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 348214 | 39.3676 | -121.0458 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1825604 | 0 | EPSS Ckt | N | 2023 | A+B+C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7359 | 20230314 | 1720 | 20230314 | 1953 | 2043733 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2975 | 39.2497 | -121.0004 | Yes | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0045799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825722 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3643 | 20230314 | 1749 | 20230314 | 1957 | 2043934 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1408 | 38.7363 | -121.196 | Yes | Clear;32-90 F |  |  | 23-0045825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1825747 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20230314 | 1808 | 20230315 | 1453 | 2043997 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 1041 | 92145 | 38.8154 | -120.8221 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825661 | 0 | EPSS Ckt | N | 2023 | A+C
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 32831 | 20230314 | 1826 | 20230315 | 943 | 2044237 | 917 | Distribution Circuit | Company Initiated | Improper Construction | 3 | 2751 | 39.3861 | -121.0336 | Yes | Clear-Strong Winds;32-90 F | Lightning Arrestor | Burned/flashed | 23-0045907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825832 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223522636765 | 20230314 | 1900 | 20230314 | 2058 | 2044384 | 118 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 118 | 38.6695 | -120.7673 | Yes | Clear;32-90 F |  |  | 23-0045881 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1825805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9393 | 20230314 | 1904 | 20230315 | 901 | 2044400 | 837 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 10044 | 38.9086 | -120.8486 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0046139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826034 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 22471 | 20230314 | 1908 | 20230315 | 1126 | 2043658 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 22494 | 38.6636 | -121.0031 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045788 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1825713 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223296637114 | 20230314 | 1929 | 20230314 | 1940 | 2043931 | 11 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 11 | 38.6798 | -120.846 | Yes | Overcast-Fog;32-90 F |  |  | 23-0045819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1825741 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20775 | 20230314 | 2033 | 20230314 | 2133 | 2044684 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 3660 | 38.6284 | -120.9483 | Yes | Clear;32-90 F |  |  | 23-0045911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825835 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224566560045 | 20230315 | 405 | 20230315 | 1510 | 2045198 | 665 | Transformer only | Environmental/External | Ice or snow | 5 | 3325 | 39.3042 | -120.3906 | No | Clear;32-90 F | Fuse | Normal | 23-0046472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1826238 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4561 | 20230315 | 804 | 20230315 | 1005 | 2045495 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 484 | 39.2119 | -121.1933 | No | Clear;32-90 F |  |  | 23-0046185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826068 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | FUSE | 21923 | 20230315 | 807 | 20230315 | 1410 | 2045502 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1076 | 38.7178 | -120.7964 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1826015 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222817656493 | 20230315 | 1423 | 20230315 | 1616 | 2046374 | 113 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 452 | 39.2137 | -121.0065 | No | Partly Cloudy-Rain;32-90 F | Secondary | Normal | 23-0046409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826203 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222735562820 | 20230315 | 1425 | 20230315 | 1452 | 2046246 | 27 | Transformer only | Vegetation | Tree - fell into line | 1 | 27 | 39.3879 | -121.0329 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0046363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826173 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | SWITCH | 9573 | 20230315 | 1516 | 20230315 | 1522 | 2046548 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 235 | 1410 | 38.8449 | -120.857 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0045724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826243 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | JUMPER | OJ'S @ CGC 222996534090 | 20230315 | 1715 | 20230315 | 2225 | 2046908 | 310 | Distribution Circuit | 3rd Party | Vehicle | 3 | 930 | 38.5978 | -120.9526 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0046585 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826307 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 3045 | 20230315 | 1758 | 20230316 | 1401 | 2047029 | 1203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1203 | 39.3132 | -120.4213 | No | Clear;32-90 F | Insulator | Broken | 23-0046603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7931 | 20230316 | 856 | 20230316 | 1030 | 2047880 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 125 | 38.846 | -121.4143 | No | Clear;32-90 F |  |  | 23-0046946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1826518 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 2553 | 20230316 | 1400 | 20230318 | 1219 | 2048692 | 2779 | Distribution Circuit | 3rd Party | Aircraft | 5 | 11663 | 38.7732 | -121.431 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1826656 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6641 | 20230316 | 1414 | 20230317 | 1604 | 2047873 | 1550 | Distribution Circuit | Environmental/External | Ice or snow | 409 | 58290 | 39.2996 | -120.3786 | No | Clear;Below 32 F | Pole-Wood | Broken | 23-0047093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826606 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15257 | 20230316 | 1934 | 20230316 | 2101 | 2049205 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1131 | 38.9265 | -121.2597 | No | Clear;32-90 F |  |  | 23-0047263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826724 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 21103 | 20230316 | 1946 | 20230317 | 1213 | s1826815 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 987 | 38.7285 | -120.774 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1826815 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1102 | 152291102 | TRANSFORMER | 224226760178 | 20230316 | 2038 | 20230317 | 1554 | 2049306 | 1156 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4624 | 39.3095 | -120.5071 | No | Clear;32-90 F | Jumper | Broken | 23-0047567 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1826890 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6647 | 20230316 | 2143 | 20230317 | 1002 | 2049486 | 739 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 35472 | 39.3066 | -120.3821 | No | Clear;Below 32 F |  |  | 23-0047481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826844 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224579460258 | 20230317 | 1044 | 20230317 | 1209 | 2049957 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 510 | 39.31 | -120.3827 | No | Clear;32-90 F | Fuse | Broken | 23-0047547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1826881 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7921 | 20230317 | 1133 | 20230317 | 1325 | 2049910 | 112 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 96 | 10752 | 39.5698 | -120.6206 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826870 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3953 | 20230317 | 1147 | 20230317 | 1316 | 2049983 | 89 | Distribution Circuit | 3rd Party | Vehicle | 33 | 2937 | 39.1909 | -121.0268 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0047549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826883 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223350739129 | 20230317 | 1558 | 20230317 | 1900 | 2050422 | 182 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 728 | 38.7351 | -120.8264 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0047714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1826960 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | 222600546365 | 20230317 | 1643 | 20230318 | 1250 | 2050500 | 1207 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 6035 | 38.9362 | -121.0871 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0047755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1826996 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225595442688 | 20230317 | 1850 | 20230318 | 1106 | 2050676 | 976 | Transformer only | Environmental/External | Ice or snow | 1 | 976 | 38.8222 | -120.0367 | No | Clear;Below 32 F | Service conductor | Broken | 23-0048286 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827510 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 22793 | 20230318 | 1130 | 20230318 | 1635 | 2051147 | 305 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 305 | 38.8248 | -120.0414 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0048301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1827519 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20230318 | 1206 | 20230318 | 1405 | 2051156 | 119 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 11543 | 39.0715 | -120.9763 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0048314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1827528 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223979237978 | 20230318 | 1435 | 20230318 | 1643 | 2051296 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 256 | 38.701 | -120.6069 | No | Clear;32-90 F |  |  | 23-0048345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1827549 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ'S @ SAP# 100004611 | 20230318 | 1436 | 20230318 | 2056 | 2051297 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2280 | 39.3041 | -120.9713 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0048328 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1827535 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | TRANSFORMER | 222404043020 | 20230318 | 1858 | 20230319 | 1318 | 2051471 | 1100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1100 | 38.8445 | -121.1572 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0048355 | OH | Sus | 35432720 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827559 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 41339 | 20230318 | 1942 | 20230318 | 2102 | 2051513 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3120 | 38.7827 | -121.2336 | No | Clear;32-90 F |  |  | 23-0048361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1827565 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 11089 | 20230318 | 2050 | 20230319 | 1030 | 2051567 | 820 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 820 | 38.6973 | -121.008 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0048364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827568 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4653 | 20230318 | 2209 | 20230319 | 105 | 2051586 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 14960 | 38.7692 | -120.9438 | No | Clear;32-90 F |  |  | 23-0048415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1827621 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50008 | 20230319 | 357 | 20230319 | 541 | 2051657 | 104 | Distribution Circuit | Equipment Failure/Involved | Underground | 1278 | 132912 | 39.2226 | -121.0515 | No | Overcast-Rain;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0048424 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827632 | 0 | EPSS Ckt | N | 2023 | A-GRD
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 5121 | 20230319 | 737 | 20230319 | 828 | 2051778 | 51 | Distribution Circuit | Animal | Bird found | 16 | 816 | 38.7827 | -121.2331 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0048447 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1827657 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224580860222 | 20230319 | 848 | 20230319 | 1615 | 2051818 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 447 | 39.3091 | -120.3822 | No | Clear;Below 32 F | Transformer | Burned Open | 23-0048486 | OH | Sus | 45702863 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827696 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222852757489 | 20230319 | 1020 | 20230319 | 1228 | 2051711 | 128 | Transformer only | Vegetation | Tree - fell into line | 2 | 256 | 39.2408 | -120.9938 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) |  | 23-0048475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827685 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 7487 | 20230320 | 21 | 20230320 | 1347 | 2052514 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 17732 | 39.0798 | -121.0131 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048706 | OH | Sus | 31640092 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1827871 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 4107 | 20230320 | 842 | 20230320 | 1121 | 2052685 | 159 | Distribution Circuit | Animal | Bird found | 48 | 7632 | 38.858 | -120.849 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0048768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1827899 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5085 | 20230320 | 853 | 20230320 | 1057 | 2052703 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 8804 | 38.7933 | -121.1712 | No | Clear;32-90 F |  |  | 23-0048755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827892 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7129 | 20230320 | 902 | 20230320 | 955 | 2052721 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 848 | 39.2295 | -121.0779 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0048714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1827878 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223257643430 | 20230320 | 1057 | 20230320 | 1232 | 2052921 | 95 | Transformer only | Animal | Bird found | 2 | 190 | 38.8535 | -120.8569 | No | Overcast-Drizzle;32-90 F | Transformer | Burned Open | 23-0048840 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827913 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10531 | 20230320 | 1115 | 20230320 | 1130 | 2052776 | 15 | Distribution Circuit | Animal | Squirrel | 3 | 45 | 38.6891 | -120.6531 | No | Overcast-Drizzle;32-90 F | Pothead(Riser Termination) | Normal | 23-0048810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1827903 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 38311 | 20230321 | 652 | 20230321 | 856 | 2053591 | 124 | Distribution Circuit | Animal | Bird found | 20 | 2480 | 38.897 | -121.433 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0049146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1828057 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4289 | 20230321 | 710 | 20230321 | 1003 | 2053598 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3633 | 39.2328 | -121.1692 | Yes | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0049212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828088 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225531042749 | 20230321 | 1152 | 20230321 | 1702 | 2054187 | 310 | Transformer only | Environmental/External | Ice or snow | 1 | 310 | 38.8243 | -120.0594 | Yes | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0049911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828600 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8215 | 20230321 | 1410 | 20230321 | 1812 | 2054657 | 242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 5566 | 39.3817 | -120.9966 | Yes | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0049617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1828357 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 8651 | 20230321 | 1500 | 20230321 | 1617 | 2056820 | 77 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 385 | 38.8013 | -121.139 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0049784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1828492 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | FUSE | 12873 | 20230321 | 1518 | 20230321 | 2308 | 2057001 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 12220 | 38.6239 | -121.0232 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0049967 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1828653 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224587059775 | 20230321 | 1530 | 20230322 | 1748 | 2054692 | 1578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 9120 | 39.2973 | -120.3801 | Yes | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049747 | OH | Sus | 35433156 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828461 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 32615 | 20230321 | 1531 | 20230321 | 2232 | 2057240 | 421 | Distribution Circuit | Environmental/External | Lightning | 9 | 1797 | 39.2265 | -121.0692 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0049884 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828577 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38885 | 20230321 | 1533 | 20230321 | 1735 | 2057193 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2074 | 38.8234 | -121.116 | Yes | Overcast;32-90 F |  |  | 23-0049863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1828561 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6455 | 20230321 | 1534 | 20230321 | 1726 | 2057338 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 4928 | 39.1515 | -120.962 | Yes | Partly Cloudy;32-90 F |  |  | 23-0050000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1828685 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7541 | 20230321 | 1632 | 20230322 | 301 | 2059758 | 629 | Distribution Circuit | 3rd Party | Vehicle | 31 | 19499 | 39.2752 | -120.9619 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 23-0049991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1828678 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | FUSE | 34999 | 20230321 | 1713 | 20230321 | 1842 | 2059133 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 5270 | 38.7387 | -121.1567 | Yes | Clear-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 23-0050017 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828700 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | OCB | 1101/2 | 20230321 | 1759 | 20230322 | 1019 | 2059736 | 980 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2927 | 156580 | 38.9006 | -121.2941 | Yes | Partly Cloudy;32-90 F | Insulator | Burned/flashed | 23-0049995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1828680 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6187 | 20230321 | 1847 | 20230322 | 1212 | 2060046 | 1045 | Distribution Circuit | 3rd Party | Vehicle | 142 | 148390 | 39.0605 | -120.984 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050086 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1828759 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222881055340 | 20230321 | 1936 | 20230322 | 939 | 2060178 | 843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 843 | 39.1816 | -120.9846 | Yes | Overcast-Drizzle;32-90 F | Cutout- fuse holder | Broken | 23-0050105 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828775 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | TRANSFORMER | T0042 | 20230321 | 2041 | 20230322 | 255 | 2060669 | 374 | Transformer only | Vegetation | Tree - fell into line | 16 | 5984 | 38.6942 | -121.0838 | Yes | Clear;32-90 F | Secondary | Arcing | 23-0050236 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1828896 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3957 | 20230322 | 1410 | 20230322 | 1745 | 2062915 | 215 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 18 | 3870 | 39.1854 | -121.0277 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050739 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1829212 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8107 | 20230322 | 1836 | 20230323 | 1411 | 2063576 | 1175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 112800 | 39.3524 | -121.0655 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0050993 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1829380 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 63823 | 20230323 | 653 | 20230323 | 1022 | 2064067 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 11495 | 38.859 | -120.8472 | No | Overcast-Fog;32-90 F |  |  | 23-0051217 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829547 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6003 | 20230323 | 846 | 20230323 | 1010 | 2064220 | 84 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 1 | 84 | 39.02 | -120.848 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0051212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1829544 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20230323 | 1048 | 20230323 | 1343 | 2064479 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 95 | 16625 | 38.9858 | -121.022 | No | Overcast;32-90 F |  |  | 23-0051346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829621 | 0 | EPSS Ckt | N | 2023 | POS 1 & 3
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 34553 | 20230323 | 1110 | 20230323 | 1204 | 2064522 | 54 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 702 | 38.9156 | -120.7781 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0051319 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1829603 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 290705 | 20230323 | 1600 | 20230323 | 1851 | 2065055 | 171 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 17344 | 38.687 | -120.8138 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1829726 | 0 | EPSS Ckt | N | 2023 | B GRD
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 5251 | 20230323 | 1945 | 20230323 | 2112 | 2065353 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1305 | 39.2355 | -121.2593 | No | Overcast-Drizzle;32-90 F |  |  | 23-0051631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1829785 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30569 | 20230323 | 1945 | 20230323 | 2207 | 2065354 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1988 | 38.9618 | -120.7168 | No | Overcast-Rain;32-90 F |  |  | 23-0051652 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829804 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 3999 | 20230323 | 2006 | 20230324 | 1137 | 2065368 | 931 | Distribution Circuit | Environmental/External | Lightning | 7 | 6517 | 39.2091 | -121.0559 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0051629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829782 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 9457 | 20230324 | 702 | 20230324 | 914 | 2065606 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4224 | 38.9014 | -121.1816 | No | Partly Cloudy;32-90 F |  |  | 23-0051750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829856 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222818056464 | 20230324 | 853 | 20230324 | 1008 | 2065727 | 75 | Transformer only | 3rd Party | Customer Equipment | 1 | 75 | 39.2128 | -121.0064 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0051809 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1829882 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6361 | 20230324 | 1117 | 20230324 | 1403 | 2065968 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 996 | 39.1567 | -120.8896 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0051844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829895 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 35861 | 20230324 | 1311 | 20230324 | 1602 | 2066122 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 6669 | 38.9081 | -120.8563 | No | Partly Cloudy;32-90 F |  |  | 23-0051992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1829965 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 346 | 20230324 | 2317 | 20230325 | 1130 | 2066653 | 733 | Distribution Circuit | 3rd Party | Vehicle | 979 | 213731 | 38.8253 | -121.1632 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0052279 | OH | Sus | 31640348 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830240 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7841 | 20230325 | 1016 | 20230325 | 1952 | 2066907 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 16272 | 39.1416 | -121.1433 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0052476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830436 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 36439 | 20230325 | 1053 | 20230325 | 1210 | 2066928 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 308 | 38.7381 | -121.1885 | No | Clear;32-90 F |  |  | 23-0052482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1830442 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224028040100 | 20230325 | 1705 | 20230325 | 1728 | 2067189 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 414 | 38.7592 | -120.5882 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0052535 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830485 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5381 | 20230326 | 852 | 20230326 | 1042 | 2067536 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 4070 | 38.9235 | -121.1807 | No | Clear;32-90 F |  |  | 23-0052654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1830597 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223374556595 | 20230327 | 1056 | 20230327 | 1841 | 2068594 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 930 | 39.2146 | -120.8102 | No | Clear;Below 32 F | Transformer (OH) | Normal | 23-0053050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830847 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6647 | 20230327 | 1105 | 20230327 | 1701 | 2068596 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 18156 | 39.3066 | -120.3821 | No | Partly Cloudy;Below 32 F | Pole-Wood | Broken | 23-0052894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830792 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | TRANSFORMER | 223789059795 | 20230327 | 1203 | 20230327 | 1810 | 2068704 | 367 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 367 | 39.3013 | -120.6616 | No | Clear;32-90 F | Jumper | Broken | 23-0053064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830854 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33257 | 20230327 | 1300 | 20230327 | 1337 | 2068785 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 37 | 39.1899 | -120.966 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0052980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830823 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6379 | 20230327 | 1532 | 20230327 | 1722 | 2069013 | 110 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1430 | 39.2052 | -120.8318 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0053069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830857 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18493 | 20230327 | 1534 | 20230327 | 1647 | s1830881 | 73 | Distribution Circuit | Animal | Squirrel | 5 | 365 | 38.7053 | -120.8418 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0053116 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830881 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39055 | 20230327 | 1650 | 20230328 | 17 | 2069177 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2235 | 39.0419 | -121.0691 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0053120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830883 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21587 | 20230327 | 1718 | 20230327 | 2115 | 2069181 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 4029 | 38.6825 | -120.854 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0053137 | OH | Sus | 31640553 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830896 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 40783 | 20230327 | 2213 | 20230327 | 2328 | 2069421 | 75 | Distribution Circuit | Animal | Bird found | 38 | 2850 | 38.7667 | -121.1775 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0053203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1830956 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20230328 | 644 | 20230328 | 1342 | 2069525 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 18399 | 39.2132 | -121.0136 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053280 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831003 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2084 | 20230328 | 811 | 20230328 | 1729 | 2069629 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 127804 | 39.0318 | -120.9741 | No | Overcast;32-90 F | Service conductor | Broken | 23-0053287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1831008 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6361 | 20230328 | 823 | 20230329 | 1229 | 2071971 | 1686 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 5058 | 39.1567 | -120.8896 | No | Overcast;32-90 F |  |  | 23-0053914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831395 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33577 | 20230328 | 823 | 20230329 | 1229 | 2073091 | 1686 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 5058 | 39.1691 | -120.893 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0053914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831635 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222564850928 | 20230328 | 845 | 20230329 | 1133 | 2069866 | 1608 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1608 | 39.0612 | -121.0987 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0053645 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1831229 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2101 | 153132101 | OCB | 2101/2 | 20230328 | 846 | 20230330 | 1822 | 2069791 | 3456 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 545 | 124909 | 39.2354 | -121.2691 | No | Overcast-Drizzle;32-90 F |  |  | 23-0053303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831022 | 0 | EPSS Ckt | N | 2023 | GRD & TIME OC
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4529 | 20230328 | 853 | 20230328 | 1712 | 2069821 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10978 | 39.2269 | -121.1413 | No | Overcast;32-90 F | Conductor- Overhead | On Ground | 23-0053383 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831080 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | T1381 | 20230328 | 901 | 20230328 | 1400 | 2070008 | 299 | Transformer only | Equipment Failure/Involved | Overhead | 27 | 8073 | 39.2495 | -121.0289 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0053656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831236 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230328 | 908 | 20230329 | 1117 | 2069856 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 2003 | 412640 | 39.0997 | -121.05 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0053335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831048 | 0 | EPSS Ckt | N | 2023 | A GRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1130 | 20230328 | 908 | 20230328 | 1055 | 2069855 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 291 | 31137 | 38.9127 | -120.9157 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 23-0053319 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831038 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 20230328 | 912 | 20230328 | 1319 | 2069869 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 10127 | 39.0098 | -120.8455 | No | Clear-Strong Winds;32-90 F |  |  | 23-0053593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831202 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5381 | 20230328 | 912 | 20230328 | 1143 | 2069865 | 151 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 5587 | 38.9235 | -121.1807 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053393 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831083 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8951 | 20230328 | 913 | 20230328 | 1943 | 2070014 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4410 | 39.1794 | -120.976 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053579 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831192 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3087 | 20230328 | 919 | 20230328 | 1215 | 2069901 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 13200 | 38.9049 | -120.8402 | No | Clear-Strong Winds;32-90 F |  |  | 23-0053528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831161 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5767 | 20230328 | 922 | 20230329 | 1222 | 2069911 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 56700 | 38.9718 | -121.0364 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831359 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31339 | 20230328 | 922 | 20230328 | 1654 | 2069910 | 452 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 1356 | 38.895 | -120.9936 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0053793 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831307 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6365 | 20230328 | 924 | 20230328 | 1454 | 2069915 | 330 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 7920 | 39.1734 | -120.8591 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0053716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831274 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | JUMPER | OJ TWDS CGC #222637043456 | 20230328 | 927 | 20230328 | 1740 | 2070062 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 493 | 38.8559 | -121.0753 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0053573 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831191 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRIP-SAVER | 6175 | 20230328 | 927 | 20230328 | 1852 | 2069929 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 34465 | 39.036 | -121.0041 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831150 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 32571 | 20230328 | 928 | 20230329 | 1047 | 2069935 | 1519 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 28861 | 39.212 | -121.0447 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053587 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831197 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 50172 | 20230328 | 929 | 20230328 | 1827 | 2069978 | 538 | Distribution Circuit | Vegetation | Tree - branch fell on line | 341 | 140973 | 38.9458 | -121.1226 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053367 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1831070 | 0 | EPSS Ckt | N | 2023 | A B C GRD
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5431 | 20230328 | 930 | 20230329 | 1120 | 2069944 | 1550 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29385 | 38.9009 | -121.1458 | No | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0053806 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831317 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33169 | 20230328 | 933 | 20230328 | 1900 | 2069993 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5670 | 39.2523 | -121.0236 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053605 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831209 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20230328 | 933 | 20230328 | 1837 | 2069989 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 198528 | 39.2034 | -121.0788 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831064 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 6261 | 20230328 | 933 | 20230329 | 1324 | 2069955 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 17084 | 39.0414 | -120.9982 | No | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0053470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831125 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 39745 | 20230328 | 936 | 20230328 | 1445 | 2069971 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 11124 | 38.9246 | -121.0894 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0053551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831179 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 3675 | 20230328 | 936 | 20230328 | 1546 | 2069977 | 370 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 5920 | 39.0552 | -121.1498 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831244 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 39067 | 20230328 | 936 | 20230328 | 1246 | 2070012 | 190 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 15801 | 39.0507 | -121.061 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053515 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831158 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 4163 | 20230328 | 937 | 20230328 | 1219 | 2069981 | 162 | Distribution Circuit | Company Initiated | Coordination failure | 21 | 3402 | 38.8381 | -120.851 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831186 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32349 | 20230328 | 937 | 20230328 | 1822 | 2070556 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1575 | 38.8398 | -120.8531 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831187 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5993 | 20230328 | 939 | 20230328 | 1903 | 2070002 | 564 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 14664 | 38.9242 | -121.1435 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831363 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1511 | 20230328 | 944 | 20230328 | 1017 | 2070034 | 33 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 3894 | 38.7377 | -120.7124 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0053409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831091 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 84017 | 20230328 | 945 | 20230328 | 1401 | 2070029 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1024 | 38.9121 | -121.2416 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053661 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831239 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8483 | 20230328 | 951 | 20230329 | 1122 | 2070048 | 1531 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 108701 | 39.0185 | -121.0227 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053788 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831303 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 3127 | 20230328 | 957 | 20230328 | 1943 | 2070064 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9962 | 38.9856 | -121.1101 | No | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831182 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7013 | 20230328 | 1000 | 20230328 | 1152 | 2070087 | 112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 6720 | 39.162 | -121.0389 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053499 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831147 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5247 | 20230328 | 1002 | 20230328 | 1651 | 2070082 | 409 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 6135 | 38.853 | -121.1528 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053796 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831309 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222523844749 | 20230328 | 1002 | 20230328 | 1940 | 2070187 | 578 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 578 | 38.8918 | -121.1138 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Contaminated | 23-0053908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831391 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223915239944 | 20230328 | 1004 | 20230328 | 1046 | 2070088 | 42 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 168 | 38.7557 | -120.6273 | No | Strong Winds-Rain-Overcast;32-90 F | Transformer | Normal | 23-0053437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831103 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | RECLOSER | 251946 | 20230328 | 1007 | 20230328 | 2101 | 2070116 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 992 | 171371 | 38.904 | -121.0666 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053401 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831088 | 0 | EPSS Ckt | N | 2023 | B & GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ'S 1 E/OF CGC 222914155088 | 20230328 | 1008 | 20230328 | 1523 | 2070105 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 315 | 39.1747 | -120.9731 | No | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken | 23-0053392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831082 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11859 | 20230328 | 1009 | 20230328 | 1751 | 2070106 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 37266 | 38.6748 | -120.9573 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053474 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831129 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20230328 | 1011 | 20230328 | 1742 | 2070118 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 18942 | 38.6321 | -120.9241 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053594 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831203 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | OTHER | WIRE DOWN @ CGC222598845787 | 20230328 | 1012 | 20230328 | 1644 | 2070124 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 61236 | 38.9203 | -121.0879 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | Yes | 1831117 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | RECLOSER | 284874 | 20230328 | 1013 | 20230328 | 1339 | 2070139 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 33990 | 38.9105 | -121.0868 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0053410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831092 | 0 | EPSS Ckt | N | 2023 | B C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10019 | 20230328 | 1014 | 20230329 | 1123 | 2070132 | 1509 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 135810 | 38.5706 | -120.6952 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053745 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831281 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223012841286 | 20230328 | 1015 | 20230328 | 1340 | 2070154 | 205 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 410 | 38.796 | -120.9438 | No | Strong Winds-Overcast-Drizzle;32-90 F |  |  | 23-0053536 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1831165 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5263 | 20230328 | 1016 | 20230328 | 1934 | 2070135 | 558 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 6696 | 38.8414 | -121.1535 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053835 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831339 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222624146152 | 20230328 | 1020 | 20230328 | 1821 | 2070789 | 481 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 3367 | 38.93 | -121.0785 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0053666 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831241 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222624246115 | 20230328 | 1020 | 20230328 | 1821 | 2070798 | 481 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3848 | 38.929 | -121.0786 | No | Overcast-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 23-0053670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831245 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 32061 | 20230328 | 1022 | 20230328 | 1702 | 2070150 | 400 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 9872 | 38.8314 | -121.1685 | No | Overcast-Rain;32-90 F |  |  | 23-0053819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831328 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4483 | 20230328 | 1023 | 20230328 | 1154 | 2070160 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 3185 | 38.9059 | -120.9756 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 23-0053501 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831149 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 33893 | 20230328 | 1024 | 20230328 | 1935 | 2070162 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8265 | 39.0379 | -120.9726 | No | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053546 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831174 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6341 | 20230328 | 1028 | 20230328 | 1916 | 2070182 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 16407 | 39.125 | -120.9435 | No | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831176 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6943 | 20230328 | 1052 | 20230328 | 1445 | 2070241 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 5592 | 38.8449 | -120.8227 | No | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 23-0053701 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831267 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 4657 | 20230328 | 1141 | 20230328 | 1235 | 2070358 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 432 | 39.2505 | -121.0135 | No | Overcast-Heavy Rain;32-90 F | Insulator | Broken | 23-0053480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1831133 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38885 | 20230328 | 1243 | 20230328 | 1809 | 2070566 | 326 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 5542 | 38.8234 | -121.116 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831293 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222374045340 | 20230328 | 1246 | 20230329 | 1400 | 2070578 | 1514 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3028 | 38.9084 | -121.1673 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 23-0053827 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831334 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 5613 | 20230328 | 1301 | 20230328 | 2133 | 2070602 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 21504 | 38.9181 | -121.0537 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0053792 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831306 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20230328 | 1312 | 20230329 | 1127 | 2070304 | 1335 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 78389 | 38.9239 | -120.9071 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053668 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831243 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 9503 | 20230328 | 1312 | 20230328 | 1813 | 2070630 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 15351 | 39.056 | -120.9978 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0053687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831258 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20230328 | 1348 | 20230328 | 1417 | 2070718 | 29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 986 | 39.2132 | -121.0136 | No | Overcast-Fog-Heavy Rain;32-90 F | Fuse | Normal | 23-0053651 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831234 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22331 | 20230328 | 1416 | 20230328 | 1716 | 2070791 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 8820 | 38.6538 | -120.9298 | No | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0053817 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831326 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 34935 | 20230328 | 1429 | 20230328 | 2044 | 2070823 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 746 | 39.0519 | -121.0712 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053749 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831283 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222448341204 | 20230328 | 1507 | 20230329 | 1209 | 2070891 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2524 | 38.7949 | -121.1417 | No | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Broken | 23-0053767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831294 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2140 | 20230328 | 1553 | 20230328 | 1819 | 2070996 | 146 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 88038 | 39.2895 | -120.9854 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0053769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831295 | 0 | EPSS Ckt | N | 2023 | A B
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 6837 | 20230328 | 1610 | 20230328 | 1817 | 2071016 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 6604 | 38.9977 | -121.0232 | No | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0053856 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831351 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | FUSE | 7409 | 20230328 | 1612 | 20230328 | 1706 | 2071019 | 54 | Distribution Circuit | Vegetation | Tree - branch fell on line | 167 | 9018 | 39.216 | -121.0657 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0053821 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831330 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222599551745 | 20230328 | 1616 | 20230329 | 1404 | 2071045 | 1308 | Transformer only | Vegetation | Tree - bark fell into line | 3 | 3924 | 39.0835 | -121.0857 | No | Partly Cloudy-Heavy Rain-Fog;32-90 F | Transformer | Broken | 23-0053832 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831337 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 20230328 | 1625 | 20230329 | 1207 | 2071052 | 1182 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 102834 | 39.3404 | -121.1319 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831304 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 31299 | 20230328 | 1633 | 20230328 | 2003 | 2071067 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1470 | 39.0936 | -121.085 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0053912 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831394 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5359 | 20230328 | 1641 | 20230328 | 1850 | 2071103 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 8256 | 38.8842 | -121.1543 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F |  |  | 23-0053878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831362 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7215 | 20230328 | 1643 | 20230328 | 1945 | 2071183 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 10920 | 39.2218 | -121.1488 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0053903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831386 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222736349131 | 20230328 | 1644 | 20230329 | 1215 | 2071312 | 1171 | Transformer only | Vegetation | Tree - fell into line | 1 | 1171 | 39.0107 | -121.0382 | No | Snow-Overcast-Fog;32-90 F | Transformer | Broken | 23-0053892 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831375 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 34063 | 20230328 | 1657 | 20230329 | 1734 | 2072781 | 1206 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5236 | 39.0768 | -121.0549 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 23-0054237 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831577 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7755 | 20230328 | 1659 | 20230329 | 1025 | 2071162 | 1046 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17782 | 39.0778 | -121.0865 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831348 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13789 | 20230328 | 1705 | 20230329 | 1258 | 2071201 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 53685 | 38.5961 | -120.8061 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831364 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 5025 | 20230328 | 1719 | 20230328 | 1955 | 2071222 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3432 | 39.1313 | -121.0714 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0053905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831387 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19732 | 20230328 | 1725 | 20230328 | 2302 | 2071233 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 1205 | 156401 | 38.7367 | -120.784 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831340 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OCB | 1104/2 | 20230328 | 1731 | 20230328 | 2130 | 2071294 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2571 | 178881 | 39.2314 | -121.0346 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Together | 23-0053844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1831344 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222624952902 | 20230328 | 1800 | 20230329 | 1058 | 2071331 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1262 | 39.1157 | -121.0755 | No | Overcast-Fog-Snow;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0053895 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831378 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 861610 | 20230328 | 1800 | 20230329 | 1306 | 2071335 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 1206 | 574912 | 39.0467 | -121.0715 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831354 | 0 | EPSS Ckt | N | 2023 | A GRD
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | OCB | 1101/2 | 20230328 | 1804 | 20230329 | 1620 | 2071371 | 1336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 412 | 494692 | 39.4382 | -120.9964 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0053866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831357 | 0 | EPSS Ckt | N | 2023 | INSTA OC
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8107 | 20230328 | 1806 | 20230329 | 1922 | 2071342 | 1516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 145536 | 39.3524 | -121.0655 | No | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken | 23-0054212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831566 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20230328 | 1807 | 20230329 | 1949 | 2071351 | 1542 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 63222 | 39.3451 | -121.0765 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0054344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831623 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 8801 | 20230328 | 1810 | 20230330 | 1544 | 2074232 | 2734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 47413 | 39.4946 | -120.9972 | No | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Normal | 23-0054906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831926 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20230328 | 1814 | 20230330 | 1619 | 2071950 | 2765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 229495 | 39.4883 | -120.8571 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0053916 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1831397 | 0 | EPSS Ckt | N | 2023 | A C GRD
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 4169 | 20230328 | 1842 | 20230328 | 2118 | 2071444 | 156 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6240 | 39.11 | -121.0303 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Together | 23-0053927 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831408 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 852240 | 20230328 | 1844 | 20230329 | 1457 | 2071852 | 1213 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 30696 | 39.2599 | -121.0236 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0053969 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1831447 | 0 | EPSS Ckt | N | 2023 | A+B+C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33795 | 20230328 | 1846 | 20230329 | 1330 | 2071919 | 1124 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3372 | 39.1997 | -121.0106 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831648 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 4173 | 20230328 | 1858 | 20230328 | 2213 | 2071592 | 195 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 19110 | 39.109 | -121.0302 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0053926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831407 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20230328 | 1859 | 20230329 | 1641 | 2071657 | 1302 | Distribution Circuit | 3rd Party | Vehicle | 613 | 182496 | 38.9 | -120.9074 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831371 | 0 | EPSS Ckt | N | 2023 | A B C
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 9909 | 20230328 | 1901 | 20230329 | 1338 | 2071728 | 1117 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 25354 | 38.951 | -121.0395 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053922 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831402 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7397 | 20230328 | 1912 | 20230329 | 1137 | 2071850 | 985 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 44325 | 39.2604 | -120.9764 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0053896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831379 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9703 | 20230328 | 1913 | 20230329 | 1431 | 2071909 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 69480 | 39.1681 | -121.0295 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831633 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7539 | 20230328 | 1914 | 20230329 | 1426 | 2071860 | 1152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 31104 | 39.3084 | -120.971 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0054450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831664 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9257 | 20230328 | 1917 | 20230329 | 1900 | 2072467 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 65458 | 39.2008 | -120.932 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831729 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7469 | 20230328 | 1922 | 20230329 | 1111 | 2071915 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 73073 | 39.2081 | -120.9493 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831600 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222945755694 | 20230328 | 1923 | 20230329 | 1313 | 2072601 | 1070 | Transformer only | Vegetation | Tree - fell into line | 1 | 1070 | 39.1914 | -120.9621 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 23-0054118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831533 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 31377 | 20230328 | 1924 | 20230329 | 1654 | 2071899 | 1290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 49020 | 39.0323 | -121.0725 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0054599 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831706 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 6571 | 20230328 | 1930 | 20230329 | 1549 | 2071916 | 1219 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23161 | 39.314 | -120.9832 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831686 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7715 | 20230328 | 1946 | 20230329 | 1407 | 2073087 | 1101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 9909 | 39.2724 | -120.9688 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0054372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831634 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | OTHER | HOT WIRE DOWN | 20230328 | 1948 | 20230329 | 1734 | 2071955 | 1306 | Distribution Circuit | Vegetation | Tree - fell into line | 1652 | 131505 | 38.9763 | -121.0252 | No | Partly Cloudy-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0053923 | OH | Sus | 35434046 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | Yes | 1831403 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9493 | 20230328 | 1956 | 20230329 | 1723 | 2071961 | 1287 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 25740 | 39.1867 | -120.9467 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831707 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 994353 | 20230328 | 2006 | 20230329 | 1206 | 2071308 | 960 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13447 | 38.8312 | -121.1678 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0054108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831526 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30353 | 20230328 | 2021 | 20230329 | 1806 | 2072021 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11850 | 39.1214 | -121.0293 | No | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0054097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831521 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6697 | 20230328 | 2022 | 20230328 | 2039 | 2072030 | 17 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 476 | 39.1942 | -120.9935 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0053924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831404 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20230328 | 2022 | 20230329 | 940 | 2071889 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 46284 | 39.1894 | -120.9612 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054113 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831531 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 20230328 | 2036 | 20230329 | 1434 | 2072042 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14014 | 39.2097 | -120.9435 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831680 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | OTHER | WIRE DOWN E/OF CGC 222861555725 | 20230328 | 2050 | 20230329 | 1901 | 2073433 | 1331 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 9158 | 39.1924 | -120.9917 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054538 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1831685 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRIP-SAVER | 5731 | 20230328 | 2105 | 20230329 | 1242 | 2072127 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 88224 | 38.9858 | -121.022 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053959 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831440 | 1 | EPSS Ckt | N | 2023 | #2 fuse saver open- no targets
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9377 | 20230328 | 2108 | 20230329 | 1057 | 2072085 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 124350 | 38.9084 | -120.8476 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054232 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831576 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | 222601245921 | 20230328 | 2117 | 20230329 | 845 | 2072039 | 688 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2064 | 38.9239 | -121.0869 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Jumper | Burned Open | 23-0053930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831411 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 20695 | 20230328 | 2140 | 20230329 | 1233 | 2072112 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10716 | 38.8331 | -120.8124 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831534 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 4257 | 20230328 | 2146 | 20230329 | 1317 | 2072116 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 37240 | 39.1039 | -121.0923 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054379 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831636 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 4997 | 20230328 | 2209 | 20230328 | 2240 | 2072169 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 13640 | 38.9892 | -120.8829 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0053970 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831448 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8755 | 20230329 | 26 | 20230329 | 1155 | 2072192 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 55120 | 39.1913 | -120.9937 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831607 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7157 | 20230329 | 48 | 20230329 | 1117 | 2072368 | 629 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 15725 | 39.2452 | -121.0035 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Together | 23-0054218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831568 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20230329 | 255 | 20230331 | 1006 | 2072241 | 3311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 130262 | 39.4655 | -120.8443 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0053985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831463 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8003 | 20230329 | 255 | 20230331 | 1514 | 2074367 | 3619 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7238 | 39.4456 | -120.8237 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0054974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831954 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33733 | 20230329 | 515 | 20230329 | 1326 | 2072290 | 491 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 982 | 39.1785 | -121.0285 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831640 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 20749 | 20230329 | 800 | 20230329 | 1230 | 2072422 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1080 | 38.832 | -120.8169 | No | Overcast;32-90 F |  |  | 23-0054310 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831608 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223959438096 | 20230329 | 841 | 20230329 | 1024 | 2072621 | 103 | Transformer only | Environmental/External | Ice or snow | 3 | 309 | 38.7041 | -120.6135 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0054132 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831537 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 542186 | 20230329 | 915 | 20230329 | 1914 | 2072600 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 55108 | 39.2144 | -120.8088 | No | Partly Cloudy-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0054144 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831541 | 0 | EPSS Ckt | N | 2023 | C
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224106039880 | 20230329 | 939 | 20230329 | 957 | 2072636 | 18 | Transformer only | Environmental/External | Ice or snow | 3 | 54 | 38.7525 | -120.5609 | No | Partly Cloudy;Below 32 F | Fuse | Normal | 23-0054169 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831550 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224095339882 | 20230329 | 939 | 20230329 | 1038 | 2072700 | 59 | Transformer only | Environmental/External | Ice or snow | 2 | 118 | 38.7526 | -120.5644 | No | Partly Cloudy;Below 32 F | Fuse | Normal | 23-0054185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831553 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224098039957 | 20230329 | 944 | 20230329 | 1102 | 2072671 | 78 | Transformer only | Vegetation | Tree - fell into line | 3 | 234 | 38.7544 | -120.5636 | No | Partly Cloudy;Below 32 F | Transformer | Arcing | 23-0054197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831560 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224010739430 | 20230329 | 949 | 20230329 | 1119 | 2072684 | 90 | Transformer only | Environmental/External | Ice or snow | 2 | 180 | 38.7397 | -120.5957 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0054272 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831589 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 875388 | 20230329 | 1009 | 20230330 | 1304 | 2072720 | 1402 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 107768 | 39.2827 | -120.9454 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0054194 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831558 | 0 | EPSS Ckt | N | 2023 | A & B
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9785 | 20230329 | 1038 | 20230329 | 1137 | 2072771 | 59 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 236 | 39.162 | -121.0627 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0054224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831573 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5833 | 20230329 | 1039 | 20230329 | 1434 | 2072683 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5640 | 38.8552 | -120.8433 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 23-0054263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831587 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3991 | 20230329 | 1050 | 20230329 | 1217 | 2072772 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 522 | 39.3935 | -121.1101 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0054227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831575 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223991040742 | 20230329 | 1056 | 20230329 | 1109 | 2072808 | 13 | Transformer only | Environmental/External | Ice or snow | 2 | 26 | 38.7754 | -120.5988 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0054248 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831583 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7467 | 20230329 | 1106 | 20230329 | 1539 | 2072766 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 546 | 39.0729 | -121.094 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0054221 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831569 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3891 | 20230329 | 1158 | 20230329 | 1638 | 2073015 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 8680 | 39.2197 | -120.9493 | No | Overcast-Drizzle;32-90 F |  |  | 23-0054583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831701 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 7353 | 20230329 | 1214 | 20230329 | 1551 | 2073018 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2604 | 39.2125 | -120.8167 | No | Overcast-Fog-Snow;Below 32 F | Lightning Arrestor | Failed/Faulted | 23-0054541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831688 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20230329 | 1221 | 20230329 | 1827 | 2073036 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5322 | 39.2095 | -120.827 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Failed/Faulted | 23-0054502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831676 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6373 | 20230329 | 1408 | 20230329 | 1629 | 2073224 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3856 | 39.1972 | -120.833 | No | Overcast-Fog-Snow;Below 32 F | Lightning Arrestor | Burned/flashed | 23-0054507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831677 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | T7650 | 20230329 | 1456 | 20230330 | 1304 | 2073318 | 1328 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1328 | 39.3173 | -120.3576 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0054949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831945 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJS 1 SPAN SS OF CGC 222412656689 | 20230329 | 1600 | 20230331 | 1103 | 2073465 | 2583 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2583 | 39.2208 | -121.1486 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Broken | 23-0054598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831704 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33253 | 20230329 | 1721 | 20230330 | 1142 | 2073532 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1101 | 39.1779 | -120.9564 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0054622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831725 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 20230329 | 2001 | 20230330 | 1146 | 2073697 | 945 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 59 | 55755 | 39.2173 | -120.8092 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0054704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831794 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | FLYERS 1 S/OF CGC 222941059335 | 20230330 | 830 | 20230330 | 1115 | 2074000 | 165 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 330 | 39.2909 | -120.9618 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 23-0054803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831852 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 3349 | 20230330 | 846 | 20230330 | 1215 | 2074023 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1881 | 38.7751 | -120.4256 | No | Clear;Below 32 F |  |  | 23-0055014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831968 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 5979 | 20230330 | 912 | 20230330 | 920 | 2074127 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 72 | 38.918 | -121.072 | No | Partly Cloudy;32-90 F |  |  | 23-0054858 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831896 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224098940013 | 20230330 | 1026 | 20230330 | 1033 | 2074191 | 7 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 21 | 38.7561 | -120.5632 | No | Partly Cloudy;32-90 F | Jumper | Arcing | 23-0054888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831916 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | JUMPER | BURNT OPEN JUMPER HS OF 38131 | 20230330 | 1309 | 20230330 | 1447 | 2074480 | 98 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1764 | 39.3117 | -120.3826 | No | Clear;32-90 F | Jumper | Burned Open | 23-0055129 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1831994 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 30757 | 20230330 | 1346 | 20230330 | 1548 | 2074521 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 814 | 39.2897 | -120.9153 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0055125 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831993 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 88079 | 20230330 | 1512 | 20230330 | 2226 | 2074584 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1736 | 38.9115 | -121.1635 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0055151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831999 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 5979 | 20230330 | 1727 | 20230330 | 1931 | 2074713 | 124 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 2208 | 38.918 | -121.072 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 23-0055217 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1832019 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 4879 | 20230330 | 2209 | 20230331 | 23 | 2074921 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 8844 | 39.091 | -121.0013 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0055297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1832093 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 9123 | 20230331 | 24 | 20230331 | 153 | 2074987 | 89 | Distribution Circuit | Vegetation | Tree - bark fell into line | 134 | 11926 | 38.7569 | -120.693 | No | Overcast;32-90 F | Conductor- Overhead | Together | 23-0055301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1832097 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | TRANSFORMER | 222625445032 | 20230331 | 1009 | 20230331 | 1301 | 2075335 | 172 | Transformer only | Vegetation | Tree - branch fell on line | 17 | 2924 | 38.8995 | -121.0785 | No | Partly Cloudy;32-90 F | Transformer | Bent or Twisted | 23-0055543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1832210 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 419207 | 20230331 | 1117 | 20230331 | 1501 | 2075382 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1344 | 38.7749 | -120.4001 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1832204 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 5121 | 20230331 | 1121 | 20230331 | 1203 | 2075394 | 42 | Distribution Circuit | Animal | Bird found | 16 | 672 | 38.7827 | -121.2331 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0055540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1832208 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224571460285 | 20230331 | 1132 | 20230331 | 1209 | 2075409 | 37 | Transformer only | Company Initiated | Construction Activity/equip- company | 3 | 111 | 39.3113 | -120.3855 | No | Clear;32-90 F | Service conductor | Broken | 23-0055551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1832213 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 5979 | 20230331 | 1203 | 20230331 | 1211 | 2075443 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 12 | 96 | 38.918 | -121.072 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0055217 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1832215 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 39323 | 20230331 | 1224 | 20230331 | 1404 | 2075451 | 100 | Distribution Circuit | Animal | Bird found | 3 | 300 | 38.8595 | -121.1421 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1832229 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 889106 | 20230331 | 1308 | 20230331 | 1451 | 2075500 | 103 | Distribution Circuit | Environmental/External | Ice or snow | 10 | 931 | 38.8035 | -120.046 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1832227 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 20230331 | 1320 | 20230331 | 1329 | 2075510 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1278 | 39.3638 | -120.7923 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0053985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1832233 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6649 | 20230331 | 1417 | 20230331 | 1515 | 2075540 | 58 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 1450 | 39.3034 | -120.3812 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0055603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1832236 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 12037 | 20230331 | 1846 | 20230331 | 2005 | 2075781 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 3952 | 38.6944 | -120.8152 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0055673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1832270 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18453 | 20230401 | 804 | 20230401 | 1041 | 2076502 | 157 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1727 | 38.7412 | -120.6977 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0055836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832447 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32349 | 20230401 | 1343 | 20230401 | 1940 | 2076763 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 543 | 38.8398 | -120.8531 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1832473 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222495060485 | 20230401 | 1523 | 20230401 | 2045 | 2076821 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 644 | 39.3246 | -121.1201 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1832481 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7721 | 20230401 | 2003 | 20230401 | 2102 | 2076997 | 59 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 295 | 39.0138 | -121.327 | No | Overcast;32-90 F |  |  | 23-0055900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832496 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32345 | 20230401 | 2005 | 20230401 | 2347 | 2076998 | 222 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2220 | 38.8325 | -120.8465 | No | Clear;32-90 F |  |  | 23-0055985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832580 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | SWITCH | 22209 | 20230402 | 1022 | 20230402 | 1047 | 2077379 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1186 | 22183 | 38.7354 | -120.7937 | No | Overcast-Fog-Drizzle;32-90 F | Switch (OH) | Normal | 23-0053836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Open Circuit | 0 | No | No | No | 1832613 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224579760131 | 20230402 | 1037 | 20230402 | 1124 | 2077362 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 94 | 39.3066 | -120.3827 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 23-0056015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1832610 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224379060490 | 20230402 | 1223 | 20230402 | 1307 | 2077374 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 44 | 39.3168 | -120.4542 | No | Overcast-Fog;Below 32 F | Secondary | Broken | 23-0056033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1832626 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 5637 | 20230402 | 1748 | 20230402 | 1857 | 2077599 | 69 | Distribution Circuit | Animal | Bird found | 1 | 69 | 38.93 | -121.0937 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0056059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832651 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11567 | 20230403 | 1148 | 20230403 | 1210 | 2078326 | 22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 88 | 38.6948 | -120.9409 | No | Clear;32-90 F |  |  | 23-0056339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832854 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 35597 | 20230403 | 1309 | 20230403 | 1535 | 2078397 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 146 | 38.7515 | -121.4624 | No | Clear;32-90 F |  |  | 23-0056480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1832919 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 38309 | 20230403 | 1312 | 20230403 | 1411 | 2078371 | 59 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2 | 118 | 38.8967 | -121.4809 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0056392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1832874 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20230403 | 2029 | 20230404 | 453 | 2079368 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 27000 | 39.1995 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833020 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223464046100 | 20230404 | 726 | 20230404 | 1640 | 2079568 | 554 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 554 | 38.9261 | -120.7835 | No | Clear;Below 32 F | Cutout- fuse holder | Normal | 23-0057115 | OH | Sus | 31641299 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1833264 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22321 | 20230404 | 759 | 20230404 | 938 | 2079622 | 99 | Distribution Circuit | Animal | Bird found | 19 | 1881 | 38.6735 | -120.9282 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056860 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833207 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222844957958 | 20230404 | 921 | 20230404 | 2111 | 2079772 | 710 | Transformer only | Vegetation | Tree - fell into line | 4 | 2840 | 39.2531 | -120.9981 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0056841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833193 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222745054520 | 20230404 | 1117 | 20230404 | 1722 | 2079756 | 365 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 365 | 39.1602 | -121.0328 | No | Clear;32-90 F |  |  | 23-0056990 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1833235 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222952657444 | 20230404 | 1432 | 20230404 | 1513 | 2080091 | 41 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 41 | 39.2397 | -120.9589 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0057143 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1833270 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 4209 | 20230404 | 1642 | 20230405 | 629 | 2080216 | 827 | Distribution Circuit | Equipment Failure/Involved | Underground | 169 | 28760 | 38.8731 | -121.0803 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0057197 | UG | Sus | 45715724 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1833286 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | OTHER | J738 TWD T1507 | 20230404 | 2253 | 20230405 | 117 | 2080333 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2880 | 39.0934 | -120.9518 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0057117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833322 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 98319 | 20230404 | 2314 | 20230405 | 210 | 2080337 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 19712 | 38.9311 | -121.0956 | No | Clear;32-90 F |  |  | 23-0057242 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833327 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223205238277 | 20230405 | 839 | 20230405 | 1204 | 2080531 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 205 | 38.7121 | -120.8772 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0057499 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1833507 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 5655 | 20230405 | 1044 | 20230405 | 1336 | 2080712 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 5504 | 38.7977 | -120.7123 | No | Clear;32-90 F |  |  | 23-0057587 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833532 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7065 | 20230405 | 1340 | 20230405 | 1428 | 2080906 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 2448 | 39.1869 | -120.9556 | No | Clear;32-90 F | Insulator | Broken | 23-0057582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833529 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 2414 | 20230405 | 2316 | 20230405 | 2324 | 2081225 | 8 | Distribution Circuit | 3rd Party | Vehicle | 405 | 3240 | 38.9663 | -121.0352 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0057737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833599 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 6077 | 20230406 | 510 | 20230406 | 748 | 2081314 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2370 | 38.8105 | -121.1644 | No | Clear;32-90 F |  |  | 23-0057764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833633 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2173 | 20230406 | 652 | 20230406 | 908 | 2081346 | 136 | Distribution Circuit | Animal | Bird found | 55 | 7480 | 38.6947 | -120.7187 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0057860 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833765 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223480338519 | 20230406 | 815 | 20230406 | 1256 | 2081399 | 281 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 281 | 38.7181 | -120.7821 | No | Clear;32-90 F |  |  | 23-0057907 | OH | Sus | 45717482 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1833798 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7737 | 20230406 | 910 | 20230406 | 1149 | 2081517 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 3021 | 38.9993 | -121.2622 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0057837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | Yes | No | 1833723 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31783 | 20230406 | 1135 | 20230406 | 1415 | 2081753 | 160 | Distribution Circuit | Vegetation | Other ground vegetation | 2 | 320 | 39.2602 | -120.9472 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0057957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833805 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 2387 | 20230406 | 1802 | 20230406 | 1954 | 2082097 | 112 | Distribution Circuit | Animal | Bird found | 19 | 2128 | 39.0279 | -121.2938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1833878 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223313545276 | 20230406 | 1857 | 20230407 | 1040 | 2082123 | 943 | Transformer only | Vegetation | Tree - fell into line | 3 | 2829 | 38.9036 | -120.837 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0058267 | OH | Sus | 35436639 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833954 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | JUMPER | SWITCH 318339 | 20230406 | 1914 | 20230406 | 1936 | 2082146 | 22 | Distribution Circuit | Company Initiated | Improper Construction | 95 | 2090 | 38.9221 | -121.0719 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 23-0018267 | OH | Sus | 35404916 | NORTH VALLEY AND SIERRA | APR | Open Circuit | 0 | No | No | No | 1833871 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9393 | 20230406 | 2217 | 20230407 | 1021 | 2082187 | 724 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 8688 | 38.9086 | -120.8486 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058272 | OH | Sus | 45717993 | NORTH VALLEY AND SIERRA | APR | Open Circuit | 0 | No | Yes | Yes | 1833959 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224580459982 | 20230407 | 1055 | 20230407 | 1619 | 2082594 | 324 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 972 | 39.3025 | -120.3824 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0058659 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834113 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222956652495 | 20230407 | 1632 | 20230407 | 1734 | 2082834 | 62 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 62 | 39.1031 | -120.9594 | No | Overcast;32-90 F |  |  | 23-0058671 | OH | Sus | 31641662 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834117 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222375642137 | 20230407 | 1804 | 20230407 | 2129 | 2082846 | 205 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 410 | 38.8208 | -121.1675 | No | Overcast;32-90 F | Secondary | Broken | 23-0058684 | OH | Sus | 45719343 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834122 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRIP-SAVER | 2679 | 20230407 | 2016 | 20230408 | 36 | 2082878 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 15748 | 38.7074 | -120.9708 | No | Overcast;32-90 F | Jumper | Broken | 23-0058695 | OH | Sus | 45719248 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834132 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | SUMMIT-1101 | 152591101 | JUMPER | OJ TWD CGC 224566859814 | 20230408 | 817 | 20230408 | 1610 | 2083081 | 473 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 2838 | 39.2981 | -120.3871 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0058741 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834187 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222050249423 | 20230408 | 1053 | 20230408 | 1733 | 2083182 | 400 | Transformer only | Animal | Bird found | 2 | 800 | 39.0217 | -121.2793 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058779 | OH | Sus | 35436936 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1834235 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222560550959 | 20230408 | 1330 | 20230408 | 1936 | 2083271 | 366 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 366 | 39.0621 | -121.099 | No | Partly Cloudy;32-90 F |  |  | 23-0058794 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834247 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223311138030 | 20230408 | 1657 | 20230408 | 2134 | 2083357 | 277 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 554 | 38.7052 | -120.8409 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1834255 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222987556615 | 20230408 | 1919 | 20230408 | 2045 | 2083413 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 39.2165 | -120.9469 | No | Clear;32-90 F |  |  | 23-0058814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834266 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 51696 | 20230409 | 1038 | 20230409 | 1812 | 2083631 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 991 | 114388 | 39.1003 | -120.9524 | No | Clear;32-90 F | Insulator | Broken | 23-0058864 | OH | Sus | 31641760 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834313 | 0 | EPSS Ckt | N | 2023 | B-C
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222537551059 | 20230409 | 1334 | 20230409 | 2230 | 2083701 | 536 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 536 | 39.0648 | -121.1076 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0058882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1834330 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 31575 | 20230410 | 639 | 20230410 | 807 | 2084077 | 88 | Distribution Circuit | Animal | Bird found | 4 | 352 | 38.8107 | -121.1861 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834404 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 21719 | 20230410 | 715 | 20230410 | 835 | 2084060 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 400 | 38.7701 | -120.8578 | No | Clear;32-90 F |  |  | 23-0059010 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834471 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3365 | 20230410 | 835 | 20230410 | 1045 | 2084162 | 130 | Distribution Circuit | Animal | Squirrel | 16 | 2081 | 38.7245 | -121.1752 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0059076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1834538 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | HIGGINS-1109 | 152691109 | FUSE | 30583 | 20230410 | 950 | 20230410 | 1323 | 2084206 | 213 | Distribution Circuit | 3rd Party | Vehicle | 2 | 426 | 39.0059 | -121.1063 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0059004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834466 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21411 | 20230410 | 1116 | 20230410 | 2215 | 2084431 | 659 | Distribution Circuit | 3rd Party | Vehicle | 17 | 11203 | 38.7165 | -120.623 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0059137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834578 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230410 | 1424 | 20230410 | 1444 | 2084632 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 840 | 38.8458 | -121.482 | No | Clear;32-90 F | Insulator | Broken | 23-0059195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834594 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4345 | 20230410 | 1511 | 20230410 | 1757 | 2084677 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 8134 | 39.2114 | -121.2015 | No | Clear;32-90 F |  |  | 23-0059257 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834622 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9493 | 20230410 | 1800 | 20230410 | 1845 | 2084830 | 45 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 900 | 39.1867 | -120.9467 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0059274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834634 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR 2110 | 152582110 | FUSE | 2489 | 20230410 | 1912 | 20230411 | 1154 | 2084858 | 1002 | Distribution Circuit | Equipment Failure/Involved | Underground | 21 | 20687 | 38.8229 | -121.2558 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0059304 | UG | Sus | 35437224 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1834646 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ'S 1/S/OF CGC#222980856721 | 20230410 | 2222 | 20230411 | 31 | 2084931 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 4119 | 39.2194 | -120.9489 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0059325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834653 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 6661 | 20230411 | 833 | 20230411 | 1023 | 2085165 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 170 | 18700 | 38.5891 | -120.8464 | No | Clear;32-90 F |  |  | 23-0059507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834851 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 9931 | 20230412 | 156 | 20230412 | 942 | 2086102 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6524 | 39.1035 | -121.1093 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0059852 | OH | Sus | 45726955 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | Yes | No | 1835014 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | T2035 | 20230412 | 825 | 20230412 | 1343 | 2086287 | 318 | Transformer only | Company Initiated | Other Circuits | 2 | 636 | 38.6882 | -120.801 | No | Partly Cloudy;32-90 F | Transformer | Normal | 23-0060001 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1835163 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33097 | 20230412 | 1332 | 20230412 | 1737 | 2086761 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 490 | 39.2451 | -121.0287 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0060213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835248 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 67415 | 20230413 | 259 | 20230413 | 616 | 2087191 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2955 | 38.883 | -120.8795 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0060450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1835357 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | JUMPER | OJ'S 2 SPANS SS OF CGC 224573260151 | 20230413 | 708 | 20230413 | 1509 | 2087265 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 17316 | 39.3067 | -120.3848 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0060477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835371 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 36327 | 20230413 | 1047 | 20230413 | 1421 | 2087539 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1284 | 39.155 | -121.1877 | No | Clear;32-90 F | Insulator | Broken | 23-0060613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835549 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222321039439 | 20230413 | 1113 | 20230413 | 1447 | 2087736 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 214 | 38.7468 | -121.1872 | No | Clear;32-90 F | Transformer | Broken | 23-0060689 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835573 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20230413 | 2115 | 20230414 | 437 | 2088098 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 608 | 63133 | 39.5596 | -120.8241 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0060891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835641 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4333 | 20230414 | 331 | 20230414 | 442 | 2088217 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 1633 | 39.2347 | -121.1072 | No | Clear;32-90 F |  |  | 23-0060944 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1835700 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5747 | 20230414 | 619 | 20230414 | 802 | 2088232 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1339 | 38.957 | -121.0486 | No | Clear;32-90 F |  |  | 23-0060971 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1835714 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20230414 | 621 | 20230414 | 915 | 2088234 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 13920 | 38.6542 | -121.0356 | No | Clear;32-90 F |  |  | 23-0061058 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1835826 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 38311 | 20230414 | 1039 | 20230414 | 1212 | 2088557 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1860 | 38.897 | -121.433 | No | Clear;32-90 F |  |  | 23-0061146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1835881 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 875 | 20230414 | 1115 | 20230414 | 1201 | 2088609 | 46 | Distribution Circuit | Company Initiated | Return Circuit Normal | 591 | 16660 | 39.5634 | -120.6434 | No | Clear;32-90 F | Generator | Normal | 23-0060891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1835890 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2715 | 20230414 | 1158 | 20230414 | 1335 | 2088649 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 224 | 21728 | 39.3081 | -120.9463 | No | Clear;32-90 F | Insulator | Broken | 23-0061143 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835879 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 10249 | 20230414 | 1256 | 20230414 | 1735 | 2088883 | 279 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 279 | 38.7545 | -120.7332 | No | Clear;32-90 F |  |  | 23-0061266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1835924 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222601856505 | 20230414 | 1524 | 20230415 | 30 | 2088837 | 546 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 546 | 39.2147 | -121.0828 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0061265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1835922 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | TRANSFORMER | 222607144806 | 20230414 | 1730 | 20230415 | 539 | 2088844 | 729 | Transformer only | Equipment Failure/Involved | Underground | 4 | 2916 | 38.8935 | -121.0848 | No | Clear;32-90 F | Secondary | Burned Open | 23-0061264 | UG | Sus | 45730764 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835921 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | SWITCH | 50103 | 20230415 | 250 | 20230415 | 1225 | 2089015 | 575 | Distribution Circuit | 3rd Party | Vehicle | 127 | 8646 | 39.045 | -121.0762 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0061297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1835953 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5303 | 20230415 | 1027 | 20230415 | 1325 | 2089209 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 5518 | 38.9009 | -121.1287 | No | Clear;32-90 F |  |  | 23-0061350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1836041 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7057 | 20230415 | 1245 | 20230415 | 1509 | 2089255 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 4896 | 39.1912 | -120.9774 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0061355 | OH | Sus | 45730929 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836042 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32927 | 20230415 | 2137 | 20230416 | 1301 | 2089452 | 924 | Distribution Circuit | 3rd Party | Vehicle | 10 | 9240 | 39.2544 | -121.1983 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0061417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1836107 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 2641 | 20230416 | 622 | 20230416 | 805 | 2089542 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1751 | 38.7609 | -120.8588 | No | Clear;32-90 F |  |  | 23-0061437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1836135 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 9777 | 20230416 | 921 | 20230416 | 1110 | 2089610 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2834 | 39.0603 | -121.1098 | No | Clear;32-90 F |  |  | 23-0061452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1836156 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223001541700 | 20230416 | 1907 | 20230416 | 2012 | 2089749 | 65 | Transformer only | Equipment Failure/Involved | Underground | 3 | 195 | 38.8069 | -120.9486 | No | Clear;32-90 F | Connector or Splice (UG) | Burned/flashed | 23-0061501 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1836190 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3841 | 20230416 | 2146 | 20230416 | 2237 | 2089838 | 51 | Distribution Circuit | 3rd Party | Vehicle | 83 | 4233 | 39.1277 | -120.9168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0061503 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836193 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 8283 | 20230416 | 2338 | 20230417 | 116 | 2089901 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 3724 | 38.9063 | -121.1501 | No | Clear;32-90 F |  |  | 23-0061523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1836215 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224519560930 | 20230417 | 733 | 20230418 | 642 | 2089995 | 1389 | Transformer only | Environmental/External | Ice or snow | 1 | 1389 | 39.3286 | -120.4036 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0061704 | OH | Sus | 45732766 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1836442 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ'S 1 POLE N/OF CGC 222871748284 | 20230417 | 1019 | 20230417 | 1331 | 2090292 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 768 | 38.9881 | -120.9907 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0061604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836386 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7101 | 20230417 | 1033 | 20230417 | 1422 | 2090238 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 40409 | 39.2691 | -121.0572 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0061623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836399 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 18157 | 20230417 | 1556 | 20230417 | 1650 | 2090716 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 62 | 38.7789 | -120.2557 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0061761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836483 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | OJ TWD CGC 222743956029 | 20230417 | 1635 | 20230417 | 1815 | 2090728 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 100 | 39.2019 | -121.033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0061790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836484 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223664435265 | 20230417 | 1713 | 20230417 | 2258 | 2090887 | 345 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 345 | 38.6271 | -120.7183 | No | Clear;32-90 F | Fuse | Burned Open | 23-0061855 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1836532 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20230418 | 247 | 20230418 | 1305 | 2090983 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 705 | 175848 | 38.773 | -120.2933 | No | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0061861 | OH | Sus | 35438503 | NORTH VALLEY AND SIERRA | APR | Multi-Fault | 0 | No | Yes | No | 1836539 | 0 | EPSS Ckt | N | 2023 | A+C+GRD
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | OJ 2 E/OF CGC 222676148908 | 20230418 | 1124 | 20230418 | 1519 | 2091484 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 470 | 39.0052 | -121.058 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0062034 | OH | Sus | 31642572 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | Yes | No | 1836730 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7289 | 20230418 | 1203 | 20230418 | 1324 | 2091517 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 648 | 39.233 | -121.1167 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 23-0062056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836738 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 992864 | 20230418 | 1302 | 20230418 | 1322 | 2091561 | 20 | Distribution Circuit | Company Initiated | Return Circuit Normal | 387 | 7740 | 38.8042 | -120.1031 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0061861 | OH | Sus | 35438503 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836755 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222505045320 | 20230418 | 1519 | 20230419 | 159 | 2091697 | 640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1884 | 38.9077 | -121.1206 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0062232 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1836793 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 6717 | 20230418 | 1715 | 20230418 | 1852 | 2091776 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 194 | 38.7237 | -120.7297 | No | Clear;32-90 F |  |  | 23-0062243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1836799 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 98319 | 20230419 | 612 | 20230419 | 1512 | 2091977 | 540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 60480 | 38.9311 | -121.0956 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0062331 | OH | Sus | 45735594 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | Yes | No | 1836851 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | OCB | 1105/2 | 20230419 | 824 | 20230419 | 928 | 2092191 | 64 | Distribution Circuit | Equipment Failure/Involved | Substation | 3807 | 243648 | 38.6933 | -120.8261 | No | Clear;32-90 F | Relay | Malfunctioning | 23-0012114 | OH | Sus | 31614770 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1836926 | 0 | EPSS Ckt | N | 2023 | GRD INST
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222904054549 | 20230419 | 1029 | 20230419 | 1924 | 2092520 | 535 | Transformer only | Animal | Squirrel | 3 | 1605 | 39.1602 | -120.9774 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0062469 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837041 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 20230419 | 1148 | 20230419 | 1346 | 2092531 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1534 | 39.2097 | -120.9435 | No | Overcast;32-90 F | Conductor- Overhead | Deteriorated | 23-0062452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837034 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9821 | 20230419 | 1811 | 20230419 | 2008 | 2092776 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 175 | 20475 | 39.3088 | -120.9318 | No | Clear;32-90 F |  |  | 23-0062714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837094 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | T1171 | 20230420 | 852 | 20230420 | 1138 | 2093002 | 166 | Transformer only | 3rd Party | Customer Equipment | 14 | 2324 | 39.1881 | -121.1817 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0062839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1837189 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4345 | 20230420 | 1019 | 20230421 | 119 | 2093078 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 9457 | 39.2114 | -121.2015 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0062957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837252 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6647 | 20230421 | 1210 | 20230421 | 1820 | 2093911 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 19240 | 39.3066 | -120.3821 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0063497 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837551 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7927 | 20230421 | 1312 | 20230423 | 1401 | 2093820 | 2929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 70296 | 39.6219 | -120.522 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837571 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 8975 | 20230421 | 1428 | 20230421 | 1637 | 2094045 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 14898 | 38.8049 | -120.1402 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0063581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837581 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222559752074 | 20230421 | 1433 | 20230421 | 1440 | 2094014 | 7 | Transformer only | Animal | Squirrel | 1 | 7 | 39.0933 | -121.0996 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0063590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837585 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 2679 | 20230421 | 1505 | 20230421 | 1621 | 2094048 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 507 | 38.9153 | -121.4513 | No | Clear;32-90 F |  |  | 23-0063608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837592 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6257 | 20230421 | 1508 | 20230422 | 1306 | 2094081 | 1318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1318 | 39.0667 | -120.7695 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0063599 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837588 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5385 | 20230422 | 506 | 20230422 | 1422 | 2094407 | 556 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 13900 | 38.9478 | -121.197 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0063711 | OH | Sus | 45738731 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1837684 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18523 | 20230422 | 637 | 20230422 | 919 | 2094427 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 13446 | 38.7478 | -121.0596 | No | Clear;32-90 F |  |  | 23-0063736 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1837743 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38445 | 20230422 | 752 | 20230422 | 1805 | 2094483 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 613 | 38.7968 | -121.1332 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0063732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR |  | 0 | No | No | No | 1837734 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8243 | 20230422 | 804 | 20230422 | 1506 | 2094469 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2532 | 39.2147 | -120.9953 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0063735 | OH | Sus | 45738603 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837739 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20230423 | 610 | 20230423 | 924 | 2094913 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 15520 | 38.6542 | -121.0356 | No | Clear;32-90 F |  |  | 23-0063819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1837847 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 938135 | 20230423 | 708 | 20230423 | 934 | 2094938 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4672 | 38.9 | -121.2193 | No | Clear;32-90 F |  |  | 23-0063830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1837863 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 83159 | 20230423 | 1016 | 20230423 | 1142 | s1837868 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 86 | 39.3045 | -120.3913 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0063839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837868 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 890670 | 20230423 | 1813 | 20230423 | 1821 | 2095144 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2705 | 21640 | 39.0196 | -120.8298 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0020909 | OH | Sus | 45203860 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837898 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 88079 | 20230423 | 2016 | 20230423 | 2135 | 2095187 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 316 | 38.9115 | -121.1635 | No | Clear;32-90 F |  |  | 23-0063885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1837908 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | SWITCH | 6665 | 20230424 | 751 | 20230424 | 1328 | 2095329 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 27297 | 39.3223 | -120.381 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0063947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837963 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | JUMPER | OJ @ LINE BUCK TWDS CGC #223568040280 | 20230424 | 921 | 20230424 | 1403 | 2095523 | 282 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 282 | 38.7668 | -120.7485 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0064001 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838080 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224137735362 | 20230424 | 921 | 20230424 | 1219 | 2095518 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 356 | 38.6288 | -120.5523 | No | Clear;32-90 F | Fuse | Broken | 23-0064112 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1838147 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3377 | 20230424 | 1010 | 20230424 | 1257 | 2095581 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 174 | 29058 | 38.9439 | -120.7215 | No | Clear;32-90 F |  |  | 23-0064069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1838123 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | JUMPER | 3 SP NW OF CGC 222267458572 | 20230424 | 1109 | 20230424 | 1244 | 2095627 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 95 | 39.2721 | -121.2011 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0064050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838115 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224429560576 | 20230424 | 1428 | 20230424 | 2023 | 2095657 | 355 | Transformer only | Environmental/External | Ice or snow | 8 | 2840 | 39.3192 | -120.4356 | No | Heavy Rain-Clear;32-90 F | Transformer | Broken | 23-0064169 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838166 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221960048210 | 20230425 | 910 | 20230425 | 1025 | 2096424 | 75 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 75 | 38.9883 | -121.3118 | No | Clear;32-90 F |  |  | 23-0064434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1838402 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224088239255 | 20230425 | 1107 | 20230425 | 1149 | 2096581 | 42 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 42 | 38.7357 | -120.5678 | No | Clear;32-90 F |  |  | 23-0064494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1838425 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222703239303 | 20230425 | 1325 | 20230425 | 1731 | 2096744 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 38.7426 | -121.0528 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0064574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1838460 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9279 | 20230425 | 1405 | 20230425 | 1457 | 2096810 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1092 | 38.9451 | -120.9136 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0064583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838463 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6129 | 20230425 | 1746 | 20230425 | 2045 | 2096982 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 19332 | 38.9854 | -121.0048 | No | Clear;32-90 F |  |  | 23-0064704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1838507 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 34523 | 20230426 | 1535 | 20230426 | 2052 | 2097731 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3487 | 39.0131 | -121.0302 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838789 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 19910 | 20230426 | 1616 | 20230426 | 1810 | 2097752 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 610 | 38588 | 38.6313 | -120.8542 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0065155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1838793 | 0 | EPSS Ckt | N | 2023 | A-GRD
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223267942569 | 20230426 | 1811 | 20230426 | 2112 | 2097824 | 181 | Transformer only | Vegetation | Tree - fell into line | 2 | 362 | 38.83 | -120.8538 | No | Clear;32-90 F | Transformer | Broken | 23-0065215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1838815 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15473 | 20230426 | 1835 | 20230426 | 1912 | 2097825 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 481 | 38.9617 | -121.3599 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0065197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838804 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5325 | 20230426 | 1903 | 20230426 | 2334 | 2097844 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 12737 | 38.9488 | -121.2191 | No | Clear;32-90 F |  |  | 23-0065264 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1838838 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | JUMPER | OJS 2 SPANS S/OF CGC 222943351499 | 20230427 | 1207 | 20230427 | 1304 | 2098401 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 57 | 39.0749 | -120.9632 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839026 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20230427 | 1221 | 20230427 | 1520 | 2098469 | 179 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 356 | 57084 | 39.1444 | -120.908 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1839038 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4289 | 20230427 | 1945 | 20230428 | 722 | 2098848 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 15334 | 39.2328 | -121.1692 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839120 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 38127 | 20230428 | 850 | 20230428 | 1400 | 2099156 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 7130 | 39.3025 | -120.3834 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0065931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839274 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | SWITCH | 467046 | 20230428 | 1139 | 20230428 | 1203 | 2099338 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1751 | 42024 | 38.7005 | -120.8485 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0066030 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839322 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222296042049 | 20230428 | 1305 | 20230428 | 1414 | 2099349 | 69 | Transformer only | 3rd Party | Customer Equipment | 14 | 966 | 38.8183 | -121.195 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0066107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839348 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 20230428 | 1323 | 20230428 | 1440 | 2099306 | 77 | Distribution Circuit | Vegetation | Tree - grew into line | 11 | 847 | 38.8791 | -120.8335 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066103 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839347 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9523 | 20230428 | 1521 | 20230428 | 1633 | 2099533 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 144 | 38.8788 | -121.4144 | No | Clear;32-90 F |  |  | 23-0066148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1839361 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222779657303 | 20230428 | 1551 | 20230428 | 2201 | 2099558 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2220 | 39.2359 | -121.0198 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0066146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839360 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223255737284 | 20230428 | 1632 | 20230428 | 2245 | 2099596 | 373 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 746 | 38.6855 | -120.8609 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839363 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222368456335 | 20230428 | 2120 | 20230429 | 35 | 2099749 | 195 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 975 | 39.2107 | -121.1657 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839412 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 938135 | 20230429 | 107 | 20230429 | 1226 | 2099782 | 679 | Distribution Circuit | 3rd Party | Vehicle | 32 | 21728 | 38.9 | -121.2193 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0066222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1839421 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20230429 | 546 | 20230429 | 1258 | 2099844 | 432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3051 | 1312076 | 38.8328 | -120.8176 | No | Partly Cloudy;32-90 F |  |  | 23-0066227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1839427 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221501544851 | 20230429 | 906 | 20230429 | 1441 | 2099969 | 335 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 335 | 38.8968 | -121.4736 | No | Partly Cloudy;32-90 F |  |  | 23-0066308 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839530 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | TRANSFORMER | T0991 | 20230429 | 931 | 20230429 | 1628 | 2099990 | 417 | Distribution Circuit | Equipment Failure/Involved | Underground | 94 | 13590 | 38.9131 | -121.0649 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0066291 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839527 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223698835550 | 20230429 | 1210 | 20230429 | 1944 | 2100037 | 454 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 454 | 38.6344 | -120.7061 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066296 | OH | Sus | 35440582 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839518 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222711046059 | 20230429 | 1654 | 20230429 | 2318 | 2100198 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 4224 | 38.9273 | -121.0482 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0066328 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839548 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20230429 | 2009 | 20230430 | 1042 | 2100253 | 873 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1530 | 284213 | 38.9052 | -120.8374 | No | Clear;32-90 F |  |  | 23-0066339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1839555 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19732 | 20230501 | 2 | 20230501 | 9 | 2101007 | 7 | Distribution Circuit | 3rd Party | Metallic Balloon | 1206 | 8442 | 38.7367 | -120.784 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066510 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1839720 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223500639914 | 20230501 | 117 | 20230501 | 341 | 2101012 | 144 | Transformer only | 3rd Party | Metallic Balloon | 5 | 720 | 38.7561 | -120.7733 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0066518 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1839728 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | FUSE | 1769 | 20230501 | 344 | 20230501 | 543 | 2101077 | 119 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 104 | 12376 | 38.7998 | -121.2621 | No | Overcast;32-90 F |  |  | 23-0066524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1839732 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 4679 | 20230501 | 744 | 20230501 | 839 | 2101181 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 2695 | 38.9276 | -121.0786 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0066577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1839801 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | 1 SPAN SS OF CGC 223968335265 | 20230501 | 1144 | 20230501 | 1610 | 2101574 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 266 | 38.6275 | -120.6115 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1839901 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 30123 | 20230501 | 1334 | 20230501 | 1342 | 2101623 | 8 | Distribution Circuit | Animal | Squirrel | 2 | 16 | 39.0368 | -120.9784 | No | Overcast;32-90 F | Fuse | Normal | 23-0066715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1839919 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 36483 | 20230501 | 1335 | 20230501 | 1512 | 2101671 | 97 | Distribution Circuit | Animal | Bird found | 4 | 388 | 38.8524 | -121.1693 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0066764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1839938 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222972557560 | 20230501 | 1832 | 20230502 | 243 | 2101941 | 491 | Transformer only | Animal | Squirrel | 1 | 491 | 39.2421 | -120.9521 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1839968 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20230501 | 2031 | 20230501 | 2211 | 2101979 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2000 | 38.8769 | -121.017 | No | Overcast;32-90 F |  |  | 23-0066846 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1839979 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9031 | 20230502 | 620 | 20230502 | 759 | 2102122 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 2673 | 39.2198 | -121.0125 | No | Overcast-Fog-Drizzle;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0066909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840032 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5747 | 20230502 | 721 | 20230502 | 1004 | 2102166 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2119 | 38.957 | -121.0486 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0067037 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1840169 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 35713 | 20230502 | 746 | 20230502 | 1025 | 2102178 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 636 | 38.975 | -121.1367 | No | Partly Cloudy-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0067034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840167 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20489 | 20230502 | 921 | 20230502 | 1344 | 2102640 | 263 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 3 | 481 | 38.7587 | -120.9089 | No | Partly Cloudy-Fog;32-90 F | Secondary | Broken | 23-0067086 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1840189 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | TRANSFORMER | 222964536147 | 20230502 | 1034 | 20230502 | 1112 | 2102567 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 38 | 38.6555 | -120.9611 | No | Clear;32-90 F | Connector or Splice (OH) | Normal | 23-0067093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840193 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | FUSE | 1769 | 20230502 | 1151 | 20230502 | 1847 | 2102740 | 416 | Distribution Circuit | Equipment Failure/Involved | Underground | 104 | 29256 | 38.7998 | -121.2621 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0067158 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1840216 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230502 | 1518 | 20230502 | 1531 | 2103037 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 2596 | 39.2562 | -120.7669 | No | Overcast-Fog;32-90 F |  |  | 23-0067309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1840251 | 0 | EPSS Ckt | N | 2023 | ABOVE MTT
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2216 | 20230502 | 1638 | 20230502 | 1659 | 2103101 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1001 | 21021 | 39.1999 | -121.1727 | No | Partly Cloudy;32-90 F |  |  | 23-0067342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840262 | 0 | EPSS Ckt | N | 2023 | B- GRD
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7595 | 20230502 | 1715 | 20230502 | 1858 | 2103141 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 309 | 38.8243 | -121.45 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0067371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Three Phase Fault | 0 | No | No | No | 1840279 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 17361 | 20230502 | 2029 | 20230502 | 2204 | 2103237 | 95 | Distribution Circuit | Animal | Bird found | 19 | 1838 | 39.0051 | -121.34 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0067399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840290 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223764339378 | 20230503 | 959 | 20230503 | 1800 | 2103589 | 481 | Transformer only | Environmental/External | Lightning | 1 | 481 | 38.7403 | -120.6813 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067586 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840474 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20230503 | 1025 | 20230503 | 1420 | 2103618 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 13160 | 39.3203 | -120.4331 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0067596 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840479 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223765239697 | 20230503 | 1136 | 20230503 | 1945 | 2103725 | 489 | Transformer only | Environmental/External | Lightning | 2 | 978 | 38.7491 | -120.6806 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840536 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33773 | 20230503 | 1154 | 20230503 | 1831 | 2103697 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 18262 | 39.1339 | -121.0183 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0067644 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840506 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223123454254 | 20230503 | 1251 | 20230503 | 1932 | 2103788 | 401 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 802 | 39.1511 | -120.8999 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0067803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840569 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230503 | 1417 | 20230503 | 1430 | 2103933 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 2606 | 39.2562 | -120.7669 | No | Overcast-Fog;Below 32 F |  |  | 23-0067756 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840552 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223809034636 | 20230504 | 822 | 20230504 | 928 | 2104363 | 66 | Transformer only | Animal | Bird found | 1 | 66 | 38.6102 | -120.6697 | No | Overcast-Fog;32-90 F | Transformer (OH) |  | 23-0068055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840788 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | JUMPER | TSB 1 S/OF FUCO 6641 | 20230504 | 903 | 20230504 | 1322 | 2104668 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 10985 | 39.2994 | -120.3785 | No | Overcast-Snow;32-90 F | Pole-Wood | Broken | 23-0067968 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840823 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1449 | 20230504 | 948 | 20230504 | 1258 | 2104623 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 13680 | 38.7543 | -120.7732 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Deteriorated | 23-0068087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840817 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | T4371 | 20230504 | 1207 | 20230504 | 1215 | 2104772 | 8 | Transformer only | Company Initiated | Other Circuits | 5 | 40 | 38.6637 | -120.947 | No | Overcast;32-90 F | Secondary | Normal | 23-0068196 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840854 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222285657007 | 20230504 | 1831 | 20230504 | 1905 | 2105033 | 34 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 272 | 39.2296 | -121.1942 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 23-0068477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840939 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 20230504 | 1832 | 20230505 | 242 | 2104938 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 12740 | 39.4382 | -120.9965 | No | Overcast;32-90 F | Insulator | Broken | 23-0068463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840932 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222289143078 | 20230505 | 739 | 20230505 | 1236 | 2105232 | 297 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 297 | 38.8468 | -121.1975 | No | Overcast;32-90 F | Transformer | Broken | 23-0068634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841094 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7007 | 20230505 | 823 | 20230505 | 951 | 2105284 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2024 | 39.2127 | -120.9877 | No | Overcast-Fog;32-90 F |  |  | 23-0068663 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841127 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 36764 | 20230505 | 940 | 20230505 | 1231 | 2105400 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 9405 | 38.787 | -120.206 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0068616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841125 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20230505 | 1122 | 20230505 | 1146 | 2105516 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1010 | 12449 | 38.6635 | -120.9306 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0068630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841159 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | SWITCH | 18640 | 20230505 | 1313 | 20230505 | 1323 | 2105642 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 103 | 1030 | 38.6604 | -120.925 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0068630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841190 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 31923 | 20230505 | 1359 | 20230510 | 1601 | 2105663 | 7322 | Distribution Circuit | Environmental/External | Ice or snow | 26 | 190372 | 39.622 | -120.6131 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0068896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | Yes | No | 1841194 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223464139184 | 20230505 | 1722 | 20230505 | 1915 | 2105777 | 113 | Transformer only | Animal | Bird found | 3 | 339 | 38.7359 | -120.7865 | No | Partly Cloudy;32-90 F | Transformer (OH) |  | 23-0069031 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841229 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | 3 SS/OF 984459 | 20230505 | 1809 | 20230505 | 2317 | 2105784 | 308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 616 | 39.2596 | -120.9064 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0068992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841217 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 176535 | 20230505 | 2124 | 20230505 | 2147 | 2105857 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 253 | 38.7523 | -121.1969 | No | Overcast;32-90 F | Secondary | Together | 23-0069066 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841240 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7059 | 20230506 | 713 | 20230506 | 953 | 2105980 | 160 | Distribution Circuit | Animal | Bird found | 39 | 6240 | 39.1011 | -121.1524 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Normal | 23-0069120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841310 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3685 | 20230506 | 1109 | 20230506 | 2120 | 2106148 | 611 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1833 | 39.2767 | -121.1943 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0069162 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1841361 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 92235 | 20230506 | 1205 | 20230506 | 1802 | 2106173 | 357 | Distribution Circuit | Environmental/External | Lightning | 6 | 827 | 38.9415 | -121.1631 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 23-0069165 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841365 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7513 | 20230506 | 1319 | 20230506 | 1530 | 2106257 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2358 | 38.7363 | -121.4399 | No | Partly Cloudy-Heavy Rain-Lightning;32-90 F |  |  | 23-0069198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Three Phase Fault | 0 | No | No | No | 1841392 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | TRANSFORMER | 222906635912 | 20230506 | 1734 | 20230507 | 22 | 2106388 | 408 | Transformer only | Environmental/External | Lightning | 1 | 408 | 38.6475 | -120.9826 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841416 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7721 | 20230506 | 1759 | 20230506 | 1902 | 2106395 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 315 | 39.0138 | -121.327 | No | Partly Cloudy;32-90 F |  |  | 23-0069221 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841410 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223500639914 | 20230506 | 2048 | 20230506 | 2319 | 2106463 | 151 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 755 | 38.7561 | -120.7733 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0069255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841443 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 6461 | 20230507 | 538 | 20230507 | 716 | 2106552 | 98 | Distribution Circuit | Animal | Bird found | 17 | 1700 | 38.9353 | -121.0644 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0069266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841455 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5775 | 20230507 | 804 | 20230507 | 947 | 2106637 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 5047 | 39.0212 | -121.1001 | No | Overcast;32-90 F |  |  | 23-0069274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841467 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6429 | 20230507 | 843 | 20230507 | 1045 | 2106652 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1586 | 39.2069 | -120.8114 | No | Overcast-Fog;32-90 F |  |  | 23-0069281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841479 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38661 | 20230507 | 1135 | 20230507 | 1228 | 2106771 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 106 | 38.8109 | -121.1543 | No | Clear;32-90 F |  |  | 23-0069290 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841487 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4353 | 20230507 | 1435 | 20230507 | 2004 | 2106864 | 329 | Distribution Circuit | 3rd Party | Vehicle | 2 | 658 | 39.2122 | -121.2012 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0069305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841501 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12615 | 20230507 | 1444 | 20230507 | 1629 | 2106833 | 105 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 7140 | 38.7994 | -120.7287 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0069306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841503 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221564839003 | 20230507 | 1540 | 20230508 | 1124 | 2106856 | 1184 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1184 | 38.7363 | -121.4525 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0069308 | OH | Sus | 35442024 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841505 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 1619 | 20230507 | 1657 | 20230507 | 1818 | 2106880 | 81 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 324 | 39.2874 | -120.9462 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0069302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841507 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5339 | 20230507 | 1708 | 20230507 | 1818 | 2106861 | 70 | Distribution Circuit | 3rd Party | Other | 15 | 1074 | 38.926 | -121.2318 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0069312 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841508 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7333 | 20230507 | 1857 | 20230507 | 1935 | 2106898 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 1102 | 39.2952 | -120.9686 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0069318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841511 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21979 | 20230507 | 1954 | 20230507 | 2205 | 2106944 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 655 | 38.7175 | -120.8799 | No | Clear;32-90 F |  |  | 23-0069336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1841531 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 2100 | 20230508 | 50 | 20230508 | 211 | 2107012 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1186 | 93201 | 38.6928 | -120.7666 | No | Clear;32-90 F |  |  | 23-0069371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841565 | 0 | EPSS Ckt | N | 2023 | SGF & GRD
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 38139 | 20230508 | 904 | 20230508 | 1250 | 2107142 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 7006 | 39.304 | -120.3902 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0069415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841608 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 20230508 | 1559 | 20230509 | 1401 | 2107994 | 1322 | Distribution Circuit | 3rd Party | Vehicle | 59 | 75086 | 39.2173 | -120.8092 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0069705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1841780 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 222656249632 | 20230508 | 2007 | 20230508 | 2039 | 2108084 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 64 | 39.0257 | -121.0655 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0069753 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841819 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | INTERRUPTER | 51684 | 20230508 | 2044 | 20230509 | 1454 | 2108152 | 1090 | Distribution Circuit | Equipment Failure/Involved | Underground | 1851 | 675936 | 38.7966 | -121.2921 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0069737 | UG | Sus | 35442358 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1841803 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 38125 | 20230509 | 924 | 20230509 | 1446 | 2108411 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 7084 | 39.2993 | -120.3803 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0069848 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1841917 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221550738910 | 20230509 | 1233 | 20230509 | 2216 | 2108593 | 583 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1166 | 38.7338 | -121.4576 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070029 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842035 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 223075358276 | 20230509 | 1445 | 20230509 | 1950 | 2108747 | 305 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 2135 | 39.2611 | -120.9153 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842054 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30167 | 20230509 | 2228 | 20230509 | 2302 | 2109049 | 34 | Distribution Circuit | Animal | Squirrel | 8 | 272 | 39.2211 | -121.0143 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 23-0070226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842120 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 36773 | 20230510 | 748 | 20230510 | 950 | 2109182 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 122 | 38.9121 | -121.1919 | No | Clear;32-90 F |  |  | 23-0070356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842283 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5247 | 20230510 | 946 | 20230510 | 1313 | 2109374 | 207 | Distribution Circuit | 3rd Party | Vehicle | 15 | 2026 | 38.853 | -121.1528 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0070396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842308 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 38131 | 20230510 | 946 | 20230510 | 1313 | 2109344 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 3726 | 39.3117 | -120.3826 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1842297 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222972557560 | 20230510 | 1117 | 20230510 | 1404 | 2109406 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 167 | 39.2421 | -120.9521 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0070377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1842299 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222608051800 | 20230510 | 1353 | 20230510 | 1947 | 2109637 | 354 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 708 | 39.0846 | -121.0853 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0070597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842354 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 10299 | 20230510 | 1521 | 20230510 | 1638 | 2109677 | 77 | Distribution Circuit | Animal | Squirrel | 2 | 154 | 38.7231 | -120.8322 | No | Clear;32-90 F | Pothead/Riser Termination | Normal | 23-0070614 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842355 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30447 | 20230511 | 400 | 20230511 | 1200 | 2109881 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 960 | 39.2144 | -120.9575 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842413 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | TRANSFORMER | T3133 | 20230511 | 901 | 20230511 | 1100 | 2110138 | 119 | Transformer only | Equipment Failure/Involved | Underground | 4 | 476 | 38.7319 | -120.7823 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0070871 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842564 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222651948723 | 20230511 | 1236 | 20230511 | 1719 | 2110397 | 283 | Transformer only | Vegetation | Tree - fell into line | 1 | 283 | 39.0006 | -121.0682 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0070988 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1842610 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | TRANSFORMER | T9820 | 20230511 | 1415 | 20230512 | 210 | 2110479 | 715 | Transformer only | Vegetation | Tree - fell into line | 2 | 1430 | 38.7057 | -121.0772 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0071108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1842646 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | RECLOSER | 8412 | 20230511 | 1614 | 20230511 | 2021 | 2110548 | 247 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 260 | 20136 | 38.7272 | -120.7379 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0071086 | OH | Sus | 45760047 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | Yes | Yes | 1842630 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222639561110 | 20230511 | 1751 | 20230512 | 241 | 2110621 | 530 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1590 | 39.3404 | -121.0672 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842673 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2695 | 20230511 | 1902 | 20230511 | 2026 | 2110668 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 5796 | 39.2949 | -120.9754 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0071020 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1842661 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | T5186 | 20230512 | 900 | 20230512 | 1219 | 2111053 | 199 | Transformer only | 3rd Party | Customer Equipment | 19 | 3781 | 39.1882 | -121.1826 | No | Clear;32-90 F | Secondary | Burned/flashed | 23-0071266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1842809 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 88399 | 20230512 | 927 | 20230512 | 1340 | 2110968 | 253 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 759 | 39.3089 | -120.3818 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071244 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1842777 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 5097 | 20230512 | 929 | 20230512 | 1034 | 2111122 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 4030 | 38.781 | -121.1735 | No | Clear;32-90 F |  |  | 23-0071318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842872 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223490536337 | 20230512 | 1212 | 20230512 | 1526 | 2111135 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 388 | 38.6589 | -120.7781 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0071376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842892 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20230513 | 849 | 20230513 | 1202 | 2111671 | 193 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 64483 | 39.2129 | -121.0129 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0071542 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842997 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20230513 | 1933 | 20230514 | 1044 | 2111950 | 911 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1080 | 37686 | 38.7607 | -120.505 | No | Clear;32-90 F | Insulator | Broken | 23-0071599 | OH | Sus | 45761602 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843048 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 4045 | 20230514 | 739 | 20230514 | 850 | 2112077 | 71 | Distribution Circuit | Animal | Squirrel | 17 | 1207 | 38.7609 | -121.192 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0071637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1843093 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223496234606 | 20230515 | 1125 | 20230515 | 1339 | 2113082 | 134 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 268 | 38.6108 | -120.7776 | No | Clear;32-90 F |  |  | 23-0071977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1843357 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 33683 | 20230515 | 1308 | 20230515 | 1443 | 2113192 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 3990 | 39.2464 | -121.0456 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0071939 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843342 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223204537442 | 20230515 | 1405 | 20230515 | 1458 | 2113267 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 53 | 38.6898 | -120.8778 | No | Clear;32-90 F | Jumper | Broken | 23-0071991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843367 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 16727 | 20230515 | 1733 | 20230516 | 115 | 2113440 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 462 | 38.8825 | -121.3775 | No | Clear;32-90 F | Insulator | Broken | 23-0072074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843408 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1037 | 20230515 | 1826 | 20230516 | 31 | 2113482 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 70080 | 38.7018 | -120.8451 | No | Clear;32-90 F |  |  | 23-0072117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1843438 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 35573 | 20230515 | 1927 | 20230515 | 2248 | 2113517 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 402 | 38.9159 | -121.2939 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072082 | OH | Sus | 31645408 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843411 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20230515 | 1942 | 20230516 | 247 | 2113479 | 425 | Distribution Circuit | 3rd Party | Vehicle | 71 | 30175 | 38.6943 | -120.6784 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843412 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 17361 | 20230515 | 1945 | 20230515 | 2133 | 2113528 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2089 | 39.0051 | -121.34 | No | Clear;32-90 F |  |  | 23-0072092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1843417 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4177 | 20230515 | 2110 | 20230516 | 23 | 2113584 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2509 | 39.2159 | -120.9505 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843421 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20230516 | 948 | 20230516 | 1900 | 2113994 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 355 | 48390 | 39.1444 | -120.908 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0072232 | OH | Sus | 31645419 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1843595 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222887062690 | 20230516 | 1013 | 20230516 | 1222 | 2114020 | 129 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 129 | 39.3835 | -120.9792 | No | Clear;32-90 F |  |  | 23-0072325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1843630 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221848749211 | 20230516 | 1407 | 20230516 | 1436 | 2114123 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 29 | 39.0161 | -121.3503 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0072392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1843659 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 2 N/OF OF CGC 222966656766 | 20230516 | 1455 | 20230516 | 1852 | 2114289 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 474 | 39.2214 | -120.9545 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843660 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | JUMPER | OJ S 3 N/ OF CGC 222652457112 | 20230516 | 1607 | 20230516 | 1807 | 2114333 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 120 | 39.2325 | -121.0647 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072427 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Three Phase Fault | 0 | No | No | No | 1843668 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | SWITCH | 7571 | 20230516 | 1830 | 20230516 | 1904 | 2114448 | 34 | Distribution Circuit | Company Initiated | Return Circuit Normal | 85 | 2890 | 38.6629 | -120.9838 | No | Clear;32-90 F | Other | Normal | 23-0060456 | OH | Sus | 35355019 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1843690 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223667241479 | 20230517 | 946 | 20230517 | 1159 | 2114920 | 133 | Transformer only | Vegetation | Tree - fell into line | 1 | 133 | 38.7983 | -120.7156 | No | Clear;32-90 F | Fuse | Burned Open | 23-0072697 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1843955 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1431 | 20230517 | 1117 | 20230517 | 1949 | 2114991 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8192 | 38.7464 | -120.7505 | No | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0072804 | OH | Sus | 45766248 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1843989 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 1 N/OF CGC 222982556776 | 20230517 | 1330 | 20230517 | 1459 | 2114965 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 890 | 39.2214 | -120.9486 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072663 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843938 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 10729 | 20230517 | 1453 | 20230517 | 1540 | 2115163 | 47 | Distribution Circuit | Company Initiated | Improper Construction | 140 | 6580 | 38.6903 | -121.0077 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0024321 | OH | Sus | 31609370 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843987 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7935 | 20230517 | 1543 | 20230519 | 0 | 2115207 | 1937 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 71669 | 39.6302 | -120.5447 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072892 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844026 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222660152394 | 20230517 | 1627 | 20230517 | 2329 | 2115241 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 422 | 39.1016 | -121.064 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844005 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | TRANSFORMER | 223253240438 | 20230518 | 129 | 20230518 | 500 | 2115501 | 211 | Transformer only | Vegetation | Tree - fell into line | 1 | 211 | 38.7713 | -120.8597 | No | Clear;32-90 F | Service conductor | Broken | 23-0072935 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844063 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 162438 | 20230518 | 556 | 20230518 | 1034 | 2115529 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 16402 | 38.9489 | -121.1628 | No | Clear;32-90 F |  |  | 23-0072983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844094 | 0 | EPSS Ckt | N | 2023 | A-B
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5613 | 20230518 | 932 | 20230518 | 1830 | 2115695 | 538 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 9556 | 38.9181 | -121.0537 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844192 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 836878 | 20230518 | 959 | 20230518 | 1958 | 2115958 | 599 | Distribution Circuit | Company Initiated | Coordination failure | 4863 | 2388135 | 38.7371 | -120.6759 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844174 | 0 | EPSS Ckt | Y | 2023 | DCD SGF
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33127 | 20230518 | 1230 | 20230518 | 1558 | 2116152 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 208 | 39.2591 | -121.0188 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0073114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844212 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4561 | 20230518 | 1633 | 20230518 | 1650 | 2116287 | 17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 68 | 39.2119 | -121.1933 | No | Clear;32-90 F |  |  | 23-0073241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844265 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222856255647 | 20230518 | 1645 | 20230519 | 140 | 2116359 | 535 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 535 | 39.1902 | -120.9934 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844271 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222274545523 | 20230518 | 1655 | 20230518 | 1810 | 2116384 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 75 | 38.9137 | -121.2028 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0073262 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844274 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221775245826 | 20230518 | 1952 | 20230518 | 2007 | 2116472 | 15 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 15 | 38.9233 | -121.377 | No | Clear;32-90 F |  |  | 23-0073278 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1844287 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221604439290 | 20230518 | 1955 | 20230519 | 1026 | 2116489 | 871 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 871 | 38.7442 | -121.439 | No | Clear;32-90 F |  |  | 23-0073288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1844297 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20230518 | 2027 | 20230519 | 13 | 2116498 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 12656 | 39.1731 | -120.9738 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 3099 | 20230518 | 2221 | 20230519 | 157 | 2116528 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1944 | 39.134 | -120.9401 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0073305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844314 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20230519 | 757 | 20230519 | 1203 | 2116734 | 246 | Distribution Circuit | Company Initiated | Coordination failure | 2004 | 346651 | 39.274 | -120.9698 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844371 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 6691 | 20230519 | 758 | 20230519 | 1310 | 2116637 | 312 | Distribution Circuit | Animal | Squirrel | 19 | 5827 | 39.0344 | -121.0978 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0073405 | OH | Sus | 31645912 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844393 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 3261 | 20230519 | 803 | 20230519 | 930 | 2116694 | 87 | Distribution Circuit | Animal | Squirrel | 3 | 261 | 39.2221 | -121.0568 | No | Clear;32-90 F | Fuse | Burned Open | 23-0073435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844462 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18417 | 20230519 | 1106 | 20230519 | 1211 | 2116969 | 65 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 21 | 1365 | 38.7652 | -120.5785 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0073529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844490 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 7591 | 20230519 | 1200 | 20230519 | 1329 | 2116934 | 89 | Distribution Circuit | 3rd Party | Metallic Balloon | 3 | 297 | 38.7362 | -121.4363 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844503 | 1 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230519 | 1229 | 20230519 | 1341 | 2117049 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2004 | 103608 | 39.2417 | -121.0264 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0073390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844514 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 23190 | 20230519 | 1437 | 20230519 | 1752 | 2117175 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2016 | 237455 | 38.7384 | -120.7798 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0073670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1844534 | 0 | EPSS Ckt | Y | 2023 | A C GRD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20230519 | 2332 | 20230520 | 920 | 2117380 | 588 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 592 | 148769 | 39.0443 | -120.9859 | No | Clear;32-90 F |  |  | 23-0073766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844595 | 0 | EPSS Ckt | Y | 2023 | A B INST
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 12955 | 20230520 | 917 | 20230520 | 1020 | 2117546 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 1386 | 38.7142 | -120.9107 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844663 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1102 | 153701102 | TRANSFORMER | 222010444638 | 20230520 | 1130 | 20230520 | 1430 | 2117597 | 180 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 1080 | 38.8901 | -121.2947 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073828 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844678 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222995553395 | 20230520 | 1132 | 20230520 | 1223 | 2117607 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 153 | 39.128 | -120.9454 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844681 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1102 | 152291102 | TRANSFORMER | 224129560238 | 20230520 | 1136 | 20230521 | 1225 | 2117609 | 1489 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 7445 | 39.3111 | -120.5407 | No | Clear;32-90 F | Other | Broken | 23-0073883 | OH | Sus | 31646142 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844715 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 30235 | 20230520 | 1232 | 20230520 | 1600 | 2117595 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 416 | 39.0355 | -120.9933 | No | Clear;32-90 F | Pothead/Riser Termination | Burned/flashed | 23-0073843 | OH | Sus | 31646055 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844691 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6257 | 20230520 | 1420 | 20230520 | 1609 | 2117628 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 109 | 39.0667 | -120.7695 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0073841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844689 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9537 | 20230520 | 1904 | 20230520 | 2110 | 2117779 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 252 | 38.8682 | -121.4239 | No | Clear;32-90 F |  |  | 23-0073909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844727 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9523 | 20230520 | 1906 | 20230520 | 2048 | 2117780 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 204 | 38.8788 | -121.4144 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0073907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844726 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 30475 | 20230521 | 756 | 20230521 | 851 | 2117946 | 55 | Distribution Circuit | Animal | Squirrel | 22 | 1210 | 38.8365 | -121.1918 | No | Clear;32-90 F | Fuse | Burned Open | 23-0073957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844783 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20230521 | 941 | 20230521 | 1512 | 2117960 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 592 | 95984 | 39.0443 | -120.9859 | No | Clear;32-90 F | Other | Broken | 23-0073959 | OH | Sus | 45770084 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844790 | 0 | EPSS Ckt | Y | 2023 | A-C INST
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222846158755 | 20230521 | 1451 | 20230521 | 2316 | 2118041 | 505 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1010 | 39.2758 | -120.995 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844828 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222367155794 | 20230521 | 2103 | 20230522 | 400 | 2118193 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 979 | 39.196 | -121.1662 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844862 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 6477 | 20230522 | 800 | 20230522 | 810 | 2118381 | 10 | Distribution Circuit | Animal | Squirrel | 3 | 30 | 39.0223 | -121.0622 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0074095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844917 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | SWITCH | 332 | 20230522 | 1149 | 20230522 | 1203 | 2118781 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 18 | 252 | 39.1982 | -121.0623 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0070170 | OH | Sus | 35315863 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845077 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | TSB 2 SPANS N/OF 4467 | 20230522 | 1253 | 20230522 | 2119 | 2118817 | 355 | Distribution Circuit | Company Initiated | Personnel- company | 467 | 13029 | 39.2003 | -121.0629 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0070170 | OH | Sus | 35315863 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845082 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224008039771 | 20230522 | 1923 | 20230523 | 55 | 2119004 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 664 | 38.75 | -120.598 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845134 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2619 | 20230522 | 2000 | 20230523 | 1323 | 2119135 | 1043 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 61537 | 38.8251 | -120.0372 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0074413 | OH | Sus | 45770986 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845136 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223876138504 | 20230522 | 2118 | 20230523 | 304 | 2119110 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 692 | 38.7165 | -120.6428 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845148 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9519 | 20230523 | 643 | 20230523 | 919 | 2119346 | 156 | Distribution Circuit | Animal | Bird found | 146 | 22776 | 38.7148 | -120.6676 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0074542 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1845266 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | FUSE | 36015 | 20230523 | 745 | 20230523 | 929 | 2119447 | 104 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 1468 | 59321 | 39.2161 | -121.0638 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0074519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845244 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7015 | 20230524 | 702 | 20230524 | 1051 | 2120220 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 10411 | 39.2244 | -121.0305 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0074962 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845478 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 2679 | 20230524 | 849 | 20230524 | 1059 | 2120360 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 867 | 38.9153 | -121.4513 | No | Clear;32-90 F |  |  | 23-0075034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845615 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2106 | 152582106 | FUSE | 30111 | 20230524 | 1128 | 20230524 | 1332 | 2120551 | 124 | Distribution Circuit | Animal | Squirrel | 26 | 3224 | 38.7884 | -121.1982 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0075168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845674 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | SWITCH | 31709 | 20230524 | 1808 | 20230525 | 742 | 2120804 | 814 | Distribution Circuit | 3rd Party | Vehicle | 265 | 215710 | 38.9389 | -121.0808 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0075294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845704 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | FUSE | 9591 | 20230524 | 1936 | 20230525 | 1213 | 2120957 | 997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 29910 | 39.212 | -121.0753 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0075306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845743 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | OCB | 1102/2 | 20230524 | 1958 | 20230525 | 545 | 2120841 | 587 | Distribution Circuit | 3rd Party | Vehicle | 1438 | 143098 | 39.2093 | -121.0615 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0075306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845709 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222994350295 | 20230525 | 442 | 20230525 | 1222 | 2120947 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 460 | 39.0426 | -120.947 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0075365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845747 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20230525 | 915 | 20230525 | 2124 | 2121134 | 729 | Distribution Circuit | 3rd Party | Vehicle | 869 | 114758 | 38.8963 | -121.1379 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0075448 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Three Phase Fault | 0 | No | Yes | No | 1845868 | 0 | EPSS Ckt | N | 2023 | ABC TIME OC
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 41505 | 20230525 | 1311 | 20230525 | 1610 | 2121350 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1432 | 39.1002 | -120.9578 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0075598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845928 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | TRANSFORMER | 222486045822 | 20230525 | 1825 | 20230525 | 2155 | 2121570 | 210 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 210 | 38.9216 | -121.1272 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 23-0075742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845972 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 344250 | 20230525 | 1841 | 20230526 | 235 | 2121576 | 474 | Distribution Circuit | 3rd Party | Vehicle | 11 | 5214 | 38.8239 | -120.0436 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0075702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1845966 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | SWITCH | 58498 | 20230526 | 701 | 20230526 | 711 | 2121864 | 10 | Distribution Circuit | Animal | Squirrel | 1487 | 14870 | 39.2089 | -121.0616 | No | Overcast;32-90 F | Recloser | Burned/flashed | 23-0075826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846052 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15487 | 20230526 | 1056 | 20230526 | 1105 | 2121876 | 9 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 9 | 38.969 | -121.4051 | No | Clear;32-90 F |  |  | 23-0076027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1846179 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223709134743 | 20230526 | 1104 | 20230526 | 1134 | 2122139 | 30 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 30 | 38.6133 | -120.7032 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 23-0076018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846172 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222332255950 | 20230526 | 2255 | 20230527 | 123 | 2122410 | 148 | Transformer only | Vegetation | Tree - fell into line | 21 | 3108 | 39.2003 | -121.1779 | No | Clear;32-90 F | Service conductor | Broken- wire on object | 23-0076253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846271 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 41535 | 20230527 | 757 | 20230527 | 845 | 2122568 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 144 | 39.0864 | -120.9667 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0076279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846295 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223281538547 | 20230528 | 518 | 20230528 | 809 | 2122902 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 513 | 38.7196 | -120.8509 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0076415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846404 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222502145465 | 20230528 | 1811 | 20230528 | 1903 | 2123170 | 52 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 52 | 38.9113 | -121.1214 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 23-0076480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846450 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | SWITCH | 1602 | 20230528 | 2002 | 20230528 | 2059 | 2123215 | 52 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 10284 | 39.252 | -120.7501 | No | Partly Cloudy;32-90 F |  |  | 23-0076489 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846457 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18678 | 20230529 | 941 | 20230529 | 1224 | 2123414 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 6947 | 38.6903 | -121.0039 | No | Clear;32-90 F |  |  | 23-0076556 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846518 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223865637515 | 20230529 | 1845 | 20230529 | 2230 | 2123584 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 225 | 38.6893 | -120.6472 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0076609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846557 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7983 | 20230530 | 946 | 20230530 | 1330 | 2123914 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 224 | 39.2472 | -121.1775 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0076726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846723 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4787 | 20230530 | 1345 | 20230530 | 1529 | 2124124 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 208 | 39.2952 | -120.991 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0076871 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846783 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 8877 | 20230601 | 1142 | 20230601 | 1416 | 2126693 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3234 | 39.2849 | -121.0669 | No | Clear;32-90 F |  |  | 23-0077832 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1847323 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | T11218 | 20230601 | 1154 | 20230601 | 1457 | 2126705 | 183 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 183 | 38.6964 | -120.9087 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0077908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847339 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20230601 | 1338 | 20230601 | 1520 | 2126768 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 6599 | 39.0715 | -120.9763 | No | Clear;32-90 F |  |  | 23-0077878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847331 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 221944046034 | 20230601 | 1956 | 20230601 | 2013 | 2126931 | 17 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 17 | 38.9285 | -121.3175 | No | Clear;32-90 F |  |  | 23-0078022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1847377 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | TRANSFORMER | 222263541801 | 20230602 | 623 | 20230602 | 744 | 2127052 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 243 | 38.8114 | -121.2067 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0078101 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847443 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7007 | 20230602 | 940 | 20230602 | 1034 | 2127290 | 54 | Distribution Circuit | Animal | Squirrel | 23 | 1242 | 39.2127 | -120.9877 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0078213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847557 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 12147 | 20230602 | 2153 | 20230603 | 2037 | 2127678 | 1364 | Distribution Circuit | 3rd Party | Vehicle | 66 | 63449 | 38.7521 | -121.0505 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0078508 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1847643 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 37339 | 20230604 | 1745 | 20230604 | 1927 | 2128552 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2040 | 38.799 | -121.1457 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0078738 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1847837 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20230605 | 246 | 20230605 | 338 | 2128811 | 52 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 355 | 18460 | 39.1444 | -120.908 | No | Partly Cloudy;32-90 F |  |  | 23-0078778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847881 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 5561 | 20230605 | 614 | 20230605 | 816 | 2128858 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1709 | 38.8833 | -121.0763 | No | Overcast;32-90 F |  |  | 23-0078799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1847898 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | OTHER | T5752 TWD T5751 | 20230605 | 950 | 20230605 | 1101 | 2129092 | 71 | Distribution Circuit | Equipment Failure/Involved | Underground | 43 | 3053 | 38.8594 | -121.2807 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0078804 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1848017 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6655 | 20230605 | 1138 | 20230605 | 1358 | 2129178 | 140 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 65 | 9100 | 39.3219 | -120.4384 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0078977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848073 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20230605 | 1453 | 20230605 | 1754 | 2129388 | 181 | Distribution Circuit | Environmental/External | Lightning | 1031 | 129764 | 38.9052 | -120.8374 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0079023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848083 | 0 | EPSS Ckt | Y | 2023 | A C GRD
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 20230605 | 1542 | 20230606 | 121 | 2129440 | 579 | Distribution Circuit | Environmental/External | Lightning | 20 | 6667 | 38.8528 | -120.789 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0079124 | OH | Sus | 35454305 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1848132 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223786038632 | 20230605 | 1548 | 20230606 | 158 | 2129439 | 610 | Transformer only | Vegetation | Tree - fell into line | 2 | 1220 | 38.7207 | -120.6749 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848105 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 21671 | 20230605 | 1626 | 20230605 | 2334 | 2129472 | 428 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2568 | 38.7371 | -120.8099 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0079088 | OH | Sus | 31651318 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | Yes | Yes | 1848108 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 39041 | 20230605 | 1914 | 20230606 | 143 | 2129627 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8169 | 39.0459 | -121.0663 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0079108 | OH | Sus | 45824555 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848120 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 83291 | 20230605 | 2101 | 20230605 | 2159 | 2130023 | 58 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 174 | 39.1448 | -121.1438 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079132 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1848141 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230605 | 2110 | 20230605 | 2120 | 2130031 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 284 | 2835 | 39.2562 | -120.7669 | No | Partly Cloudy;32-90 F |  |  | 23-0079133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848143 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 17231 | 20230606 | 523 | 20230606 | 917 | 2130147 | 234 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 13423 | 39.0285 | -121.2919 | No | Clear;32-90 F |  |  | 23-0079243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848248 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222650358325 | 20230606 | 820 | 20230606 | 1339 | 2130328 | 319 | Transformer only | 3rd Party | Vehicle | 1 | 319 | 39.2641 | -121.0651 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0079294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848348 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 50324 | 20230606 | 1431 | 20230606 | 1651 | 2130994 | 140 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1943 | 187105 | 38.6953 | -120.818 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0079507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Three Phase Fault | 0 | No | No | No | 1848450 | 0 | EPSS Ckt | N | 2023 | ABC GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21179 | 20230606 | 1450 | 20230607 | 300 | 2131058 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 21906 | 38.695 | -120.8114 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0079497 | OH | Sus | 31651417 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | Yes | No | 1848446 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230606 | 1708 | 20230606 | 1801 | 2131159 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 15047 | 39.2562 | -120.7669 | No | Overcast-Rain;32-90 F |  |  | 23-0079542 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848462 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7223 | 20230606 | 1711 | 20230606 | 1851 | 2131163 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 5700 | 39.23 | -121.1382 | No | Partly Cloudy;32-90 F |  |  | 23-0079552 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848470 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222249458346 | 20230606 | 1715 | 20230606 | 2139 | 2131229 | 264 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 264 | 39.2659 | -121.2062 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0079582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848495 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38845 | 20230606 | 1742 | 20230606 | 1923 | 2131184 | 101 | Distribution Circuit | 3rd Party | Vehicle | 27 | 2762 | 38.8109 | -121.1335 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 23-0079565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848483 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221612241152 | 20230607 | 805 | 20230607 | 1149 | 2131609 | 224 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 224 | 38.7953 | -121.4354 | No | Partly Cloudy;32-90 F |  |  | 23-0079849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1848764 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | JUMPER | OJ'S 1 S/OF CGC 222249458346 | 20230607 | 925 | 20230607 | 1315 | 2131738 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 230 | 39.2653 | -121.2063 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0079744 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1848690 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20911 | 20230607 | 1429 | 20230607 | 1812 | 2132041 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 223 | 38.5921 | -120.6089 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0080068 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1848834 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230608 | 704 | 20230608 | 817 | 2132334 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 20717 | 39.2562 | -120.7669 | No | Partly Cloudy;32-90 F |  |  | 23-0080149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848894 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 37349 | 20230608 | 1037 | 20230608 | 1144 | 2132638 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 67 | 38.9265 | -121.279 | No | Overcast;32-90 F |  |  | 23-0080309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849062 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | JUMPER | OJ'S 1 N/OF MTR 1004246729 | 20230608 | 1239 | 20230608 | 1338 | 2132741 | 59 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 354 | 38.8869 | -121.1499 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0080342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1849076 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 32875 | 20230609 | 858 | 20230609 | 1320 | 2133410 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 3552 | 39.0694 | -121.1616 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0080734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1849349 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222776552564 | 20230610 | 121 | 20230610 | 1613 | 2134031 | 892 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1784 | 39.1059 | -121.0231 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0081117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849578 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | OCB | 2107/2 | 20230610 | 409 | 20230610 | 1745 | 2134043 | 816 | Distribution Circuit | Equipment Failure/Involved | Underground | 3236 | 136913 | 38.8222 | -121.306 | No | Partly Cloudy;32-90 F | Elbow | Failed/Faulted | 23-0081090 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849503 | 0 | Non-EPSS | N | 2023 | PH/GRD INST & TIME
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222456653731 | 20230610 | 953 | 20230610 | 1212 | 2134190 | 139 | Transformer only | Animal | Squirrel | 1 | 139 | 39.1386 | -121.135 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849591 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 5963 | 20230610 | 1618 | 20230611 | 450 | 2134367 | 752 | Distribution Circuit | Environmental/External | Lightning | 37 | 5324 | 38.6331 | -120.5421 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081177 | OH | Sus | 35457040 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849622 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 20230610 | 1636 | 20230611 | 59 | 2134377 | 503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 10060 | 38.7853 | -120.6077 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0081234 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849679 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22089 | 20230610 | 1646 | 20230611 | 245 | 2134386 | 599 | Distribution Circuit | Environmental/External | Lightning | 7 | 1838 | 38.7497 | -120.6454 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081169 | OH | Sus | 35456980 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849615 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223976240822 | 20230610 | 1653 | 20230611 | 1126 | 2134389 | 1113 | Transformer only | Environmental/External | Lightning | 1 | 1113 | 38.7783 | -120.6058 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081239 | OH | Sus | 35457023 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849684 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223970541066 | 20230611 | 124 | 20230611 | 1603 | 2134516 | 879 | Transformer only | Environmental/External | Lightning | 1 | 879 | 38.7859 | -120.6077 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0081235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849680 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 3141 | 20230611 | 630 | 20230611 | 636 | 2134551 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 12 | 38.8072 | -120.7003 | No | Clear;32-90 F | Other | Failed/Faulted | 23-0081245 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849693 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222200646869 | 20230611 | 724 | 20230611 | 1339 | 2134574 | 375 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 375 | 38.9505 | -121.2278 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081263 | OH | Sus | 35457123 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849708 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223938040859 | 20230611 | 843 | 20230611 | 1715 | 2134719 | 512 | Transformer only | Environmental/External | Lightning | 1 | 512 | 38.7801 | -120.6193 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849738 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223961541100 | 20230611 | 911 | 20230611 | 1216 | 2134567 | 185 | Transformer only | Environmental/External | Lightning | 1 | 185 | 38.7867 | -120.6118 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 23-0081258 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849702 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 611199 | 20230611 | 1401 | 20230612 | 1339 | 2134656 | 1418 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 1418 | 38.6346 | -120.5242 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0081422 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849866 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 2667 | 20230612 | 910 | 20230612 | 1150 | 2135245 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 480 | 38.6785 | -120.8842 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0081490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1849969 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 939459 | 20230612 | 1308 | 20230614 | 737 | 2135393 | 1327 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 2549 | 38.632 | -120.5201 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0081579 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850025 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | JUMPER | OJ SS OF CGC 222839948117 | 20230612 | 1853 | 20230613 | 145 | 2135653 | 412 | Distribution Circuit | Animal | Other | 3 | 1236 | 38.984 | -121.0035 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0081691 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850076 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 9989 | 20230613 | 0 | 20230613 | 124 | 2135718 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 3528 | 38.9845 | -121.0054 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0081726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1850108 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223183638336 | 20230613 | 520 | 20230613 | 1001 | 2135737 | 281 | Transformer only | Vegetation | Tree - fell into line | 3 | 843 | 38.7137 | -120.8847 | No | Fog;32-90 F | Secondary | Broken- wire on ground | 23-0081760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850133 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | SWITCH | 51857 | 20230613 | 947 | 20230613 | 1252 | 2136024 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 370 | 38.8677 | -121.3002 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0081740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850278 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ 1 SS OF CGC 222284655753 | 20230613 | 1306 | 20230613 | 1446 | 2136189 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1000 | 39.195 | -121.1941 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0081942 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850344 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225620442305 | 20230613 | 1444 | 20230613 | 1549 | 2136245 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 390 | 38.8116 | -120.0286 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0082020 | OH | Sus | 31652229 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850359 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225571542726 | 20230613 | 1542 | 20230613 | 1659 | 2136281 | 77 | Transformer only | Environmental/External | Ice or snow | 1 | 77 | 38.8233 | -120.0452 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0082043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850365 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6045 | 20230613 | 1710 | 20230614 | 1301 | 2136336 | 1191 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 19056 | 38.9775 | -120.8892 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0082116 | UG | Sus | 45846456 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1850425 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6033 | 20230613 | 1711 | 20230614 | 124 | 2136333 | 493 | Distribution Circuit | Equipment Failure/Involved | Underground | 119 | 54587 | 38.986 | -120.8891 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0082053 | UG | Sus | 31652249 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850372 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ SS OF CGC222935359225 | 20230613 | 1717 | 20230613 | 2040 | 2136337 | 203 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 406 | 39.2882 | -120.9645 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0082048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850367 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 222657052930 | 20230614 | 511 | 20230614 | 1151 | 2136541 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1713 | 39.1163 | -121.0651 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0082124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850432 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRANSFORMER | 222747849331 | 20230614 | 819 | 20230614 | 1242 | 2136645 | 263 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 789 | 39.0199 | -121.0339 | No | Clear;32-90 F | Transformer | Leaking | 23-0082183 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850487 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 1812 | 20230614 | 858 | 20230614 | 1452 | 2136780 | 354 | Distribution Circuit | Equipment Failure/Involved | Underground | 36 | 1743 | 38.9841 | -120.8926 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0082053 | UG | Sus | 31652249 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850567 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6373 | 20230614 | 1309 | 20230614 | 1529 | 2136984 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 5740 | 39.1972 | -120.833 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0082339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850628 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 6585 | 20230614 | 1516 | 20230615 | 1328 | 2137122 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3220 | 38.9292 | -120.8907 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0082439 | OH | Sus | 31652347 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | Yes | No | 1850665 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5211 | 20230615 | 811 | 20230615 | 958 | 2137493 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 9737 | 38.8401 | -121.1386 | No | Clear;32-90 F |  |  | 23-0082597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1850776 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223462448152 | 20230615 | 906 | 20230615 | 942 | 2137559 | 36 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 36 | 38.9817 | -120.782 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0082634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850806 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223582648377 | 20230615 | 1044 | 20230615 | 1111 | 2137633 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 27 | 38.9878 | -120.7412 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0082696 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850839 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 8469 | 20230615 | 1200 | 20230615 | 1311 | 2137681 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 1562 | 38.9765 | -121.0192 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0082734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850850 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230615 | 1454 | 20230615 | 1648 | 2137825 | 114 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 936 | 106704 | 38.7391 | -120.6681 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1850880 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9867 | 20230615 | 1554 | 20230615 | 1725 | 2137868 | 91 | Distribution Circuit | Vegetation | Other ground vegetation | 4 | 364 | 39.3122 | -120.9812 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850898 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222121655636 | 20230615 | 1554 | 20230615 | 1725 | 2137864 | 91 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 91 | 39.1914 | -121.252 | No | Clear;32-90 F |  |  | 23-0082894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1850905 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 30899 | 20230615 | 1702 | 20230615 | 1854 | 2137905 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 2912 | 39.0205 | -120.8136 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0082886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850901 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS 2104 | 153132104 | TRANSFORMER | 222252857235 | 20230615 | 1839 | 20230615 | 2339 | 2137970 | 300 | Transformer only | Unknown Cause | Patrol - found nothing | 7 | 2100 | 39.236 | -121.2054 | No | Clear;32-90 F |  |  | 23-0082961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1850951 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230615 | 1936 | 20230615 | 2109 | 2138002 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 3906 | 38.8458 | -121.482 | No | Clear;32-90 F |  |  | 23-0082938 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1850925 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 4119 | 20230616 | 819 | 20230617 | 343 | 2138262 | 1164 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 3492 | 38.7879 | -121.2442 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0083213 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851164 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | SWITCH | 6305 | 20230616 | 907 | 20230616 | 1125 | 2138377 | 138 | Distribution Circuit | Company Initiated | Return Circuit Normal | 19 | 2618 | 39.0899 | -120.98 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1851089 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20230616 | 1109 | 20230616 | 1234 | 2138506 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 18530 | 39.1336 | -121.0717 | No | Clear;32-90 F |  |  | 23-0083147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851139 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230616 | 1137 | 20230616 | 1617 | 2138542 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 831 | 232680 | 38.6858 | -121.0119 | No | Clear;32-90 F |  |  | 23-0083168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851145 | 0 | EPSS Ckt | Y | 2023 | B- GRD
SIERRA | NEVADA | NARROWS-2104 | 153132104 | FUSE | 32967 | 20230616 | 1329 | 20230616 | 1645 | 2138646 | 196 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2548 | 39.258 | -121.2402 | No | Clear;Above 90 |  |  | 23-0083276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851191 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | SWITCH | 645945 | 20230616 | 1355 | 20230616 | 1601 | 2138666 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 4788 | 38.609 | -120.8441 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083178 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851168 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18957 | 20230616 | 1642 | 20230617 | 433 | 2138801 | 711 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 24174 | 38.7274 | -121.0567 | No | Clear;Above 90 |  |  | 23-0083324 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851247 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 20230616 | 1714 | 20230617 | 633 | 2139150 | 799 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2397 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0083326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851249 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20230616 | 1834 | 20230617 | 119 | 2138921 | 405 | Distribution Circuit | Company Initiated | Personnel- company | 2121 | 841341 | 38.7138 | -120.9394 | No | Clear;32-90 F | Recloser | Normal | 23-0083294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851204 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 221972146076 | 20230616 | 2022 | 20230617 | 925 | 2139002 | 783 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2349 | 38.9297 | -121.3081 | No | Clear;32-90 F | Jumper | Broken | 23-0083319 | OH | Sus | 45851627 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851239 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 16751 | 20230616 | 2036 | 20230616 | 2244 | 2139006 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 11648 | 38.8245 | -121.391 | No | Clear;32-90 F |  |  | 23-0083317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851231 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222707738646 | 20230617 | 456 | 20230617 | 2027 | 2139137 | 931 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3724 | 38.7237 | -121.0522 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0083340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851274 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1104 | 152061104 | FUSE | 7481 | 20230617 | 634 | 20230617 | 1242 | 2139153 | 368 | Distribution Circuit | Animal | Squirrel | 6 | 2208 | 38.7898 | -121.2291 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083343 | OH | Sus | 45851496 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851283 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 20230617 | 640 | 20230617 | 752 | 2139154 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 216 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0083327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851250 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 20230617 | 814 | 20230617 | 940 | 2139184 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 258 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0083351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851300 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20230617 | 1042 | 20230618 | 0 | 2139273 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 2846 | 282872 | 39.0317 | -121.0046 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1851319 | 0 | EPSS Ckt | Y | 2023 | C+GRD TARGET
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 9907 | 20230617 | 1414 | 20230617 | 1800 | 2139357 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2938 | 38.966 | -121.0245 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083389 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851340 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230617 | 1451 | 20230617 | 2028 | 2139406 | 337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 827 | 203030 | 38.6858 | -121.0119 | No | Clear;32-90 F |  |  | 23-0083396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851346 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222877650244 | 20230617 | 1551 | 20230618 | 123 | 2139454 | 572 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 572 | 39.0417 | -120.9887 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0083422 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851365 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3643 | 20230618 | 429 | 20230618 | 846 | 2139676 | 257 | Distribution Circuit | Animal | Bird found | 11 | 2827 | 38.7363 | -121.196 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0083484 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851429 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | RECLOSER | 1680 | 20230618 | 1538 | 20230618 | 1638 | 2139868 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 9120 | 38.7549 | -121.1919 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0083529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1851474 | 1 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 5281 | 20230618 | 2158 | 20230619 | 1129 | 2140103 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2443 | 38.8362 | -121.1807 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0083574 | OH | Sus | 31652685 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1851516 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 464570 | 20230619 | 559 | 20230619 | 1513 | 2140200 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 21606 | 39.1559 | -120.9797 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0083595 | OH | Sus | 45851909 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851537 | 0 | EPSS Ckt | Y | 2023 | A&B
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 2112 | 20230619 | 1149 | 20230619 | 1955 | 2140483 | 486 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 531 | 190336 | 39.2413 | -121.0566 | No | Clear;32-90 F |  |  | 23-0083651 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851633 | 0 | EPSS Ckt | Y | 2023 | B & GROUND
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | TRANSFORMER | 223364456315 | 20230619 | 1627 | 20230619 | 1941 | 2140644 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 388 | 39.207 | -120.8136 | No | Overcast;32-90 F | Fuse | Burned Open | 23-0083722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851686 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 4121 | 20230619 | 2310 | 20230620 | 1026 | 2140790 | 676 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2028 | 38.8988 | -121.0727 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0083751 | OH | Sus | 31652705 | NORTH VALLEY AND SIERRA | JUN | Open Circuit | 0 | No | No | No | 1851715 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223266538055 | 20230620 | 627 | 20230620 | 803 | 2140849 | 96 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 192 | 38.7064 | -120.8564 | No | Clear;32-90 F |  |  | 23-0083775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1851752 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | JUMPER | FLYING BELLS 1 SP E/OF CGC 222599645858 | 20230620 | 917 | 20230620 | 1220 | 2141077 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 183 | 38.9222 | -121.0871 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0083810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851846 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 394169 | 20230620 | 1245 | 20230620 | 1329 | 2141401 | 44 | Distribution Circuit | Company Initiated | Personnel- company | 9 | 396 | 38.6965 | -120.8366 | No | Clear;32-90 F | Recloser | Normal | 23-0083904 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851920 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2228 | 20230620 | 1345 | 20230620 | 1414 | 2141476 | 29 | Distribution Circuit | Company Initiated | Personnel- company | 228 | 6612 | 39.2009 | -121.209 | No | Clear;32-90 F | Fuse | Normal | 23-0083931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851929 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230620 | 1400 | 20230620 | 1411 | 2141494 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 934 | 10274 | 38.7391 | -120.6681 | No | Clear;32-90 F | Woodpin | Normal | 23-0083938 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851931 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 20230620 | 2044 | 20230621 | 1517 | 2141776 | 1113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 42420 | 39.4642 | -120.8458 | No | Clear;32-90 F | Insulator | Broken | 23-0084019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851973 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | OCB | 1104/2 | 20230620 | 2147 | 20230621 | 440 | 2141813 | 413 | Distribution Circuit | Animal | Squirrel | 1016 | 280938 | 38.6933 | -120.8261 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0084045 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851979 | 1 | EPSS Ckt | Y | 2023 | INST- GRD- PHASE OC
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20230620 | 2356 | 20230621 | 337 | 2141836 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 18343 | 39.4883 | -120.8571 | No | Clear;32-90 F | Insulator | Broken | 23-0084072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852006 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 660 | 20230621 | 633 | 20230621 | 748 | 2141922 | 75 | Distribution Circuit | Animal | Bird found | 453 | 33975 | 38.8494 | -121.1596 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0084103 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852025 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2784 | 20230621 | 721 | 20230621 | 1250 | 2141950 | 329 | Distribution Circuit | Animal | Squirrel | 1280 | 104424 | 39.2591 | -121.0187 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0084128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852036 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 2768 | 20230621 | 828 | 20230621 | 932 | 2142030 | 64 | Distribution Circuit | Animal | Squirrel | 178 | 11392 | 39.1028 | -120.9601 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0084170 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852086 | 0 | EPSS Ckt | Y | 2023 | A & GRD INST
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223022845646 | 20230621 | 853 | 20230621 | 1407 | 2142063 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 628 | 38.9148 | -120.9391 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0084347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852205 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | TRANSFORMER | 223068548540 | 20230621 | 858 | 20230621 | 1010 | 2142090 | 72 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 72 | 38.9943 | -120.922 | No | Clear;32-90 F |  |  | 23-0084191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852122 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 20230621 | 1537 | 20230621 | 1547 | 2142584 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1420 | 39.3638 | -120.7923 | No | Clear;32-90 F | Insulator | Normal | 23-0084019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852222 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | RECLOSER | 19642 | 20230621 | 1820 | 20230621 | 2006 | 2142647 | 106 | Distribution Circuit | Animal | Bird found | 847 | 89782 | 38.6832 | -121.0684 | No | Clear;32-90 F | Fuse | Normal | 23-0084439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852233 | 0 | EPSS Ckt | Y | 2023 | A & GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222815057025 | 20230622 | 831 | 20230622 | 1223 | 2142855 | 232 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 464 | 39.2275 | -121.0077 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0084589 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852388 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | INTERRUPTER | 507670 | 20230622 | 1155 | 20230622 | 1230 | 2143185 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 1015 | 38.6169 | -121.0633 | No | Overcast;32-90 F | Transformer (UG) | Broken | 23-0084680 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852454 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20230623 | 732 | 20230623 | 857 | 2143785 | 85 | Distribution Circuit | Animal | Bird found | 345 | 29325 | 38.9276 | -121.2469 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0084930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852588 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222267342318 | 20230623 | 825 | 20230623 | 1026 | 2143875 | 121 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 242 | 38.8257 | -121.2053 | No | Clear;32-90 F |  |  | 23-0085046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852712 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 35729 | 20230623 | 1026 | 20230623 | 1259 | 2144023 | 153 | Distribution Circuit | Animal | Squirrel | 64 | 9792 | 38.9585 | -121.0149 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852729 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11597 | 20230623 | 1055 | 20230623 | 1334 | 2144203 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 954 | 38.6992 | -120.9615 | No | Clear;32-90 F |  |  | 23-0085117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852731 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 12392 | 20230623 | 1056 | 20230623 | 1251 | 2144083 | 115 | Distribution Circuit | Animal | Squirrel | 871 | 100165 | 38.711 | -120.9433 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0085040 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852709 | 0 | EPSS Ckt | Y | 2023 | B & INST DCD
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 55686 | 20230623 | 1105 | 20230623 | 1604 | 2144125 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 164 | 49036 | 39.4652 | -120.8449 | No | Clear;32-90 F |  |  | 23-0085064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852717 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8021 | 20230623 | 1755 | 20230624 | 1310 | 2144359 | 1155 | Distribution Circuit | Animal | Bird found | 9 | 10395 | 39.463 | -120.8507 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852776 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20230624 | 1554 | 20230625 | 1042 | 2145015 | 1128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 507 | 324237 | 39.153 | -121.0774 | No | Clear;32-90 F |  |  | 23-0085356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852902 | 0 | EPSS Ckt | Y | 2023 | A+B
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222390153975 | 20230625 | 1119 | 20230625 | 1648 | 2145302 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 329 | 39.1464 | -121.1568 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852983 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20230625 | 2004 | 20230625 | 2229 | 2145510 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 270 | 29004 | 38.887 | -121.2381 | No | Clear;32-90 F |  |  | 23-0085447 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852999 | 0 | EPSS Ckt | Y | 2023 | A+C
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223204943047 | 20230626 | 1114 | 20230626 | 1136 | 2145975 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 38.8431 | -120.8753 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0085595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853196 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223621436625 | 20230626 | 1355 | 20230626 | 2033 | 2146213 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1194 | 38.6653 | -120.7326 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853270 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 538135 | 20230626 | 1927 | 20230626 | 2332 | 2146417 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 245 | 38.8864 | -121.2561 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0085837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853293 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223537137417 | 20230626 | 1955 | 20230627 | 135 | 2146427 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2280 | 38.6873 | -120.7625 | No | Clear;32-90 F | Fuse | Arcing | 23-0085843 | OH | Sus | 35461802 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853299 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | TRANSFORMER | 222562937844 | 20230627 | 703 | 20230627 | 900 | 2146611 | 117 | Transformer only | Animal | Bird found | 1 | 117 | 38.7023 | -121.1028 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0085974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853445 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222303055320 | 20230627 | 732 | 20230627 | 1435 | 2146623 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 846 | 39.1831 | -121.1887 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0085919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853352 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | OCB | 2106/2 | 20230627 | 736 | 20230627 | 1654 | 2146691 | 558 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5899 | 719565 | 38.7313 | -120.784 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 23-0002206 | OH | Sus | 31618293 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1853371 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 2645 | 20230627 | 958 | 20230627 | 1211 | 2146928 | 126 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 600 | 38.8123 | -120.0339 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0055438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1853473 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ'S @FLYING BELLS 4SPANS E/OF 2365 | 20230627 | 1750 | 20230628 | 125 | 2147251 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10920 | 39.2184 | -121.1885 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0086180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853536 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20230627 | 1959 | 20230627 | 2017 | 2147317 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 165 | 2970 | 39.4655 | -120.8443 | No | Clear;32-90 F |  |  | 23-0040752 | OH | Sus | 31605566 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853552 | 0 | EPSS Ckt | N | 2023 | SGF
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20230628 | 926 | 20230628 | 1153 | 2147698 | 147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 4557 | 38.7607 | -120.505 | No | Clear;32-90 F | Insulator | Broken | 23-0086352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853753 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 1348 | 20230628 | 1240 | 20230628 | 1316 | 2148099 | 36 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 4896 | 38.9867 | -121.3653 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0086517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853816 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 56817 | 20230628 | 1440 | 20230628 | 2249 | 2148162 | 489 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 3 | 1467 | 38.8574 | -121.2084 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0086849 | UG | Sus | 45864003 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853861 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51790 | 20230629 | 451 | 20230629 | 856 | 2148593 | 245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 200 | 49000 | 38.6639 | -120.9308 | No | Clear;32-90 F |  |  | 23-0086908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1853906 | 0 | EPSS Ckt | Y | 2023 | A - B
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20230629 | 1434 | 20230629 | 2251 | 2149068 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1016 | 193918 | 38.7759 | -120.4031 | No | Clear;32-90 F | Other | Broken | 23-0087265 | OH | Sus | 45865022 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854120 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2463 | 20230629 | 1443 | 20230629 | 1614 | 2149081 | 91 | Distribution Circuit | 3rd Party | Vehicle | 6 | 546 | 38.7643 | -120.5577 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854138 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222623757260 | 20230629 | 2300 | 20230630 | 430 | 2149462 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 35836 | 39.235 | -121.0747 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0087417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854219 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20230630 | 537 | 20230630 | 743 | 2149506 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2520 | 38.8769 | -121.017 | No | Clear;32-90 F |  |  | 23-0087450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854248 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222670449014 | 20230630 | 933 | 20230630 | 1045 | 2149710 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 216 | 39.0084 | -121.0613 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0087523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854348 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | OCB | 1104/2 | 20230630 | 1115 | 20230630 | 1251 | 2149829 | 96 | Distribution Circuit | 3rd Party | Vehicle | 1873 | 150981 | 38.9014 | -121.0878 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0087593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1854373 | 0 | EPSS Ckt | N | 2023 | B-C INST
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4787 | 20230630 | 1258 | 20230630 | 1659 | 2149919 | 241 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 482 | 39.2952 | -120.991 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0087641 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854395 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 31601 | 20230630 | 1345 | 20230630 | 1358 | 2149955 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 13 | 39.3316 | -120.5727 | No | Clear;32-90 F |  |  | 23-0087667 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854403 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 222651044997 | 20230630 | 1433 | 20230630 | 2148 | 2149885 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 5382 | 38.8984 | -121.0696 | No | Clear;Above 90 | Fuse | Broken | 23-0087685 | OH | Sus | 45867032 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854406 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 20623 | 20230630 | 1514 | 20230630 | 1822 | 2150038 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1316 | 38.7269 | -120.8341 | No | Clear;Above 90 | Fuse | Burned Open | 23-0087767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854431 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7089 | 20230630 | 1530 | 20230630 | 1923 | 2149980 | 233 | Distribution Circuit | Vegetation | Tree - grew into line | 67 | 15611 | 38.7626 | -120.5817 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0087715 | OH | Sus | 31654039 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854416 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | TRANSFORMER | T9611 | 20230630 | 1751 | 20230701 | 1236 | 2150185 | 1124 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 15462 | 38.7081 | -121.0608 | No | Clear;Above 90 | Conductor- Underground | Deteriorated | 23-0087802 | UG | Sus | 45867137 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1854464 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ 2 SPANS SS OF CGC 222971053592 | 20230630 | 1958 | 20230630 | 2318 | 2150308 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 18600 | 39.1332 | -120.9533 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0087749 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854447 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224040740194 | 20230701 | 49 | 20230701 | 910 | 2150528 | 501 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 4509 | 38.7615 | -120.584 | No | Clear;32-90 F | Secondary | Broken | 23-0087843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854521 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | RECLOSER | 50022 | 20230701 | 654 | 20230701 | 1144 | 2150597 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 50231 | 38.7357 | -121.1705 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0087851 | OH | Sus | 31653957 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1854529 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221696144889 | 20230701 | 958 | 20230701 | 1320 | 2150791 | 202 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 202 | 38.8977 | -121.4053 | No | Clear;Above 90 |  |  | 23-0087933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1854588 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | SWITCH | 418 | 20230701 | 1500 | 20230701 | 1524 | 2150920 | 24 | Distribution Circuit | Company Initiated | Return Circuit Normal | 53 | 1272 | 38.7148 | -121.1846 | No | Clear;Above 90 | Switch (UG) | Normal | 23-0087851 | UG | Sus | 31653957 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1854600 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20230701 | 1622 | 20230701 | 2108 | 2150963 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 11726 | 38.7404 | -120.6542 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0087974 | OH | Sus | 45867217 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854620 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20230701 | 2007 | 20230702 | 1252 | 2151469 | 1005 | Distribution Circuit | Equipment Failure/Involved | Underground | 1922 | 333178 | 38.6569 | -120.9928 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0088012 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854654 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12691 | 20230701 | 2048 | 20230702 | 40 | 2151530 | 232 | Distribution Circuit | Animal | Bird found | 32 | 7424 | 38.626 | -120.7375 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088079 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1854718 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21133 | 20230702 | 917 | 20230702 | 1446 | 2151959 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 987 | 38.6426 | -120.6995 | No | Clear;32-90 F | Other | Malfunctioning | 23-0088148 | OH | Sus | 45867513 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1854777 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | SWITCH | 4688 | 20230702 | 1016 | 20230702 | 1026 | 2151992 | 10 | Distribution Circuit | Equipment Failure/Involved | Underground | 194 | 1940 | 38.6806 | -120.9978 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0088123 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1854773 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | SWITCH | 4688 | 20230702 | 1218 | 20230702 | 1230 | 2152056 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 194 | 2328 | 38.6806 | -120.9978 | No | Clear;Above 90 | Transformer (UG) | Normal | 23-0088123 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1854789 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 8327 | 20230702 | 1300 | 20230702 | 1447 | 2152075 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2033 | 38.8974 | -121.3606 | No | Clear;Above 90 |  |  | 23-0088179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1854808 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | OCB | 1110/2 | 20230702 | 1421 | 20230703 | 138 | 2152165 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 1397 | 256995 | 39.0444 | -121.0909 | No | Clear;Above 90 | Conductor- Overhead | Broken | 23-0088178 | OH | Sus | 45867544 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854807 | 0 | EPSS Ckt | Y | 2023 | INST OC
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7065 | 20230702 | 1721 | 20230702 | 2031 | 2152309 | 190 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 9880 | 39.1869 | -120.9556 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0088227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854848 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222761055346 | 20230703 | 454 | 20230703 | 1048 | 2152968 | 354 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1062 | 39.1823 | -121.0271 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0088330 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1854957 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20230703 | 523 | 20230703 | 704 | 2152980 | 101 | Distribution Circuit | Animal | Bird found | 272 | 27472 | 38.887 | -121.2381 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1854948 | 0 | EPSS Ckt | Y | 2023 | A+C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20230703 | 1024 | 20230703 | 1505 | 2153231 | 281 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2743 | 245683 | 38.6943 | -120.6784 | No | Clear;32-90 F |  |  | 23-0088434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855015 | 0 | EPSS Ckt | Y | 2023 | A
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 222717454436 | 20230703 | 1320 | 20230703 | 1728 | 2153429 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 496 | 39.158 | -121.0423 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0088572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855050 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 5549 | 20230703 | 1505 | 20230703 | 1848 | 2153192 | 223 | Distribution Circuit | 3rd Party | Vehicle | 48 | 10704 | 38.8613 | -121.076 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0088557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855046 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11659 | 20230703 | 1526 | 20230703 | 1648 | 2153580 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 984 | 38.5702 | -120.7324 | No | Clear;Above 90 |  |  | 23-0088434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855061 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | JUMPER | BAD CONNECTOR 2 POLES W/OF CGC 222780834273 | 20230704 | 1110 | 20230704 | 1722 | 2154054 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 378 | 136191 | 38.6034 | -121.0292 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0088748 | OH | Sus | 45869747 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1855155 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | OCB | 1101/2 | 20230705 | 100 | 20230705 | 327 | 2154314 | 147 | Distribution Circuit | Animal | Squirrel | 2369 | 348243 | 38.9566 | -121.0427 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0088808 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855216 | 0 | EPSS Ckt | Y | 2023 | PHASE+GRD INST
SIERRA | PLACER | PLACER-1101 | 152461101 | FUSE | 8825 | 20230705 | 911 | 20230705 | 927 | 2154515 | 16 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 32 | 38.8933 | -121.0731 | No | Clear;32-90 F |  |  | 23-0088889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855297 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 56865 | 20230705 | 1102 | 20230705 | 1255 | 2154617 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 4633 | 39.1923 | -120.832 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0088943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1855321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5591 | 20230705 | 1200 | 20230705 | 1505 | 2154650 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3700 | 38.8608 | -120.7883 | No | Clear;32-90 F |  |  | 23-0089028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855335 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 73953 | 20230705 | 1205 | 20230705 | 1311 | 2154655 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 594 | 38.7848 | -121.1797 | No | Clear;32-90 F |  |  | 23-0089018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855334 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 215201 | 20230705 | 1555 | 20230705 | 1813 | 2154862 | 138 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 4002 | 38.7512 | -121.4391 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0089151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855370 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222937354664 | 20230705 | 1838 | 20230706 | 355 | 2154929 | 557 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1671 | 39.1632 | -120.9659 | No | Clear;32-90 F | Service conductor | Broken | 23-0089158 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855376 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 960916 | 20230706 | 1014 | 20230706 | 1637 | 2155325 | 383 | Distribution Circuit | Company Initiated | Improper Construction | 892 | 17544 | 39.2538 | -121.1981 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0066095 | OH | Sus | 35328981 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855506 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 3657 | 20230706 | 1110 | 20230706 | 1203 | 2155377 | 53 | Distribution Circuit | Animal | Squirrel | 1 | 53 | 39.0354 | -120.9939 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0089390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855528 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20230706 | 1118 | 20230706 | 1521 | 2155387 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 518 | 118659 | 39.153 | -121.0774 | No | Clear;32-90 F |  |  | 23-0089372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855519 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 18753 | 20230706 | 1320 | 20230706 | 1614 | 2155499 | 174 | Distribution Circuit | Animal | Squirrel | 12 | 2088 | 38.6982 | -120.8479 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0089552 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855573 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12842 | 20230706 | 1720 | 20230707 | 412 | 2155738 | 652 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 563 | 252631 | 38.7536 | -120.6799 | No | Clear;32-90 F |  |  | 23-0089582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855583 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 660 | 20230706 | 2014 | 20230707 | 56 | 2155815 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 453 | 91722 | 38.8494 | -121.1596 | No | Clear;32-90 F |  |  | 23-0089599 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855593 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6611 | 20230707 | 837 | 20230707 | 1038 | 2156086 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 3509 | 39.3192 | -120.432 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0089721 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855665 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225397341999 | 20230707 | 925 | 20230707 | 1040 | 2156157 | 75 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 900 | 38.8043 | -120.1071 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0089760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855698 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12842 | 20230707 | 1831 | 20230707 | 2042 | 2156537 | 131 | Distribution Circuit | Animal | Bird found | 563 | 73753 | 38.7536 | -120.6799 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090007 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855762 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 20230708 | 827 | 20230708 | 949 | 2156969 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1640 | 38.7853 | -120.6077 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0090069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855829 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | OCB | 1103/2 | 20230708 | 919 | 20230708 | 1506 | 2157022 | 347 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2313 | 709245 | 38.9014 | -121.088 | No | Clear;32-90 F |  |  | 23-0090080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855844 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 935730 | 20230708 | 1205 | 20230708 | 1643 | 2157148 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 24186 | 39.4387 | -120.9996 | No | Clear;32-90 F |  |  | 23-0090108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855861 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | RECLOSER | 2222 | 20230708 | 1423 | 20230709 | 1550 | 2157222 | 1527 | Distribution Circuit | 3rd Party | Metallic Balloon | 312 | 23297 | 38.7708 | -121.2524 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0090125 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855878 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | PLACER | DEL MAR 2105 | 152582105 | FUSE | 34869 | 20230708 | 1850 | 20230708 | 1937 | 2157347 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 3619 | 38.7977 | -121.2497 | No | Clear;32-90 F |  |  | 23-0090160 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855903 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 51696 | 20230709 | 653 | 20230709 | 1143 | 2157578 | 290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 991 | 131829 | 39.1003 | -120.9524 | No | Clear;32-90 F |  |  | 23-0090196 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855938 | 0 | EPSS Ckt | Y | 2023 | B-C
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2708 | 20230709 | 1024 | 20230709 | 1225 | 2157645 | 121 | Distribution Circuit | Animal | Bird found | 382 | 46222 | 38.7961 | -121.1633 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855956 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20230710 | 440 | 20230710 | 1020 | 2158005 | 340 | Distribution Circuit | Animal | Bird found | 454 | 32320 | 38.8637 | -121.1283 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856017 | 0 | EPSS Ckt | Y | 2023 | b-c
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | RECLOSER | 705100 | 20230710 | 731 | 20230710 | 911 | 2158127 | 100 | Distribution Circuit | Animal | Bird found | 105 | 10500 | 38.6812 | -120.836 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856027 | 0 | EPSS Ckt | Y | 2023 | A & G PHASE
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222990051862 | 20230710 | 820 | 20230710 | 1259 | 2158192 | 279 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 279 | 39.0851 | -120.9477 | No | Clear;32-90 F |  |  | 23-0090394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1856155 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ 3 SS OF CGC 222335352825 | 20230710 | 1157 | 20230710 | 1324 | 2158586 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 261 | 39.1167 | -121.1723 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856184 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | SWITCH | 217974 | 20230710 | 1213 | 20230710 | 1410 | 2158606 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 12051 | 38.7078 | -120.826 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0090457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856190 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | T5182 | 20230710 | 1459 | 20230711 | 219 | 2158791 | 680 | Distribution Circuit | 3rd Party | Vehicle | 11 | 7480 | 39.241 | -121.0644 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0090596 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856236 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | SWITCH | 1557 | 20230710 | 1726 | 20230710 | 2020 | 2158896 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 14964 | 39.1396 | -121.0695 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856242 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22349 | 20230710 | 2022 | 20230711 | 55 | 2158981 | 273 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 1368 | 38.6213 | -120.932 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856253 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222644956820 | 20230710 | 2147 | 20230711 | 1110 | 2158983 | 803 | Transformer only | Equipment Failure/Involved | Electrical Overload | 17 | 13651 | 39.223 | -121.0675 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090655 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856282 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221826548720 | 20230710 | 2147 | 20230710 | 2246 | 2159015 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 39.0027 | -121.3584 | No | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 23-0090656 | OH | Sus | 45882182 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856285 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | OTHER | T5628 TWD T5182 | 20230710 | 2207 | 20230710 | 2257 | 2159024 | 50 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 550 | 39.2418 | -121.0654 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0090616 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856287 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20230711 | 610 | 20230711 | 904 | 2159280 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 777 | 135198 | 38.7523 | -120.6821 | No | Clear;32-90 F |  |  | 23-0090672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856309 | 0 | EPSS Ckt | Y | 2023 | INST OC-B-GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ'S AT HARD TAP | 20230711 | 841 | 20230711 | 1247 | 2159483 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 492 | 39.0635 | -121.1276 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0090728 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856413 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | T0817 | 20230711 | 1044 | 20230712 | 27 | 2159797 | 823 | Distribution Circuit | 3rd Party | Vehicle | 19 | 13411 | 38.7482 | -121.1965 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0090863 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856543 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 56026 | 20230711 | 1657 | 20230712 | 414 | 2160101 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 234 | 40794 | 38.6906 | -120.7644 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0091001 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856588 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | RECLOSER | 8582 | 20230711 | 1908 | 20230711 | 2057 | 2160213 | 109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 381 | 41529 | 38.7245 | -120.802 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 23-0091026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856599 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | SWITCH | 9501 | 20230711 | 2253 | 20230711 | 2306 | 2160280 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 19 | 247 | 38.8026 | -121.4103 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1856634 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20230712 | 634 | 20230712 | 1341 | 2160370 | 427 | Distribution Circuit | Animal | Squirrel | 920 | 135436 | 38.9928 | -120.8828 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0091102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856653 | 0 | EPSS Ckt | Y | 2023 | A-GRD
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4381 | 20230712 | 834 | 20230712 | 840 | 2160515 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 39.2528 | -121.1847 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 23-0091159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856722 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6161 | 20230712 | 921 | 20230712 | 1452 | 2160606 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8937 | 39.0231 | -120.9583 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091188 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856789 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20230712 | 930 | 20230712 | 1426 | 2160628 | 296 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 840 | 121286 | 38.643 | -120.6953 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091202 | OH | Sus | 31655232 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856805 | 0 | EPSS Ckt | Y | 2023 | A/B
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2784 | 20230712 | 1047 | 20230712 | 1722 | 2160721 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 1280 | 63412 | 39.2591 | -121.0187 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0091274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856835 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223817734761 | 20230712 | 1238 | 20230712 | 1645 | 2160858 | 247 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 247 | 38.6135 | -120.6661 | No | Clear;32-90 F |  |  | 23-0091487 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856915 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20230712 | 1259 | 20230712 | 1455 | 2160877 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 462 | 37830 | 38.9945 | -121.026 | No | Clear;32-90 F |  |  | 23-0091353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856877 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 697216 | 20230712 | 1854 | 20230712 | 2120 | 2161160 | 146 | Distribution Circuit | Animal | Bird found | 221 | 32266 | 38.9366 | -121.1763 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0091514 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856924 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222683356936 | 20230712 | 1917 | 20230713 | 254 | 2161171 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1371 | 39.2261 | -121.0539 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0091517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856926 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223837633802 | 20230712 | 1936 | 20230713 | 340 | 2161187 | 484 | Transformer only | 3rd Party | Vehicle | 1 | 484 | 38.5868 | -120.658 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0091548 | OH | Sus | 31655156 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856941 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9775 | 20230712 | 2038 | 20230713 | 842 | 2161217 | 724 | Distribution Circuit | 3rd Party | Vehicle | 22 | 15928 | 39.3087 | -120.9742 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856936 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | TRANSFORMER | 223418938523 | 20230712 | 2302 | 20230713 | 30 | 2161274 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 528 | 38.7179 | -120.8029 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0091584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856965 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8483 | 20230713 | 1014 | 20230713 | 1050 | 2161561 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 2412 | 39.0185 | -121.0227 | No | Clear;32-90 F | Insulator | Failed/Faulted | 23-0091716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857135 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | RECLOSER | 1101/2 | 20230713 | 1227 | 20230713 | 1249 | 2161592 | 22 | Distribution Circuit | 3rd Party | Vehicle | 360 | 7920 | 39.214 | -120.8098 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857180 | 0 | EPSS Ckt | Y | 2023 | N/A
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7679 | 20230713 | 1558 | 20230713 | 2356 | 2161872 | 478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 80304 | 39.611 | -120.6049 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0091999 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | Yes | Yes | 1857229 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20230713 | 1621 | 20230714 | 602 | 2161892 | 821 | Distribution Circuit | 3rd Party | Vehicle | 1207 | 210284 | 39.0473 | -121.0486 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0092001 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857231 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222685658210 | 20230713 | 1812 | 20230714 | 222 | 2162023 | 490 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 490 | 39.2614 | -121.0527 | No | Clear;32-90 F |  |  | 23-0092070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857260 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20230713 | 2048 | 20230713 | 2207 | 2162037 | 79 | Distribution Circuit | Vegetation | Tree - branch fell on line | 374 | 29546 | 38.8101 | -121.1629 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0092063 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857252 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230714 | 812 | 20230714 | 1628 | 2162256 | 496 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2081 | 691696 | 38.7606 | -120.5589 | No | Clear;32-90 F |  |  | 23-0092174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857385 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | OJ'S 1 SS/OF CGC 222775148952 | 20230714 | 1009 | 20230714 | 1125 | 2162426 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 76 | 39.0055 | -121.0245 | No | Clear;32-90 F | Bushing | Broken | 23-0092236 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857465 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222445056820 | 20230714 | 1355 | 20230714 | 2008 | 2162689 | 373 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 746 | 39.2245 | -121.1371 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857530 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222972755727 | 20230714 | 1847 | 20230715 | 916 | 2162927 | 869 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 869 | 39.1924 | -120.9527 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857552 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 99373 | 20230714 | 1921 | 20230714 | 2100 | 2162928 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3675 | 323444 | 38.8745 | -121.0199 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857548 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 2100 | 20230715 | 38 | 20230715 | 557 | 2163033 | 319 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1192 | 348424 | 38.6928 | -120.7666 | No | Clear;32-90 F |  |  | 23-0092517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857584 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 31239 | 20230715 | 1748 | 20230715 | 1858 | 2163711 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 700 | 39.1009 | -121.1654 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857716 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20230715 | 1956 | 20230716 | 1152 | 2163818 | 956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1042 | 703940 | 38.8154 | -120.8221 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857733 | 0 | EPSS Ckt | Y | 2023 | C AND GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20507 | 20230715 | 2001 | 20230715 | 2144 | 2163830 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 412 | 38.6891 | -120.6708 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0092732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857749 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8725 | 20230716 | 508 | 20230716 | 626 | 2163995 | 78 | Distribution Circuit | Animal | Bird found | 16 | 1248 | 39.0749 | -121.112 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0092762 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857784 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223327945000 | 20230716 | 736 | 20230716 | 1316 | 2164077 | 340 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 340 | 38.8964 | -120.8318 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0092780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857807 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 166282 | 20230716 | 746 | 20230716 | 1204 | 2164046 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 329 | 84882 | 39.068 | -121.0335 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0092775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857797 | 0 | EPSS Ckt | Y | 2023 | A AND C
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223292034834 | 20230716 | 902 | 20230716 | 1007 | 2164085 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 130 | 38.6177 | -120.8488 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0092792 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857824 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 498932 | 20230716 | 943 | 20230716 | 1102 | 2164119 | 79 | Distribution Circuit | Animal | Bird found | 1873 | 142810 | 39.1181 | -121.0392 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0092785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857816 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | OCB | 2107/2 | 20230716 | 1833 | 20230717 | 429 | 2164584 | 596 | Distribution Circuit | Equipment Failure/Involved | Underground | 3236 | 564822 | 38.8222 | -121.306 | No | Partly Cloudy;Above 90 | Elbow | Broken | 23-0092892 | UG | Sus | 45889360 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857914 | 0 | Non-EPSS | N | 2023 | PH TIME AND GRD TIME
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | SWITCH | 1199 | 20230716 | 1859 | 20230716 | 1950 | 2164603 | 24 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 3305 | 48650 | 39.1439 | -121.0557 | No | Partly Cloudy;Above 90 | Circuit Breaker | Normal | 23-0092852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857921 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3407 | 20230716 | 2025 | 20230716 | 2100 | 2164764 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 105 | 39.0977 | -121.0183 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0092920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1857940 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222894538745 | 20230716 | 2109 | 20230717 | 245 | 2164788 | 336 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 336 | 38.7261 | -120.9867 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857979 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 294550 | 20230716 | 2358 | 20230717 | 236 | 2164915 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1025 | 161950 | 38.6674 | -120.9933 | No | Overcast;32-90 F |  |  | 23-0092967 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857981 | 0 | EPSS Ckt | Y | 2023 | A B 50 INST
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20230717 | 555 | 20230717 | 1026 | 2165017 | 271 | Distribution Circuit | Animal | Bird found | 1042 | 245014 | 38.8154 | -120.8221 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857995 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 20230717 | 815 | 20230717 | 2334 | 2165237 | 919 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 919 | 38.6344 | -120.6373 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093061 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858106 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230717 | 843 | 20230717 | 1248 | 2165182 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2073 | 484587 | 38.7606 | -120.5589 | No | Clear;32-90 F | Insulator | Broken | 23-0093131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858170 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | TAMARACK-1102 | 152291102 | SWITCH | 31443 | 20230717 | 1243 | 20230717 | 1907 | 2165576 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 12672 | 39.3111 | -120.5013 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0093197 | OH | Sus | 31655869 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858192 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | SWITCH | 51637 | 20230717 | 1438 | 20230717 | 1447 | 2165705 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 437 | 3933 | 39.1453 | -121.0567 | No | Clear;Above 90 | Circuit Breaker | Normal | 23-0093216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1858224 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | FB 2 POLES SS OF CGC 222641060670 | 20230717 | 1457 | 20230717 | 1553 | 2165722 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 112 | 39.3312 | -121.0667 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0093281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858220 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2410 | 20230717 | 2208 | 20230718 | 1024 | 2166079 | 736 | Distribution Circuit | Vegetation | Tree - branch fell on line | 175 | 15874 | 38.7953 | -121.1642 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0093447 | OH | Sus | 35469611 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858304 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4261 | 20230718 | 546 | 20230718 | 715 | 2166197 | 89 | Distribution Circuit | Animal | Bird found | 22 | 1958 | 39.1642 | -121.1509 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093505 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858339 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223497339207 | 20230718 | 752 | 20230718 | 1359 | 2166247 | 367 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 367 | 38.7366 | -120.775 | No | Clear;32-90 F |  |  | 23-0093805 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1858532 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223887035590 | 20230718 | 804 | 20230718 | 1433 | 2166263 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 389 | 38.6352 | -120.6401 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0093698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858512 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20230718 | 851 | 20230718 | 1052 | 2166374 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 507 | 49972 | 39.0351 | -121.0957 | No | Clear;32-90 F |  |  | 23-0093560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858424 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | PLACER | BELL-1109 | 152701109 | TRANSFORMER | 222620047400 | 20230718 | 1745 | 20230718 | 1751 | 2166894 | 6 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 6 | 38.9646 | -121.0795 | No | Clear;Above 90 | Service conductor | Broken | 23-0093981 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858618 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223063541590 | 20230718 | 1852 | 20230718 | 2340 | 2167240 | 288 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 576 | 38.8036 | -120.9269 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0093935 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858580 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 32515 | 20230718 | 2106 | 20230719 | 38 | 2167313 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 7420 | 39.6227 | -120.526 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0093943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858586 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223823239455 | 20230719 | 101 | 20230719 | 245 | 2167362 | 104 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 312 | 38.7423 | -120.6605 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0093988 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858626 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20230719 | 514 | 20230719 | 945 | 2167390 | 271 | Distribution Circuit | Animal | Bird found | 1223 | 331433 | 38.6406 | -120.7047 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0093992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858632 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 23279 | 20230719 | 718 | 20230719 | 935 | 2167602 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 548 | 38.6779 | -121.0259 | No | Clear;32-90 F |  |  | 23-0094058 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858703 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20230719 | 745 | 20230719 | 930 | 2167500 | 105 | Distribution Circuit | Animal | Bird found | 2130 | 156045 | 39.1995 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094039 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858658 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20230719 | 1020 | 20230719 | 1121 | 2167792 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 827 | 48084 | 38.643 | -120.6953 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0094149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858823 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8417 | 20230719 | 1538 | 20230719 | 2156 | 2168345 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 13230 | 39.4605 | -121.0327 | No | Clear;Above 90 | Conductor- Overhead | Deteriorated | 23-0094334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858903 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 20230719 | 1627 | 20230719 | 1716 | 2168326 | 49 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 8575 | 38.9133 | -120.9318 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0094353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858908 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 6795 | 20230719 | 1831 | 20230719 | 2010 | 2168423 | 99 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 21 | 2079 | 38.7623 | -120.5744 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0094384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858919 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S 1 SPAN S/S OF CGC 223552240344 | 20230719 | 2045 | 20230720 | 27 | 2168484 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 222 | 38.7674 | -120.7558 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0094399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858928 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20509 | 20230720 | 755 | 20230720 | 904 | 2168657 | 69 | Distribution Circuit | Animal | Squirrel | 6 | 414 | 38.6821 | -120.6604 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859040 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222818738030 | 20230720 | 1042 | 20230720 | 1459 | 2168831 | 257 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 514 | 38.7068 | -121.0135 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0094717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1859109 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20230720 | 1210 | 20230720 | 1352 | s1859103 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 533 | 34481 | 39.214 | -120.8098 | No | Clear;32-90 F |  |  | 23-0094678 |  | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859103 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20230720 | 1257 | 20230720 | 2148 | 2168966 | 531 | Distribution Circuit | 3rd Party | Vehicle | 518 | 39306 | 39.153 | -121.0774 | No | Clear;Above 90 | Pole-Wood | Broken- wire on ground | 23-0094720 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | Yes | No | 1859110 | 0 | EPSS Ckt | Y | 2023 | A&C
SIERRA | PLACER | CATLETT-1101 | 153761101 | FUSE | 37593 | 20230720 | 1313 | 20230720 | 1452 | 2168983 | 99 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1881 | 38.8025 | -121.4503 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0094732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859114 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20230720 | 1315 | 20230720 | 1556 | 2168991 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 862 | 118637 | 38.8932 | -120.9965 | No | Clear;Above 90 |  |  | 23-0094737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859116 | 0 | EPSS Ckt | Y | 2023 | A&C
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | OCB | 1101/2 | 20230720 | 1443 | 20230720 | 1626 | 2169115 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1060 | 109180 | 39.2092 | -121.0615 | No | Clear;Above 90 |  |  | 23-0094816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1859141 | 0 | EPSS Ckt | Y | 2023 | ABC GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7787 | 20230720 | 1443 | 20230720 | 1725 | 2169085 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 3134 | 39.1456 | -121.0784 | No | Clear;Above 90 |  |  | 23-0094896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859164 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 13755 | 20230720 | 2315 | 20230721 | 918 | 2169394 | 603 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 9045 | 38.6657 | -120.9916 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0094989 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859234 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230721 | 905 | 20230722 | 46 | 2169718 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 51191 | 39.2562 | -120.7669 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0095098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859374 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 50548 | 20230721 | 957 | 20230721 | 1040 | 2169802 | 43 | Distribution Circuit | Animal | Bird found | 240 | 10223 | 38.8541 | -121.1806 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859394 | 0 | EPSS Ckt | Y | 2023 | AC INST OC
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 221932646852 | 20230721 | 1219 | 20230721 | 2207 | 2169950 | 588 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1176 | 38.951 | -121.3215 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859462 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 497205 | 20230721 | 1447 | 20230721 | 2108 | 2170075 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 19431 | 39.4657 | -120.8447 | No | Clear;Above 90 | Insulator | Broken | 23-0095353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859463 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 93753 | 20230721 | 1816 | 20230721 | 2035 | 2170234 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 139 | 39.1992 | -121.2184 | No | Clear;Above 90 | Crossarm- Wood | Normal | 23-0095418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859485 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222707649100 | 20230721 | 1928 | 20230721 | 1942 | 2170308 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 42 | 39.0108 | -121.0483 | No | Clear;Above 90 | Lightning Arrestor | Broken | 23-0095429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859495 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20230721 | 2103 | 20230721 | 2301 | 2170422 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 512 | 60416 | 39.0351 | -121.0957 | No | Clear;32-90 F |  |  | 23-0095449 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859510 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4331 | 20230721 | 2146 | 20230722 | 17 | 2170410 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 6342 | 39.2003 | -121.2089 | No | Clear;32-90 F | Crossarm- Wood | Normal | 23-0095445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859508 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224436460690 | 20230721 | 2213 | 20230721 | 2243 | 2170449 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 19 | 570 | 39.3225 | -120.4331 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0095477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859537 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HIGGINS-1109 | 152691109 | FUSE | 9715 | 20230722 | 16 | 20230722 | 201 | 2170498 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3570 | 39.0031 | -121.091 | No | Clear;32-90 F |  |  | 23-0095487 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859546 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 11092 | 20230722 | 250 | 20230722 | 1353 | 2170526 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 915 | 277214 | 38.7741 | -120.9204 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0095491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1859550 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222705354732 | 20230722 | 919 | 20230722 | 1407 | 2170786 | 288 | Transformer only | Vegetation | Tree - fell into line | 6 | 1728 | 39.1658 | -121.0468 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0095541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859646 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222608051800 | 20230722 | 1031 | 20230722 | 1710 | 2170773 | 399 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 798 | 39.0846 | -121.0853 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859664 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 3657 | 20230722 | 1143 | 20230722 | 1212 | 2170784 | 29 | Distribution Circuit | Animal | Squirrel | 1 | 29 | 39.0354 | -120.9939 | No | Clear;Above 90 | Pole-Wood | Normal | 23-0095551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859653 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | JUMPER | VERT JUMPERS TWDS 8759 | 20230722 | 1157 | 20230722 | 1553 | 2170805 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3973 | 39.0357 | -121.0957 | No | Partly Cloudy;Above 90 | Pole-Wood | Broken | 23-0095547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859651 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | OCB | 1103/2 | 20230722 | 1423 | 20230722 | 1831 | 2170929 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2499 | 493847 | 38.6933 | -120.8262 | No | Clear;Above 90 |  |  | 23-0095576 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859667 | 0 | EPSS Ckt | Y | 2023 | A & GRD INST
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 861610 | 20230722 | 1850 | 20230722 | 2016 | 2171099 | 86 | Distribution Circuit | 3rd Party | Vehicle | 1208 | 75046 | 39.0467 | -121.0715 | No | Clear;Above 90 | Anchor or Guy | Broken | 23-0095601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859692 | 0 | EPSS Ckt | Y | 2023 | A/B
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4643 | 20230722 | 1913 | 20230722 | 2154 | 2171109 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 9982 | 39.2012 | -121.2131 | No | Partly Cloudy;Above 90 | Crossarm- Wood | Deteriorated | 23-0095608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859699 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20230722 | 2029 | 20230723 | 914 | 2171139 | 765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 23988 | 38.8543 | -121.1728 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859704 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20230722 | 2227 | 20230723 | 1532 | 2171209 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 3009 | 2027404 | 39.2082 | -121.2033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0095639 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859727 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222442043825 | 20230723 | 600 | 20230723 | 1335 | 2171438 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1365 | 38.8668 | -121.144 | No | Partly Cloudy;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859780 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 76297 | 20230723 | 605 | 20230723 | 819 | 2171307 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 626 | 38.8704 | -121.1449 | No | Clear;32-90 F |  |  | 23-0095662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859756 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 294550 | 20230723 | 758 | 20230723 | 1236 | 2171336 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1025 | 284950 | 38.6674 | -120.9933 | No | Clear;32-90 F |  |  | 23-0095665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859765 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20230723 | 1022 | 20230723 | 1749 | 2171391 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 10540 | 39.4553 | -121.053 | No | Partly Cloudy;32-90 F | Woodpin | Broken | 23-0095676 | OH | Sus | 45897564 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859777 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | HALSEY-1102 | 152241102 | OCB | 1102/2 | 20230723 | 1619 | 20230723 | 2155 | 2171723 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2363 | 298207 | 38.9566 | -121.0428 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0074153 | OH | Sus | 31615017 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1859809 | 0 | EPSS Ckt | N | 2023 | C & GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | 2 SS OF CGC 223734534441 | 20230723 | 2319 | 20230724 | 210 | 2171916 | 171 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 342 | 38.6043 | -120.6955 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0095748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859850 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 48484 | 20230724 | 829 | 20230724 | 1036 | 2172241 | 127 | Distribution Circuit | Animal | Bird found | 619 | 49081 | 39.2545 | -121.1458 | No | Clear;32-90 F | Regulator | Burned/flashed | 23-0095830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1859942 | 0 | EPSS Ckt | Y | 2023 | C+GRD
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 1411 | 20230724 | 1053 | 20230724 | 1143 | 2172477 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 450 | 38.7287 | -120.768 | No | Clear;32-90 F | Insulator | Broken | 23-0095914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860031 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230724 | 1109 | 20230724 | 1316 | 2172510 | 127 | Distribution Circuit | 3rd Party | Vehicle | 2004 | 245518 | 39.2417 | -121.0264 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0095930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1860041 | 0 | EPSS Ckt | Y | 2023 | B-C-SGF-DCD
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 20230724 | 1214 | 20230724 | 1721 | 2172571 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3377 | 39.4564 | -121.0375 | No | Clear;32-90 F | Insulator | Broken | 23-0095986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860061 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230725 | 109 | 20230725 | 300 | 2172977 | 111 | Distribution Circuit | Animal | Squirrel | 1872 | 207792 | 39.0997 | -121.05 | No | Clear;32-90 F | Regulator | Normal | 23-0096270 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1860172 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223224742837 | 20230725 | 158 | 20230725 | 944 | 2172994 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1398 | 38.8373 | -120.8685 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0096279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1860181 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19552 | 20230725 | 722 | 20230725 | 737 | 2173087 | 15 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 159 | 2385 | 38.7436 | -120.7818 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0080603 | OH | Sus | 35080029 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1860198 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20230725 | 830 | 20230725 | 929 | 2173220 | 59 | Distribution Circuit | Company Initiated | Personnel- company | 625 | 36875 | 38.7523 | -120.6821 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0096381 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1860337 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | T3723 | 20230725 | 1046 | 20230725 | 1159 | 2173439 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 584 | 38.6941 | -121.0049 | No | Clear;32-90 F |  |  | 23-0096481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1860384 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2204 | 20230725 | 1125 | 20230725 | 1421 | 2173480 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2004 | 232345 | 39.2643 | -120.9855 | No | Clear;32-90 F |  |  | 23-0096465 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1860378 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 31649 | 20230725 | 1223 | 20230726 | 19 | 2173795 | 716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2864 | 39.6858 | -120.6528 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0096746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1860437 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 19772 | 20230725 | 2232 | 20230726 | 550 | 2173936 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 60668 | 38.713 | -121.0455 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0096809 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1860483 | 0 | EPSS Ckt | Y | 2023 | INST OC & GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | JUMPER | BROKEN SPLICE SS OF 11605 | 20230726 | 821 | 20230726 | 830 | 2174135 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 81 | 38.6947 | -120.9639 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0096913 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1860596 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 4513 | 20230726 | 908 | 20230726 | 1229 | 2174224 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 11055 | 39.2037 | -120.8377 | No | Clear;32-90 F | Secondary | Broken | 23-0096934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860628 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20230726 | 1401 | 20230726 | 2232 | 2174540 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 15330 | 39.4553 | -121.053 | No | Clear;32-90 F | Insulator | Broken | 23-0097110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860718 | 0 | EPSS Ckt | Y | 2023 | N/A
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32307 | 20230726 | 2028 | 20230727 | 216 | 2174811 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 9396 | 39.2224 | -121.0833 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0097257 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860752 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222292941820 | 20230727 | 354 | 20230727 | 1133 | 2174949 | 459 | Transformer only | Vegetation | Tree - fell into line | 2 | 918 | 38.8119 | -121.1964 | No | Clear;32-90 F | Transformer | Broken | 23-0097387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860805 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 789062 | 20230727 | 925 | 20230727 | 950 | 2175207 | 25 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1 | 25 | 39.2416 | -121.0547 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0097471 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860939 | 0 | EPSS Ckt | Y | 2023 | GEN L/OUT ALARM
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 83079 | 20230727 | 1002 | 20230727 | 1701 | 2175463 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3771 | 39.1326 | -121.144 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0097622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1861007 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 871 | 20230727 | 1125 | 20230727 | 1211 | 2175412 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 565 | 25976 | 39.5657 | -120.6983 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0097333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860990 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2106 | 152582106 | TRANSFORMER | T8933 | 20230727 | 1415 | 20230727 | 2034 | 2175550 | 379 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 1895 | 38.7723 | -121.2306 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0097696 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861022 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | RECLOSER | 63100 | 20230727 | 1431 | 20230727 | 1444 | 2175542 | 13 | Distribution Circuit | Vegetation | Tree - fell into line | 210 | 2730 | 39.2282 | -121.1005 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0097670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861017 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223777537275 | 20230727 | 1511 | 20230727 | 1838 | 2175589 | 207 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 207 | 38.6825 | -120.6776 | No | Clear;32-90 F |  |  | 23-0097811 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861049 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230727 | 1648 | 20230728 | 254 | 2175677 | 606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1872 | 222205 | 39.0997 | -121.05 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0097764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861033 | 0 | EPSS Ckt | Y | 2023 | C
SIERRA | PLACER | DEL MAR-2106 | 152582106 | OTHER | T8934 TWD T8933 | 20230727 | 1927 | 20230727 | 2032 | 2175793 | 65 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 2015 | 38.773 | -121.2288 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0097690 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861051 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7879 | 20230728 | 145 | 20230728 | 332 | 2175914 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1071 | 38.8968 | -121.4519 | No | Clear;32-90 F |  |  | 23-0097883 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861099 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221682543279 | 20230728 | 837 | 20230728 | 1310 | 2176061 | 273 | Transformer only | Animal | Bird found | 1 | 273 | 38.8531 | -121.4098 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0098128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861304 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20230728 | 1005 | 20230728 | 1441 | 2176228 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 662 | 171582 | 38.9128 | -120.82 | No | Clear;32-90 F |  |  | 23-0098058 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861280 | 0 | EPSS Ckt | Y | 2023 | A+B
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20230728 | 1009 | 20230728 | 1212 | 2176229 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2091 | 38.8265 | -120.812 | No | Clear;32-90 F |  |  | 23-0098080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861287 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 20230728 | 1038 | 20230728 | 1511 | 2176297 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 12058 | 39.4642 | -120.8458 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0097949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861279 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 863 | 20230728 | 1122 | 20230728 | 1246 | 2176317 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1010 | 84840 | 39.4673 | -120.8462 | No | Clear;32-90 F | Insulator | Broken | 23-0097928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861286 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 2226 | 20230728 | 1607 | 20230728 | 1823 | 2176631 | 136 | Distribution Circuit | Animal | Squirrel | 843 | 89879 | 38.9598 | -121.1016 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0098206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861329 | 0 | EPSS Ckt | Y | 2023 | C & GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 5171 | 20230728 | 1728 | 20230728 | 2003 | 2176654 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 930 | 39.2697 | -120.9919 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861334 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20230728 | 1911 | 20230729 | 934 | 2176733 | 863 | Distribution Circuit | Animal | Bird found | 520 | 81960 | 38.9452 | -121.1218 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098221 | OH | Sus | 35472044 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861341 | 0 | EPSS Ckt | Y | 2023 | A B & GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230728 | 2032 | 20230728 | 2205 | 2176791 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2004 | 186372 | 39.2417 | -121.0264 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0098227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1861348 | 0 | EPSS Ckt | Y | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230729 | 605 | 20230729 | 814 | 2176905 | 129 | Distribution Circuit | Animal | Bird found | 664 | 56678 | 38.8415 | -121.0158 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0098268 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861386 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20230729 | 835 | 20230729 | 1001 | 2176988 | 71 | Distribution Circuit | Company Initiated | Other Circuits | 1003 | 77135 | 38.6779 | -120.8495 | No | Clear;32-90 F | Fuse | Arcing | 23-0098284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1861431 | 0 | EPSS Ckt | Y | 2023 | DCD EVENT DETECTED
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 676064 | 20230729 | 1141 | 20230729 | 1242 | 2177110 | 61 | Distribution Circuit | Company Initiated | Coordination failure | 26 | 1586 | 38.9974 | -120.9795 | No | Clear;32-90 F | Fuse | Normal | 23-0098322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1861467 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | OCB | 1107/2 | 20230729 | 1144 | 20230729 | 1308 | 2177116 | 84 | Distribution Circuit | Animal | Bird found | 2750 | 231000 | 39.2314 | -121.0345 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0098323 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861468 | 0 | EPSS Ckt | Y | 2023 | I OC
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | TRANSFORMER | T5566 | 20230729 | 1400 | 20230729 | 2319 | 2177164 | 559 | Distribution Circuit | Equipment Failure/Involved | Underground | 1025 | 342755 | 38.6766 | -120.9981 | No | Clear;Above 90 | Transformer (UG) | Broken | 23-0098345 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861483 | 0 | EPSS Ckt | Y | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221729144846 | 20230729 | 1441 | 20230729 | 1626 | 2177182 | 105 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 210 | 38.8967 | -121.3935 | No | Clear;Above 90 |  |  | 23-0098350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1861485 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 875BP | 20230729 | 1529 | 20230729 | 1633 | 2177231 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 558 | 35706 | 39.5634 | -120.6434 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0098311 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861489 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20230729 | 1847 | 20230729 | 2158 | 2177324 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1223 | 122993 | 38.6406 | -120.7047 | No | Clear;32-90 F |  |  | 23-0098368 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861502 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11659 | 20230729 | 2219 | 20230729 | 2355 | 2177440 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1152 | 38.5702 | -120.7324 | No | Clear;32-90 F |  |  | 23-0098410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861546 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 6063 | 20230730 | 838 | 20230730 | 1249 | 2177655 | 251 | Distribution Circuit | Animal | Squirrel | 28 | 7028 | 38.8216 | -121.192 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0098435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861597 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | RECLOSER | 2716 | 20230730 | 839 | 20230730 | 855 | 2177587 | 16 | Distribution Circuit | Animal | Squirrel | 2075 | 33200 | 38.811 | -121.2075 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0098435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861572 | 0 | EPSS Ckt | N | 2023 | TOC C GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20230730 | 2151 | 20230731 | 854 | 2178018 | 663 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1410 | 602860 | 39.1048 | -121.0852 | No | Clear;32-90 F |  |  | 23-0098494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1861632 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | TRANSFORMER | 222821751079 | 20230730 | 2235 | 20230731 | 1125 | 2178027 | 770 | Transformer only | Vegetation | Tree - fell into line | 1 | 770 | 39.0644 | -121.0072 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0098534 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1861672 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32285 | 20230731 | 1049 | 20230731 | 1338 | 2178409 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 4563 | 39.2286 | -121.0968 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098663 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861825 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | OCB | 1102/2 | 20230731 | 1459 | 20230731 | 1512 | 2178737 | 13 | Distribution Circuit | Company Initiated | Improper Construction | 641 | 8333 | 39.0363 | -120.9882 | No | Clear;Above 90 | Jumper | Arcing | 23-0098792 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861881 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230731 | 1624 | 20230731 | 1714 | 2178808 | 50 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 1401 | 38.8458 | -121.482 | No | Clear;Above 90 |  |  | 23-0098846 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861892 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221565242949 | 20230801 | 957 | 20230801 | 1818 | 2179423 | 501 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 501 | 38.8445 | -121.4515 | No | Clear;32-90 F |  |  | 23-0099092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862140 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20230801 | 1319 | 20230801 | 1427 | 2179594 | 68 | Distribution Circuit | Company Initiated | Personnel- company | 622 | 42296 | 39.2129 | -121.0129 | No | Partly Cloudy;32-90 F | Jumper | Normal | 23-0099166 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862167 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20230801 | 1418 | 20230802 | 205 | 2179640 | 707 | Distribution Circuit | 3rd Party | Vehicle | 1011 | 107076 | 38.6635 | -120.9306 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0099208 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | Yes | No | 1862182 | 0 | EPSS Ckt | Y | 2023 | B - C & GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221565444736 | 20230801 | 1433 | 20230801 | 1459 | 2179653 | 26 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 52 | 38.8936 | -121.4509 | No | Partly Cloudy;32-90 F |  |  | 23-0099220 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1862185 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20230801 | 1438 | 20230801 | 1517 | 2179673 | 39 | Distribution Circuit | Company Initiated | Personnel- company | 670 | 26130 | 39.2129 | -121.0129 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0099166 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862187 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ TWD CGC 222798648183 | 20230802 | 830 | 20230802 | 1105 | 2180242 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 465 | 38.9859 | -121.0169 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0099448 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1862344 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 9967 | 20230802 | 1228 | 20230802 | 1444 | 2180666 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2993 | 38.642 | -120.8518 | No | Clear;32-90 F |  |  | 23-0099664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862511 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222939052708 | 20230802 | 1903 | 20230802 | 2348 | 2181041 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 1710 | 39.1096 | -120.9654 | No | Clear;32-90 F | Service conductor | Deteriorated | 23-0099823 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1862582 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 660 | 20230803 | 629 | 20230803 | 742 | 2181127 | 73 | Distribution Circuit | Animal | Bird found | 454 | 33142 | 38.8494 | -121.1596 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1862604 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | PLACER | BELL-1109 | 152701109 | TRANSFORMER | 222639947320 | 20230803 | 806 | 20230803 | 1134 | 2181281 | 208 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 208 | 38.9622 | -121.0727 | No | Clear;32-90 F | Jumper | Broken | 23-0100100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862800 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20230803 | 848 | 20230803 | 1008 | 2181275 | 80 | Distribution Circuit | Animal | Bird found | 334 | 14948 | 38.8544 | -121.1507 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0099968 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1862685 | 0 | EPSS Ckt | Y | 2023 | A-C
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223235436568 | 20230803 | 854 | 20230803 | 1032 | 2181287 | 98 | Transformer only | Animal | Squirrel | 1 | 98 | 38.6648 | -120.868 | No | Clear;32-90 F | Fuse | Normal | 23-0100056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862778 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | SWITCH | 670928 | 20230803 | 923 | 20230803 | 933 | 2181384 | 10 | Distribution Circuit | Equipment Failure/Involved | Underground | 48 | 480 | 38.9052 | -120.84 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0061336 | UG | Sus | 35233996 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1862739 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2796 | 20230803 | 1130 | 20230803 | 1301 | 2181535 | 91 | Distribution Circuit | Vegetation | Tree - fell into line | 1408 | 42196 | 39.1981 | -121.0285 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1862797 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222795148402 | 20230803 | 1232 | 20230803 | 1305 | 2181611 | 33 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 33 | 38.9912 | -121.0178 | No | Clear;32-90 F |  |  | 23-0100152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1862829 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223393039034 | 20230803 | 1703 | 20230804 | 134 | 2181823 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2555 | 38.7327 | -120.8112 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862871 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 6519 | 20230803 | 1916 | 20230804 | 1136 | 2181915 | 980 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2940 | 39.3184 | -120.5631 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0100301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1862877 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 10575 | 20230804 | 219 | 20230804 | 1144 | 2182038 | 565 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4422 | 38.7398 | -121.0846 | No | Clear;32-90 F | Pothead(Riser Termination) | Broken | 23-0100371 | OH | Sus | 31659033 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862930 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222373651829 | 20230804 | 1145 | 20230804 | 1308 | 2182401 | 83 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 83 | 39.088 | -121.1633 | No | Clear;32-90 F | Fuse | Burned Open | 23-0100659 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863134 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 273542 | 20230804 | 1404 | 20230804 | 1445 | 2182525 | 41 | Distribution Circuit | Company Initiated | Personnel- company | 7 | 287 | 38.7126 | -120.9522 | No | Clear;32-90 F | Jumper | Normal | 23-0100714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863149 | 0 | EPSS Ckt | Y | 2023 | C AND OC TGT
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20230804 | 1736 | 20230805 | 322 | 2182697 | 586 | Distribution Circuit | 3rd Party | Vehicle | 41 | 15122 | 39.3451 | -121.0765 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0100800 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1863179 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 307494 | 20230805 | 106 | 20230805 | 359 | 2182813 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 29927 | 38.934 | -121.1793 | No | Clear;32-90 F |  |  | 23-0100831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1863214 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 223047936270 | 20230805 | 815 | 20230805 | 1230 | 2182905 | 255 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 510 | 38.6576 | -120.9337 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100864 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863292 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 343667 | 20230805 | 1500 | 20230805 | 1653 | 2183174 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 8249 | 38.9562 | -121.2184 | No | Clear;Above 90 | Insulator | Failed/Faulted | 23-0100920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1863328 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 41503 | 20230805 | 1951 | 20230805 | 2333 | 2183358 | 222 | Distribution Circuit | 3rd Party | Vehicle | 2 | 444 | 39.1002 | -120.9587 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0100973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1863374 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230806 | 610 | 20230806 | 923 | 2183496 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 833 | 94096 | 38.6858 | -121.0119 | No | Clear;32-90 F |  |  | 23-0100982 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863385 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | PLACER | PENRYN-1106 | 152561106 | RECLOSER | 51674 | 20230806 | 825 | 20230806 | 905 | 2183522 | 40 | Distribution Circuit | Animal | Bird found | 924 | 36960 | 38.8252 | -121.1919 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0100989 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1863395 | 0 | EPSS Ckt | Y | 2023 | A-C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230806 | 828 | 20230806 | 948 | 2183535 | 80 | Distribution Circuit | Animal | Bird found | 664 | 53057 | 38.8415 | -121.0158 | No | Clear;32-90 F | Fuse | Burned Open | 23-0100991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1863397 | 0 | EPSS Ckt | Y | 2023 | B-C
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230807 | 845 | 20230807 | 1248 | 2184219 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 833 | 202419 | 38.6858 | -121.0119 | No | Clear;32-90 F |  |  | 23-0101161 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863590 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | SWITCH | 1709 | 20230807 | 1212 | 20230807 | 1643 | 2184605 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 9553 | 39.1844 | -121.0655 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1863698 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | RECLOSER | 19692 | 20230807 | 1331 | 20230807 | 1644 | 2184704 | 191 | Distribution Circuit | Equipment Failure/Involved | Underground | 4084 | 553382 | 38.6772 | -121.0813 | No | Clear;Above 90 | Conductor- Underground | Broken | 23-0101301 | UG | Sus | 45916522 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863724 | 1 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | SWITCH | 750804 | 20230807 | 2057 | 20230808 | 309 | 2185106 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2604 | 39.1979 | -121.0573 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0101467 | OH | Sus | 31662075 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1863802 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | OCB | 1107/2 | 20230807 | 2345 | 20230808 | 919 | 2185149 | 574 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2888 | 650615 | 38.8448 | -121.1663 | No | Clear;32-90 F |  |  | 23-0101496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1863825 | 0 | EPSS Ckt | Y | 2023 | C - GRD - INST
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15257 | 20230808 | 156 | 20230808 | 651 | 2185163 | 295 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3835 | 38.9265 | -121.2597 | No | Clear;32-90 F |  |  | 23-0101504 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1863836 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 34701 | 20230808 | 901 | 20230808 | 1308 | 2185420 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 6669 | 39.1468 | -120.9002 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1863968 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | JUMPER | OJ'S 1 SPAN SS OF CGC 223002350060 | 20230808 | 1147 | 20230808 | 1355 | 2185758 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 128 | 39.0366 | -120.9448 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1864041 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20230808 | 1229 | 20230808 | 1550 | 2185794 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 18090 | 38.9 | -120.9074 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0101531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1864050 | 0 | EPSS Ckt | Y | 2023 | NA
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230808 | 1630 | 20230808 | 1818 | 2185995 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 1872 | 202176 | 39.0997 | -121.05 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0101901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864092 | 0 | EPSS Ckt | Y | 2023 | B
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20230808 | 1744 | 20230808 | 1927 | 2186065 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 199 | 20497 | 38.8543 | -121.1728 | No | Clear;32-90 F |  |  | 23-0101919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1864104 | 0 | EPSS Ckt | Y | 2023 | A C GRD
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222715654062 | 20230809 | 734 | 20230809 | 1000 | 2186304 | 146 | Transformer only | Animal | Squirrel | 4 | 584 | 39.1468 | -121.0434 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0102087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864327 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222347056915 | 20230809 | 1114 | 20230809 | 1745 | 2186476 | 391 | Transformer only | Equipment Failure/Involved | Underground | 1 | 391 | 39.2266 | -121.1724 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 23-0102147 | UG | Sus | 45918303 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864358 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2615 | 20230809 | 1130 | 20230809 | 1341 | 2186648 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2096 | 38.8249 | -120.0599 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0102149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1864359 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230809 | 1804 | 20230810 | 136 | 2186986 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2081 | 556982 | 38.7606 | -120.5589 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0102387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864417 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230810 | 238 | 20230810 | 1055 | 2187232 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2082 | 400396 | 38.7606 | -120.5589 | No | Clear;32-90 F | Regulator | Malfunctioning | 23-0102479 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1864462 | 0 | EPSS Ckt | Y | 2023 | A & C INST OC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230810 | 1706 | 20230810 | 1815 | 2188113 | 69 | Distribution Circuit | Company Initiated | Personnel- company | 2004 | 138276 | 39.2417 | -121.0264 | No | Clear;32-90 F | Recloser | Normal | 23-0102929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864746 | 0 | EPSS Ckt | Y | 2023 | DCD SGF
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 3383 | 20230811 | 819 | 20230811 | 911 | 2188375 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 1144 | 38.8033 | -120.0984 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0103121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1864867 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222981540800 | 20230811 | 1242 | 20230811 | 1330 | 2188675 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 96 | 38.7817 | -120.9554 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103331 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865013 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30865 | 20230811 | 1423 | 20230811 | 1615 | 2188738 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 224 | 39.2183 | -120.9703 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0103393 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865036 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 30665 | 20230812 | 522 | 20230812 | 745 | 2189001 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1001 | 38.9094 | -121.0916 | No | Clear;32-90 F |  |  | 23-0103557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865133 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20230812 | 923 | 20230812 | 1307 | 2189100 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1233 | 128332 | 39.2407 | -121.0299 | No | Clear;32-90 F |  |  | 23-0103583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865184 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 9432 | 20230812 | 1837 | 20230813 | 1426 | 2189365 | 1189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 622051 | 38.7312 | -120.8428 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0103667 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1865254 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 5097 | 20230812 | 2000 | 20230812 | 2116 | 2189388 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 4712 | 38.781 | -121.1735 | No | Clear;32-90 F |  |  | 23-0103678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865268 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 31563 | 20230812 | 2022 | 20230812 | 2230 | 2189395 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1024 | 38.8144 | -121.209 | No | Clear;32-90 F |  |  | 23-0103691 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865281 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | 222599746384 | 20230813 | 844 | 20230813 | 1127 | 2189559 | 163 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 326 | 38.9366 | -121.0874 | No | Clear;32-90 F | Jumper | Burned Open | 23-0103727 | OH | Sus | 45924842 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865329 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | TRANSFORMER | 222634938419 | 20230813 | 918 | 20230813 | 1710 | 2189570 | 472 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 472 | 38.7182 | -121.0777 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0103760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1865346 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | 222599746384 | 20230814 | 908 | 20230814 | 1329 | 2190185 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 522 | 38.9366 | -121.0874 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0103905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865523 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32161 | 20230814 | 955 | 20230814 | 1033 | 2190282 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 874 | 38.7897 | -121.2516 | No | Clear;32-90 F |  |  | 23-0103957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865575 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20230814 | 1726 | 20230814 | 2310 | 2190795 | 344 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 663 | 174671 | 38.9128 | -120.82 | No | Partly Cloudy;32-90 F |  |  | 23-0104262 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865670 | 0 | EPSS Ckt | Y | 2023 | C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230814 | 1807 | 20230814 | 1948 | 2190833 | 101 | Distribution Circuit | Animal | Bird found | 664 | 67037 | 38.8415 | -121.0158 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Normal | 23-0104257 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865667 | 0 | EPSS Ckt | Y | 2023 | B / C
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225240041319 | 20230814 | 2201 | 20230815 | 857 | 2191123 | 656 | Transformer only | Environmental/External | Lightning | 4 | 2624 | 38.7866 | -120.1625 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0104321 | OH | Sus | 35480808 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865725 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230814 | 2211 | 20230815 | 1304 | 2191162 | 893 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2081 | 1224681 | 38.7606 | -120.5589 | No | Partly Cloudy;32-90 F |  |  | 23-0104306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865713 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222813759217 | 20230815 | 414 | 20230815 | 859 | 2191223 | 285 | Transformer only | Animal | Squirrel | 1 | 285 | 39.2885 | -121.0073 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865740 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | RECLOSER | 51538 | 20230815 | 835 | 20230815 | 955 | 2191389 | 80 | Distribution Circuit | Animal | Bird found | 368 | 22200 | 38.767 | -121.1646 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0104432 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865868 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | JUMPER | OJS 2 N/O MTR #1010167245 | 20230815 | 855 | 20230815 | 1243 | 2191418 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1368 | 38.7517 | -121.3332 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0104414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865835 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 5097 | 20230815 | 1201 | 20230815 | 1259 | 2191660 | 58 | Distribution Circuit | Animal | Bird found | 62 | 3596 | 38.781 | -121.1735 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865922 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38015 | 20230815 | 1329 | 20230815 | 1642 | 2191748 | 193 | Distribution Circuit | Vegetation | Tree - grew into line | 5 | 965 | 38.8252 | -121.1589 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865930 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30929 | 20230815 | 1332 | 20230815 | 1449 | 2191765 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 77 | 38.896 | -120.9189 | No | Clear;Above 90 |  |  | 23-0104669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865947 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230815 | 1537 | 20230815 | 1731 | 2191893 | 114 | Distribution Circuit | Vegetation | Tree - fell into line | 937 | 106818 | 38.7391 | -120.6681 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104720 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865963 | 0 | EPSS Ckt | Y | 2023 | B-C
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | TRANSFORMER | T7867 | 20230815 | 1610 | 20230816 | 335 | 2191916 | 685 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 7063 | 38.655 | -121.0684 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 23-0104845 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866034 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20230815 | 1747 | 20230815 | 2128 | 2192065 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 863 | 168205 | 38.643 | -120.6953 | No | Clear;Above 90 |  |  | 23-0104786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865987 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 836878 | 20230816 | 936 | 20230816 | 1128 | 2192681 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4951 | 273331 | 38.7371 | -120.6759 | No | Clear;32-90 F | Metering Equipment | Malfunctioning | 23-0104980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866203 | 0 | EPSS Ckt | Y | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6277 | 20230816 | 1140 | 20230816 | 1224 | 2192710 | 44 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 176 | 39.0233 | -120.8146 | No | Partly Cloudy;Above 90 |  |  | 23-0105065 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866260 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223164739955 | 20230816 | 1241 | 20230816 | 1828 | 2192869 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 694 | 38.7588 | -120.8911 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0105159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866289 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20230816 | 1246 | 20230816 | 1520 | 2192910 | 154 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 650 | 100100 | 39.0757 | -121.1143 | No | Clear;Above 90 | Conductor- Overhead | Burned/flashed | 23-0105087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866266 | 0 | EPSS Ckt | Y | 2023 | C & GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223289838418 | 20230816 | 1304 | 20230816 | 1337 | 2192919 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 33 | 38.716 | -120.8479 | No | Clear;Above 90 | Transformer (OH) | Leaking | 23-0105098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866270 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222448742165 | 20230816 | 1600 | 20230816 | 1805 | 2193090 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 250 | 38.8212 | -121.1414 | No | Clear;Above 90 | Transformer | Broken | 23-0105263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866319 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJS 2P SS OF CGC#222308352025 | 20230816 | 1639 | 20230818 | 100 | 2193132 | 1941 | Distribution Circuit | 3rd Party | Other | 2 | 3882 | 39.0923 | -121.1872 | No | Partly Cloudy;Above 90 | Pole-Wood | Normal | 23-0105255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866314 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 223016236282 | 20230816 | 1814 | 20230817 | 109 | 2193223 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1660 | 38.6578 | -120.9447 | No | Overcast;Above 90 | Transformer (OH) | Failed/Faulted | 23-0105300 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866342 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | OTHER | ECHO SUMMIT | 20230816 | 1848 | 20230816 | 1905 | 2193255 | 17 | Distribution Circuit | 3rd Party | Other | 163 | 2771 | 0 | 0 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0105302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1866344 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 223046536309 | 20230816 | 1925 | 20230817 | 149 | 2193277 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1536 | 38.6587 | -120.9341 | No | Overcast;Above 90 | Transformer (OH) | Failed/Faulted | 23-0105310 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866349 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | OTHER | ECHO SUMMIT | 20230817 | 134 | 20230817 | 150 | s1866407 | 16 | Distribution Circuit | 3rd Party | Other | 297 | 4752 | 0 | 0 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0105302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1866407 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | TSB 2 SPANS NORTH OF CGC 222930539983 | 20230817 | 833 | 20230817 | 1528 | 2193518 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1245 | 38.7604 | -120.9732 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0105422 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866435 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7153 | 20230817 | 920 | 20230817 | 1048 | 2193608 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 6864 | 39.2455 | -121.0448 | No | Clear;32-90 F |  |  | 23-0105529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1866526 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20230817 | 1339 | 20230817 | 2328 | 2193846 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 32775 | 38.9276 | -121.2469 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0105624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1866568 | 0 | EPSS Ckt | Y | 2023 | C & GRD
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 660 | 20230817 | 1646 | 20230817 | 2234 | 2194032 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 39116 | 38.8494 | -121.1596 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0105748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866588 | 0 | EPSS Ckt | Y | 2023 | B+GRD
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38025 | 20230817 | 1738 | 20230817 | 1835 | 2194066 | 57 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 513 | 38.8251 | -121.152 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0105766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866594 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230818 | 200 | 20230818 | 1929 | 2194327 | 1049 | Distribution Circuit | Equipment Failure/Involved | Underground | 833 | 116596 | 38.6858 | -121.0119 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0105849 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866660 | 0 | EPSS Ckt | Y | 2023 | B/GRD
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 3147 | 20230818 | 232 | 20230818 | 340 | 2194352 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 612 | 39.0029 | -121.0199 | No | Clear;32-90 F | Insulator | Broken | 23-0105851 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866662 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38015 | 20230818 | 606 | 20230818 | 750 | 2194432 | 104 | Distribution Circuit | Animal | Bird found | 5 | 520 | 38.8252 | -121.1589 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0105891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1866684 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20230818 | 804 | 20230818 | 1101 | 2194523 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1173 | 207381 | 38.6779 | -120.8495 | No | Clear;32-90 F |  |  | 23-0105926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866721 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S @ CGC 222960040320 | 20230818 | 810 | 20230818 | 1210 | 2194503 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 240 | 38.7687 | -120.9626 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0105912 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866692 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20230818 | 1341 | 20230818 | 1717 | 2194976 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 17928 | 39.4883 | -120.8571 | No | Partly Cloudy;32-90 F |  |  | 23-0106150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1866885 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | JUMPER | OJ'S @ CGC 222551737666 | 20230818 | 1510 | 20230818 | 1745 | 2195122 | 155 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 1085 | 38.6974 | -121.1068 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106225 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866906 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2140 | 20230818 | 2133 | 20230819 | 200 | 2195347 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 106899 | 39.2895 | -120.9854 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1866934 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20230819 | 946 | 20230819 | 1032 | 2195571 | 46 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 6210 | 39.0914 | -121.0565 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106338 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1867038 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 774652 | 20230819 | 1112 | 20230819 | 1536 | 2195624 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 13 | 3432 | 38.693 | -120.7152 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106350 | OH | Sus | 31663978 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1867048 | 0 | EPSS Ckt | Y | 2023 | NONE
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230819 | 1415 | 20230819 | 1850 | 2195726 | 275 | Distribution Circuit | Animal | Bird found | 746 | 87379 | 38.6858 | -121.0119 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0106390 | OH | Sus | 31664013 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867066 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20230819 | 1615 | 20230819 | 1701 | 2195813 | 46 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2115 | 81120 | 39.2042 | -121.2005 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0106415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867086 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20230819 | 1856 | 20230820 | 1846 | 2196205 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 1665 | 193438 | 39.0162 | -120.8351 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0106455 | OH | Sus | 35482465 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1867120 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | JUMPER | OJ @ CGC# 100000051964 HARD TAP | 20230819 | 2048 | 20230819 | 2337 | 2196355 | 169 | Distribution Circuit | Animal | Bird found | 1 | 169 | 38.7518 | -121.0554 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0106390 | OH | Sus | 31664013 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1867146 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | JUMPER | OJ @ CGC# 100000051964 HARD TAP | 20230819 | 2048 | 20230819 | 2337 | 2196355 | 169 | Distribution Circuit | Animal | Bird found | 1 | 169 | 38.7518 | -121.0554 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0106390 | OH | Sus | 31664013 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1867146 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 20230819 | 2110 | 20230820 | 1324 | 2196476 | 974 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4870 | 38.8277 | -120.9417 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106527 | OH | Sus | 31664104 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1867197 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223047736629 | 20230819 | 2215 | 20230820 | 315 | 2196509 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 600 | 38.6679 | -120.9335 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0106510 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867178 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20230819 | 2216 | 20230820 | 8 | 2196559 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 681 | 71873 | 38.8546 | -121.1508 | No | Partly Cloudy;32-90 F |  |  | 23-0106513 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867182 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 8597 | 20230819 | 2218 | 20230820 | 1253 | 2196564 | 875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 11675 | 38.8189 | -121.1641 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106555 | OH | Sus | 31664103 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1867227 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4899 | 20230820 | 39 | 20230820 | 1149 | 2196612 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 22780 | 39.1993 | -121.187 | No | Clear;32-90 F | Other | Burned Open | 23-0106542 | OH | Sus | 35482450 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1867214 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 59597 | 20230820 | 46 | 20230820 | 1345 | 2196650 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3116 | 38.789 | -121.1642 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106550 | OH | Sus | 31664025 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | Yes | No | 1867221 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | OCB | 1107/2 | 20230820 | 205 | 20230820 | 310 | 2196680 | 65 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2855 | 185575 | 38.8448 | -121.1663 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106559 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1867232 | 0 | EPSS Ckt | Y | 2023 | INST -GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20230820 | 210 | 20230820 | 1223 | 2196683 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 867 | 121926 | 39.1911 | -120.9965 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106556 | OH | Sus | 31664015 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1867228 | 0 | EPSS Ckt | Y | 2023 | A-GRD
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20230820 | 700 | 20230820 | 907 | 2196747 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 681 | 61441 | 38.8546 | -121.1508 | No | Overcast;32-90 F |  |  | 23-0106581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867256 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | OCB | 2105/2/NORM | 20230820 | 1823 | 20230821 | 800 | 2197241 | 817 | Distribution Circuit | Animal | Bird found | 3780 | 831370 | 39.2354 | -121.269 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0106732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1867380 | 0 | EPSS Ckt | Y | 2023 | A + B + C + GRD
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 4813 | 20230820 | 2240 | 20230821 | 5 | 2197398 | 85 | Distribution Circuit | Animal | Bird found | 48 | 4080 | 39.0366 | -121.0763 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0106774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867422 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 5117 | 20230821 | 339 | 20230821 | 844 | 2197529 | 305 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 14959 | 38.8054 | -121.2425 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0106808 | OH | Sus | 45934730 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867458 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | RECLOSER | 251946 | 20230821 | 502 | 20230821 | 910 | 2197532 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 992 | 195273 | 38.904 | -121.0666 | No | Overcast-Drizzle;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0106803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867455 | 0 | EPSS Ckt | Y | 2023 | B GRD INST
SIERRA | PLACER | PLACER-1103 | 152461103 | OCB | 1103/2 | 20230821 | 716 | 20230821 | 1052 | 2197609 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2313 | 389304 | 38.9014 | -121.088 | No | Overcast-Drizzle;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0106836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867481 | 0 | EPSS Ckt | Y | 2023 | INST OC- GRD
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 542186 | 20230821 | 849 | 20230821 | 1231 | 2197748 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 533 | 19845 | 39.2144 | -120.8088 | No | Overcast-Fog-Rain;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0106888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867549 | 0 | EPSS Ckt | Y | 2023 | C MTT
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222610052805 | 20230821 | 1147 | 20230821 | 1941 | 2198562 | 474 | Transformer only | 3rd Party | Vehicle | 2 | 948 | 39.1129 | -121.0814 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 23-0107236 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867744 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224582660256 | 20230821 | 1241 | 20230821 | 1820 | 2198057 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 843 | 37543 | 39.3102 | -120.3815 | No | Clear;32-90 F | Insulator | Broken | 23-0107207 | OH | Sus | 31664038 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1867728 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20230821 | 1307 | 20230821 | 2007 | 2198222 | 420 | Distribution Circuit | 3rd Party | Vehicle | 882 | 370440 | 39.2609 | -120.9817 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 23-0107069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867672 | 0 | EPSS Ckt | Y | 2023 | A/B
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20230821 | 1307 | 20230821 | 1348 | 2198227 | 41 | Distribution Circuit | Company Initiated | Coordination failure | 206 | 8446 | 39.274 | -120.9698 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0107070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867673 | 0 | EPSS Ckt | Y | 2023 | B/C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9519 | 20230821 | 1412 | 20230821 | 1815 | 2198318 | 243 | Distribution Circuit | Environmental/External | Lightning | 146 | 17353 | 38.7148 | -120.6676 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107158 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867707 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223083045790 | 20230821 | 1445 | 20230821 | 1830 | 2198367 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 450 | 38.919 | -120.917 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0107174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867711 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20230821 | 1518 | 20230821 | 1537 | 2198402 | 19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 863 | 16258 | 38.643 | -120.6953 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0107184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867713 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 19809 | 20230821 | 1538 | 20230821 | 1630 | 2198442 | 52 | Distribution Circuit | Vegetation | Tree - branch fell on line | 863 | 29882 | 38.6157 | -120.7026 | No | Partly Cloudy-Drizzle-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0107209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867729 | 1 | EPSS Ckt | Y | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230821 | 1546 | 20230822 | 920 | 2198448 | 1054 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 202 | 170632 | 39.2562 | -120.7669 | No | Partly Cloudy-Rain-Lightning;32-90 F |  |  | 23-0107212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867731 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | PLACER | PENRYN-1107 | 152561107 | OCB | 1107/2 | 20230821 | 1559 | 20230821 | 1758 | 2198480 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2888 | 343672 | 38.8448 | -121.1663 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0107214 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Three Phase Fault | 0 | No | No | No | 1867733 | 0 | EPSS Ckt | Y | 2023 | INST OC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 39544 | 20230821 | 1603 | 20230821 | 1927 | s1867738 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 362 | 46722 | 38.6345 | -120.5557 | No | Clear;32-90 F |  |  | 23-0107209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867738 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12685 | 20230821 | 1612 | 20230821 | 1815 | 2198519 | 123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 3690 | 38.6465 | -120.564 | No | Clear-Lightning;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0107256 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867758 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223870034367 | 20230821 | 1709 | 20230821 | 1842 | 2198580 | 93 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 186 | 38.6026 | -120.6475 | No | Overcast-Drizzle;32-90 F |  |  | 23-0107263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867765 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9523 | 20230821 | 1714 | 20230821 | 1916 | 2198586 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 244 | 38.8788 | -121.4144 | No | Clear;32-90 F |  |  | 23-0107270 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1867768 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223882338785 | 20230821 | 1751 | 20230821 | 2127 | 2198617 | 216 | Transformer only | Environmental/External | Lightning | 2 | 432 | 38.724 | -120.6405 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867774 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | TRANSFORMER | 100000040705 | 20230821 | 1857 | 20230822 | 150 | 2198658 | 413 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 413 | 38.7282 | -120.8186 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 23-0107317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867813 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20230822 | 1101 | 20230822 | 1207 | 2199263 | 66 | Distribution Circuit | Company Initiated | Personnel- company | 2002 | 132132 | 39.2417 | -121.0264 | No | Partly Cloudy-Drizzle;32-90 F | Recloser | Normal | 23-0107528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868005 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15249 | 20230822 | 1639 | 20230822 | 1728 | 2199552 | 49 | Distribution Circuit | Animal | Bird found | 9 | 441 | 38.9265 | -121.2688 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0107771 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1868082 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222811155768 | 20230822 | 1918 | 20230822 | 2010 | 2199629 | 52 | Transformer only | 3rd Party | Vehicle | 1 | 52 | 39.1937 | -121.0092 | No | Clear;32-90 F | Secondary | Broken | 23-0107782 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1868097 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | OCB | 1101/2 | 20230822 | 2043 | 20230823 | 512 | 2199647 | 509 | Distribution Circuit | 3rd Party | Vehicle | 2430 | 221888 | 38.9566 | -121.0427 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0107784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1868099 | 0 | EPSS Ckt | Y | 2023 | PRI RLY PH GRD INST
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2392 | 20230822 | 2102 | 20230823 | 941 | 2199685 | 759 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2130 | 328440 | 39.1451 | -120.9717 | No | Partly Cloudy;32-90 F |  |  | 23-0107786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1868100 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 20230823 | 1829 | 20230823 | 1838 | 2200596 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3676 | 33084 | 38.9144 | -121.0197 | No | Clear;32-90 F | Other | Broken | 23-0108297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1868407 | 0 | EPSS Ckt | Y | 2023 | N/A
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222328757668 | 20230823 | 1957 | 20230823 | 2055 | 2200663 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 39.2474 | -121.1785 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0108341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868427 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222328757668 | 20230823 | 1957 | 20230823 | 2055 | 2200663 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 39.2474 | -121.1785 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0108341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868427 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20230823 | 2040 | 20230824 | 925 | 2200692 | 765 | Distribution Circuit | Company Initiated | Coordination failure | 663 | 507195 | 38.9128 | -120.82 | No | Clear;32-90 F | Recloser | Normal | 23-0108338 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1868425 | 0 | EPSS Ckt | Y | 2023 | A+C
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15257 | 20230824 | 153 | 20230824 | 1049 | 2200791 | 536 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 6968 | 38.9265 | -121.2597 | No | Clear;32-90 F |  |  | 23-0108557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868670 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33147 | 20230824 | 754 | 20230824 | 1341 | 2200900 | 347 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 694 | 39.2687 | -121.0068 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1868516 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222129847595 | 20230824 | 1454 | 20230824 | 1507 | 2201426 | 13 | Transformer only | 3rd Party | Dig in- 3rd party | 2 | 26 | 38.9712 | -121.2529 | No | Clear;Above 90 | Other | Broken | 23-0108737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868742 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 13771 | 20230824 | 1932 | 20230824 | 1955 | 2201666 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 789 | 38.6648 | -121.0017 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 23-0080052 | OH | Sus | 35312202 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868780 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 2645 | 20230824 | 1945 | 20230825 | 1 | 2201678 | 256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 768 | 38.8123 | -120.0339 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0108717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | Yes | No | 1868782 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6185 | 20230824 | 2043 | 20230824 | 2150 | 2201692 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1072 | 39.0561 | -120.9817 | No | Clear;32-90 F | Insulator | Broken | 23-0108812 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1868786 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 32536 | 20230825 | 203 | 20230825 | 510 | 2201751 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 85646 | 39.2398 | -120.9935 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0108886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1868850 | 0 | EPSS Ckt | Y | 2023 | A+C
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9063 | 20230825 | 1157 | 20230825 | 1354 | 2202198 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1638 | 39.2185 | -120.9648 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0109148 | OH | Sus | 45941137 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869039 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20230825 | 1207 | 20230825 | 1229 | 2202208 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 445 | 9790 | 39.214 | -120.8098 | No | Clear;32-90 F | Circuit Breaker | Normal | 23-0109152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869046 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20230826 | 737 | 20230826 | 1258 | 2202681 | 321 | Distribution Circuit | Animal | Squirrel | 1084 | 92501 | 38.8101 | -121.1629 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869167 | 0 | EPSS Ckt | Y | 2023 | A+GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15261 | 20230826 | 759 | 20230826 | 1057 | 2202690 | 178 | Distribution Circuit | Animal | Squirrel | 14 | 2492 | 38.9264 | -121.2561 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869221 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | JUMPER | OJS @ CGC 222194457777 | 20230827 | 4 | 20230827 | 805 | 2203066 | 481 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1443 | 39.2509 | -121.2261 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869292 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2392 | 20230827 | 856 | 20230827 | 1105 | 2203258 | 129 | Distribution Circuit | Animal | Squirrel | 551 | 57352 | 39.1451 | -120.9717 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0109495 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869317 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20230827 | 923 | 20230827 | 1215 | 2203264 | 172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1218 | 86100 | 38.6406 | -120.7047 | No | Clear;32-90 F |  |  | 23-0109499 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869321 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20230827 | 1115 | 20230827 | 1344 | 2203318 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 48044 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 23-0109509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869329 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20230827 | 2016 | 20230827 | 2144 | 2203463 | 88 | Distribution Circuit | Animal | Bird found | 272 | 23936 | 38.887 | -121.2381 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0109562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869354 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20230828 | 306 | 20230828 | 945 | 2203570 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 863 | 219450 | 38.643 | -120.6953 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869382 | 0 | EPSS Ckt | Y | 2023 | A+GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2392 | 20230828 | 741 | 20230828 | 1451 | 2203683 | 430 | Distribution Circuit | Animal | Squirrel | 551 | 46027 | 39.1451 | -120.9717 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0109628 | OH | Sus | 31665552 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869415 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | PLACER | WISE-1101 | 152271101 | JUMPER | 5245 | 20230828 | 909 | 20230828 | 1519 | 2203834 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1110 | 38.8826 | -121.0968 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0109753 | OH | Sus | 31665571 | NORTH VALLEY AND SIERRA | AUG | Open Circuit | 0 | No | Yes | No | 1869577 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223870034367 | 20230828 | 1033 | 20230828 | 1432 | 2203982 | 239 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 478 | 38.6026 | -120.6475 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0109778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869591 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 58527 | 20230828 | 1246 | 20230828 | 1726 | 2204158 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1400 | 38.7467 | -120.7915 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109806 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869616 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20230828 | 1725 | 20230828 | 1842 | 2204392 | 77 | Distribution Circuit | Company Initiated | Personnel- company | 121 | 9317 | 39.6081 | -120.6068 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0109936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869647 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 693294 | 20230828 | 1730 | 20230828 | 1744 | 2204358 | 14 | Distribution Circuit | Vegetation | Tree - branch fell on line | 239 | 3346 | 38.912 | -121.2487 | No | Clear;Above 90 | Conductor- Overhead | Arcing | 23-0109939 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869648 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | JUMPER | OJ 2 SS MTR#1007481255 | 20230828 | 2155 | 20230829 | 602 | 2204487 | 487 | Distribution Circuit | 3rd Party | Vehicle | 1 | 487 | 38.7178 | -120.8336 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0109963 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869667 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33703 | 20230828 | 2204 | 20230829 | 455 | 2204504 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 822 | 39.2057 | -121.0203 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0109981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1869685 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223236642746 | 20230828 | 2354 | 20230829 | 140 | 2204511 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 38.8352 | -120.8652 | No | Clear;32-90 F | Secondary | Broken | 23-0109991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1869689 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4569 | 20230829 | 32 | 20230829 | 231 | 2204532 | 119 | Distribution Circuit | Animal | Bird found | 85 | 10115 | 39.1994 | -121.1803 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0110004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869694 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | OCB | 2104/2 | 20230829 | 449 | 20230829 | 835 | 2204566 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3922 | 754246 | 38.6555 | -121.0604 | No | Clear;32-90 F | Stepdown | Failed/Faulted | 23-0110014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869704 | 0 | EPSS Ckt | Y | 2023 | A+GRD
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 19652 | 20230829 | 836 | 20230829 | 1021 | 2204741 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 16485 | 38.6715 | -121.0081 | No | Clear;32-90 F | Stepdown | Failed/Faulted | 23-0110014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1869869 | 0 | EPSS Ckt | N | 2023 | A B C GRD
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224335060258 | 20230829 | 1813 | 20230830 | 1231 | 2205367 | 1098 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1098 | 39.3131 | -120.4693 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0110467 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869999 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | RECLOSER | 284874 | 20230830 | 924 | 20230830 | 1631 | 2205787 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 166 | 15112 | 38.9105 | -121.0868 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0110642 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1870167 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | OCB | 2106/2 | 20230831 | 321 | 20230831 | 1801 | 2206543 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 5338 | 1710626 | 38.7313 | -120.784 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0111044 | OH | Sus | 45947351 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1870336 | 0 | EPSS Ckt | Y | 2023 | A+C+TIME OC
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | OCB | 1103/2 | 20230831 | 352 | 20230831 | 402 | 2206564 | 10 | Distribution Circuit | Company Initiated | Operating error | 1159 | 11590 | 38.6597 | -120.9473 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0103615 | OH | Sus | 35442456 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1870338 | 0 | EPSS Ckt | Y | 2023 | GRD+ INST
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | INTERRUPTER | 18092 | 20230831 | 838 | 20230831 | 923 | 2206785 | 45 | Distribution Circuit | Equipment Failure/Involved | Underground | 28 | 1260 | 38.6544 | -120.9689 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0103615 | UG | Sus | 35442456 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1870449 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222656656746 | 20230831 | 1210 | 20230831 | 1422 | 2207009 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 132 | 39.2211 | -121.0634 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 23-0111292 | OH | Sus | 31666013 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1870578 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | SWITCH | 774186 | 20230901 | 249 | 20230901 | 551 | 2207497 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1237 | 181394 | 38.7259 | -120.7943 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0111577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870677 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 9575 | 20230901 | 616 | 20230901 | 801 | 2207517 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2310 | 38.7503 | -121.2241 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0111612 | OH | Sus | 45949104 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870689 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 4939 | 20230901 | 829 | 20230901 | 950 | 2207606 | 81 | Distribution Circuit | Animal | Bird found | 2 | 162 | 38.9239 | -121.1676 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0111686 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1870759 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1101 | 152461101 | RECLOSER | 208930 | 20230901 | 1102 | 20230901 | 1348 | s1870795 | 166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 14276 | 38.8984 | -121.0811 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0111739 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1870795 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | SWITCH | 460 | 20230901 | 1238 | 20230901 | 1245 | 2207894 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 22 | 154 | 38.7485 | -121.2216 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 23-0111612 | OH | Sus | 45949104 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1870818 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | SWITCH | 971 | 20230901 | 1525 | 20230901 | 1621 | 2207944 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 435 | 24360 | 39.2063 | -120.9802 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0111931 | OH | Sus | 45949377 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1870835 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223271845534 | 20230901 | 1551 | 20230901 | 1651 | 2208025 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 120 | 38.9109 | -120.8516 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0111973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870842 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | RECLOSER | 556218 | 20230902 | 722 | 20230902 | 744 | 2208336 | 22 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 643 | 14146 | 38.6342 | -120.9454 | No | Overcast-Fog;32-90 F |  |  | 23-0112055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1870909 | 0 | EPSS Ckt | Y | 2023 | inst oc a-c
SIERRA | PLACER | DEL MAR-2105 | 152582105 | TRANSFORMER | 222136941303 | 20230902 | 744 | 20230902 | 1130 | 2208352 | 226 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 904 | 38.7982 | -121.2514 | No | Clear-Drizzle;32-90 F | Transformer (OH) | Broken | 23-0112071 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1870932 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20230902 | 1005 | 20230902 | 1624 | 2208598 | 379 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1218 | 93525 | 38.6406 | -120.7047 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 23-0112098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1870948 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | OCB | 1103/2 | 20230902 | 1338 | 20230902 | 1957 | 2208740 | 379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1159 | 150857 | 38.6597 | -120.9473 | No | Overcast;32-90 F | Woodpin | Broken | 23-0112124 | OH | Sus | 31667423 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870958 | 0 | EPSS Ckt | Y | 2023 | INST OC GRD
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230902 | 1629 | 20230902 | 2347 | 2208817 | 438 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 936 | 136254 | 38.7391 | -120.6681 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1870971 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222802857930 | 20230902 | 2319 | 20230903 | 951 | 2208935 | 632 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 3792 | 39.2532 | -121.0113 | No | Overcast;32-90 F | Secondary | Broken | 23-0112223 | OH | Sus | 31667440 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | No | No | 1871034 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20230903 | 504 | 20230903 | 625 | 2208980 | 81 | Distribution Circuit | Animal | Squirrel | 1873 | 151713 | 39.0997 | -121.05 | No | Overcast-Fog-Drizzle;32-90 F | Regulator | Normal | 23-0112203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871014 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222685446067 | 20230903 | 757 | 20230903 | 841 | 2209010 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 176 | 38.9276 | -121.0568 | No | Overcast-Fog;32-90 F | Fuse | Broken | 23-0112216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871027 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230903 | 804 | 20230903 | 1017 | 2209014 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 833 | 70853 | 38.6858 | -121.0119 | No | Overcast-Drizzle;32-90 F |  |  | 23-0112210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871021 | 0 | EPSS Ckt | Y | 2023 | C PH AND GRD TGT
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 76952 | 20230904 | 1258 | 20230904 | 2046 | 2209406 | 468 | Distribution Circuit | Animal | Squirrel | 904 | 184415 | 39.253 | -121.1971 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0112340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871123 | 0 | EPSS Ckt | Y | 2023 | C & GRD
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 48484 | 20230904 | 1259 | 20230904 | 1402 | s1871128 | 63 | Distribution Circuit | Company Initiated | Coordination failure | 619 | 38997 | 39.2545 | -121.1458 | No | Clear;32-90 F | Recloser | Normal | 23-0112340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871128 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230904 | 1444 | 20230904 | 1643 | 2209468 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 111384 | 38.7391 | -120.6681 | No | Clear;32-90 F |  |  | 23-0112354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871133 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20230905 | 803 | 20230905 | 1405 | 2209718 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2081 | 575321 | 38.7606 | -120.5589 | No | Clear;32-90 F |  |  | 23-0112475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871260 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 891 | 20230905 | 1225 | 20230905 | 1455 | 2210117 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 600 | 39.553 | -120.859 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0112532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1871364 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20230905 | 1627 | 20230905 | 2336 | 2210308 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 1009 | 218918 | 38.6635 | -120.9306 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112774 | OH | Sus | 31667664 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1871387 | 0 | EPSS Ckt | Y | 2023 | C - GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223335338257 | 20230905 | 2046 | 20230906 | 406 | 2210439 | 440 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1760 | 38.7113 | -120.8321 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0112844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871412 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2072 | 20230906 | 725 | 20230906 | 1116 | 2210574 | 231 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 357 | 61154 | 38.9256 | -121.2468 | No | Clear;32-90 F |  |  | 23-0112924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871446 | 0 | EPSS Ckt | Y | 2023 | INST & GRD
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | TRANSFORMER | 222624356431 | 20230906 | 1006 | 20230906 | 1245 | 2210689 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 636 | 39.2124 | -121.0749 | No | Clear;32-90 F | Secondary | Broken | 23-0113053 | OH | Sus | 31667493 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871594 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20230906 | 1239 | 20230906 | 1309 | 2210971 | 30 | Distribution Circuit | Animal | Squirrel | 73 | 2190 | 38.7721 | -120.5821 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0113193 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871642 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20230906 | 1249 | 20230906 | 1542 | 2210981 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 172 | 21776 | 39.3251 | -120.6429 | No | Clear;32-90 F |  |  | 23-0113184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871640 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222791254679 | 20230906 | 1326 | 20230906 | 1855 | 2211003 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 658 | 39.1641 | -121.0167 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0113220 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871646 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222067545383 | 20230906 | 1608 | 20230906 | 1710 | 2211119 | 62 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 124 | 38.9104 | -121.2747 | No | Clear;32-90 F |  |  | 23-0113356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871684 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 4525 | 20230907 | 745 | 20230907 | 820 | 2211404 | 35 | Distribution Circuit | Animal | Squirrel | 5 | 175 | 39.0356 | -120.9922 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0113473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871758 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1101/2 | 20230907 | 802 | 20230907 | 906 | 2211455 | 64 | Distribution Circuit | Company Initiated | Personnel- company | 2227 | 142528 | 39.02 | -120.8294 | No | Clear;32-90 F | Recloser | Normal | 23-0113485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1871778 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | PLACER | BELL-1108 | 152701108 | JUMPER | OJ @ CGC# 22491748683 | 20230907 | 900 | 20230907 | 1107 | 2211611 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 127 | 38.9999 | -121.1246 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0113461 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1871840 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 8837 | 20230907 | 1116 | 20230907 | 1223 | 2211760 | 67 | Distribution Circuit | Animal | Squirrel | 10 | 670 | 39.0413 | -121.0776 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0113664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871913 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | OCB | 1101/2 | 20230907 | 2042 | 20230908 | 1506 | 2212162 | 1104 | Distribution Circuit | 3rd Party | Vehicle | 1059 | 59274 | 39.2092 | -121.0615 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0113879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1871976 | 0 | EPSS Ckt | Y | 2023 | N/A
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222671556565 | 20230908 | 244 | 20230908 | 431 | 2212321 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 1819 | 39.2159 | -121.0581 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0113933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872002 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | OLETA-1102 | 163541102 | RECLOSER | 186326 | 20230908 | 834 | 20230908 | 1217 | 2212540 | 223 | Distribution Circuit | Company Initiated | Personnel- company | 21 | 4643 | 38.482 | -120.8432 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872203 | 0 | EPSS Ckt | Y | 2023 | DCD
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32285 | 20230908 | 1136 | 20230908 | 1359 | 2212740 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3861 | 39.2286 | -121.0968 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0114145 | OH | Sus | 31668174 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1872169 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 85766 | 20230908 | 1516 | 20230908 | 1854 | 2212962 | 218 | Distribution Circuit | Company Initiated | Personnel- company | 260 | 56680 | 38.8027 | -120.9071 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0114277 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872212 | 0 | EPSS Ckt | Y | 2023 | SGF + DCD
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 881364 | 20230909 | 837 | 20230909 | 1011 | 2213484 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 5546 | 38.8856 | -121.2378 | Yes | Clear;32-90 F |  |  | 23-0114410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Three Phase Fault | 0 | No | No | No | 1872352 | 0 | EPSS Ckt | N | 2023 | a-b-c
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 38311 | 20230909 | 1540 | 20230909 | 1710 | 2213891 | 90 | Distribution Circuit | Animal | Bird found | 20 | 1800 | 38.897 | -121.433 | Yes | Clear;Above 90 | Conductor- Overhead | Normal | 23-0114515 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1872446 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | JUMPER | 1P E/O 10256 LAKE SPAULDING DRIVE | 20230909 | 1549 | 20230909 | 1920 | 2213896 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1055 | 39.3154 | -120.6396 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0114496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1872435 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223266834303 | 20230910 | 113 | 20230910 | 553 | 2214410 | 280 | Transformer only | 3rd Party | Fire- house or bldg. | 2 | 560 | 38.6032 | -120.858 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0114616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872554 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230910 | 1714 | 20230910 | 1817 | 2214833 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 2646 | 38.8458 | -121.482 | No | Clear;Above 90 |  |  | 23-0114715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1872674 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20230910 | 1950 | 20230910 | 2222 | 2214957 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 4258 | 38.8458 | -121.482 | No | Clear;32-90 F |  |  | 23-0114740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872707 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6613 | 20230911 | 123 | 20230911 | 512 | 2215049 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 9623 | 39.3178 | -120.4494 | No | Clear;32-90 F |  |  | 23-0114763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872739 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7259 | 20230911 | 721 | 20230911 | 739 | 2215113 | 18 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 19 | 342 | 39.2274 | -121.1009 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 23-0114789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1872757 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 881364 | 20230911 | 1042 | 20230911 | 1439 | 2215478 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 13983 | 38.8856 | -121.2378 | No | Clear;32-90 F |  |  | 23-0114995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1872988 | 0 | EPSS Ckt | Y | 2023 | SGF + 50 INST
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2796 | 20230911 | 1806 | 20230911 | 1822 | 2215882 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 1476 | 23616 | 39.1981 | -121.0285 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1873086 | 0 | EPSS Ckt | Y | 2023 | SGF+DCD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20230911 | 1822 | 20230911 | 1839 | 2215911 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 2130 | 36210 | 39.1995 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1873090 | 0 | EPSS Ckt | Y | 2023 | SGF + DCD
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | RECLOSER | 50142 | 20230912 | 709 | 20230912 | 1457 | 2216169 | 468 | Distribution Circuit | Equipment Failure/Involved | Underground | 389 | 75282 | 38.767 | -121.1548 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0089421 | UG | Sus | 35342137 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1873152 | 0 | EPSS Ckt | Y | 2023 | A
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20230912 | 741 | 20230912 | 1122 | 2216202 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3029 | 457097 | 38.7716 | -120.8148 | No | Clear;32-90 F |  |  | 23-0115321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1873158 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | PLACER | SPAULDING-1101 | 152251101 | JUMPER | OJ'S SS OF CGC 223874660452 | 20230912 | 1200 | 20230912 | 1248 | 2216646 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 96 | 39.3183 | -120.6303 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0115478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873354 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | OCB | ECHO SUMMIT | 20230912 | 1625 | 20230912 | 1720 | 2216878 | 55 | Distribution Circuit | 3rd Party | Other | 297 | 11531 | 0 | 0 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0115678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1873414 | 0 | Non-EPSS | N | 2023 | N/A
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2216 | 20230912 | 1739 | 20230913 | 517 | 2216937 | 698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1934 | 131486 | 39.1999 | -121.1727 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115703 | OH | Sus | 45977394 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1873421 | 0 | EPSS Ckt | Y | 2023 | b+c targets
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51484 | 20230912 | 2234 | 20230913 | 408 | 2217161 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 987 | 57218 | 39.1909 | -120.9998 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0115800 | OH | Sus | 45977566 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1873498 | 0 | EPSS Ckt | Y | 2023 | INST OC & B
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222671556565 | 20230913 | 25 | 20230913 | 57 | 2217218 | 32 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 544 | 39.2159 | -121.0581 | No | Clear;32-90 F |  |  | 23-0115817 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1873504 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 10669 | 20230913 | 731 | 20230913 | 933 | 2217362 | 122 | Distribution Circuit | Animal | Squirrel | 41 | 5002 | 38.7 | -120.8325 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115944 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1873671 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20230913 | 1539 | 20230913 | 1600 | 2218107 | 21 | Distribution Circuit | Company Initiated | Personnel- company | 2103 | 44163 | 39.1995 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0116254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1873770 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 227062 | 20230913 | 1600 | 20230913 | 1656 | 2218171 | 56 | Distribution Circuit | Company Initiated | Personnel- company | 144 | 8064 | 39.1876 | -120.9498 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0116254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1873777 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | JUMPER | OJ 8 POLES N/OF CGC 223279856195 | 20230913 | 1736 | 20230913 | 1924 | 2218208 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 216 | 39.2059 | -120.8405 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0116288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873780 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 10747 | 20230913 | 2245 | 20230914 | 317 | 2218334 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 4624 | 38.6591 | -120.8352 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0116387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873851 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 7319 | 20230914 | 905 | 20230914 | 1647 | 2218641 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15640 | 38.711 | -120.944 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0116548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874022 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | SWITCH | 781566 | 20230914 | 916 | 20230914 | 1121 | 2218703 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2125 | 38.7295 | -121.0777 | No | Clear;32-90 F | Jumper | Bent or Twisted | 23-0116482 | OH | Sus | 31668479 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873992 | 0 | EPSS Ckt | Y | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222633856763 | 20230914 | 1534 | 20230914 | 2345 | 2219025 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 491 | 39.2215 | -121.0715 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0116864 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874106 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20230914 | 1708 | 20230914 | 1912 | 2219102 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 514 | 38428 | 39.0351 | -121.0957 | No | Clear;32-90 F |  |  | 23-0116845 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874097 | 0 | EPSS Ckt | Y | 2023 | A-C
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 875 | 20230914 | 2017 | 20230914 | 2029 | 2219188 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 12 | 39.5634 | -120.6434 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082035 | OH | Sus | 31449604 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1874124 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 881364 | 20230914 | 2151 | 20230915 | 14 | 2219215 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 8437 | 38.8856 | -121.2378 | No | Clear;32-90 F |  |  | 23-0116906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874131 | 0 | EPSS Ckt | Y | 2023 | INST OC- B
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | OCB | 2110/2 | 20230915 | 326 | 20230915 | 342 | 2219272 | 16 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4387 | 55122 | 38.6555 | -121.0602 | No | Clear;32-90 F |  |  | 23-0116940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874160 | 0 | EPSS Ckt | N | 2023 | INST OC
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 51676 | 20230915 | 1356 | 20230915 | 1436 | 2219956 | 40 | Distribution Circuit | 3rd Party | Vehicle | 1034 | 37150 | 38.8519 | -121.1638 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117273 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874397 | 0 | EPSS Ckt | Y | 2023 | C & GRD
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 210168 | 20230915 | 1819 | 20230915 | 1841 | 2220097 | 22 | Distribution Circuit | 3rd Party | Vehicle | 113 | 2486 | 38.8867 | -121.2371 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0117359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1874420 | 0 | EPSS Ckt | Y | 2023 | INST OC GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9533 | 20230916 | 1112 | 20230916 | 1228 | 2220585 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 760 | 38.8679 | -121.4506 | No | Clear;32-90 F |  |  | 23-0117457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874545 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20230916 | 1303 | 20230916 | 1324 | 2220653 | 21 | Distribution Circuit | Company Initiated | Personnel- company | 120 | 2520 | 39.1986 | -121.0343 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874550 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222778557382 | 20230916 | 1432 | 20230917 | 505 | 2220688 | 873 | Distribution Circuit | 3rd Party | Vehicle | 1234 | 228267 | 39.238 | -121.0198 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874557 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 307494 | 20230917 | 734 | 20230917 | 952 | 2220941 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 38088 | 38.934 | -121.1793 | No | Clear;32-90 F |  |  | 23-0117525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874605 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 795556 | 20230917 | 1530 | 20230917 | 1710 | 2221058 | 100 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 47 | 4700 | 39.3127 | -120.9819 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117559 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874640 | 0 | EPSS Ckt | Y | 2023 | A-C
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 5117 | 20230918 | 831 | 20230918 | 2215 | 2221327 | 824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 9892 | 38.8054 | -121.2425 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0117748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874876 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 9937 | 20230918 | 1054 | 20230918 | 1802 | 2221553 | 428 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2430 | 172248 | 38.9749 | -121.0257 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0117755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1874884 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 20675 | 20230918 | 1143 | 20230918 | 1431 | 2221548 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 7056 | 38.6707 | -121.007 | No | Clear;32-90 F | Other | Broken | 23-0117803 | OH | Sus | 31669390 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1874900 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | INTERRUPTER | 390732 | 20230918 | 1405 | 20230918 | 1446 | 2221757 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 943 | 38.8867 | -121.2589 | No | Clear;32-90 F |  |  | 23-0094502 | OH | Sus | 35207558 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1874933 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221729144846 | 20230918 | 1609 | 20230918 | 1833 | 2221854 | 144 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 288 | 38.8967 | -121.3935 | No | Clear;32-90 F |  |  | 23-0117992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874966 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230918 | 1850 | 20230918 | 1940 | 2221967 | 50 | Distribution Circuit | Animal | Bird found | 664 | 33200 | 38.8415 | -121.0158 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0117994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874969 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | SWITCH | 10181 | 20230918 | 2110 | 20230919 | 146 | 2222024 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 30912 | 38.8054 | -120.8181 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1874979 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 881364 | 20230919 | 128 | 20230919 | 316 | 2222057 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 6372 | 38.8856 | -121.2378 | No | Clear;32-90 F |  |  | 23-0118016 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1874996 | 0 | EPSS Ckt | Y | 2023 | B-PHASE INST ONLY
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 222624146188 | 20230919 | 1115 | 20230919 | 1454 | 2222190 | 219 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1752 | 38.931 | -121.0785 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0118180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1875215 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 76088 | 20230919 | 1500 | 20230919 | 1732 | 2222625 | 152 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 406 | 61712 | 38.6737 | -120.76 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875265 | 0 | EPSS Ckt | Y | 2023 | a-b
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222671355435 | 20230919 | 1517 | 20230919 | 2238 | 2222632 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 882 | 39.1851 | -121.0587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1875271 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 4911 | 20230919 | 1631 | 20230919 | 1806 | 2222696 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 9310 | 38.7273 | -121.189 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0118414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875283 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 20675 | 20230919 | 1700 | 20230919 | 1917 | 2222709 | 137 | Distribution Circuit | Vegetation | Tree - grew into line | 42 | 5754 | 38.6707 | -121.007 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875280 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223552240344 | 20230919 | 1730 | 20230920 | 243 | 2222746 | 553 | Transformer only | Vegetation | Tree - fell into line | 1 | 553 | 38.7679 | -120.7549 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0118480 | OH | Sus | 35490040 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1875321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | SWITCH | 394 | 20230920 | 530 | 20230920 | 543 | 2222875 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 98 | 1274 | 38.7184 | -121.1809 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 23-0118414 | OH | Sus | 31669668 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1875336 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20230920 | 724 | 20230920 | 916 | 2222934 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 272 | 30464 | 38.887 | -121.2381 | No | Clear;32-90 F |  |  | 23-0118550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875362 | 0 | EPSS Ckt | Y | 2023 | A +B
SIERRA | PLACER | PENRYN-1103 | 152561103 | TRANSFORMER | 222452843588 | 20230920 | 815 | 20230920 | 1053 | 2223031 | 158 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 158 | 38.8595 | -121.1406 | No | Clear;32-90 F |  |  | 23-0118711 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1875560 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20230920 | 845 | 20230920 | 912 | 2223093 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 570 | 15390 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875459 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 44899 | 20230920 | 1018 | 20230920 | 1046 | 2223277 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 28 | 38.9009 | -120.853 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0118678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875545 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225408142074 | 20230920 | 1433 | 20230920 | 1605 | 2223509 | 92 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 276 | 38.8062 | -120.1031 | No | Clear;32-90 F |  |  | 23-0118932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1875641 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 6837 | 20230920 | 1609 | 20230920 | 1755 | 2223587 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 2992 | 38.9977 | -121.0232 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0118941 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875644 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | TRANSFORMER | T6816 | 20230920 | 2154 | 20230920 | 2220 | 2223743 | 26 | Transformer only | Equipment Failure/Involved | Underground | 12 | 312 | 38.7952 | -121.2683 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0118984 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875663 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20230921 | 1021 | 20230921 | 1208 | 2223968 | 107 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1031 | 109213 | 38.9052 | -120.8374 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0119184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875759 | 0 | EPSS Ckt | Y | 2023 | A + B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230921 | 1546 | 20230921 | 1640 | 2224188 | 54 | Distribution Circuit | Animal | Bird found | 664 | 35856 | 38.8415 | -121.0158 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119405 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875809 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 32515 | 20230921 | 2209 | 20230922 | 140 | 2224350 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 7385 | 39.6227 | -120.526 | No | Clear;32-90 F | Insulator | Broken | 23-0119498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875849 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 2102 | 20230922 | 733 | 20230922 | 1124 | 2224441 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1081 | 69306 | 38.6825 | -120.8522 | No | Clear;32-90 F | Insulator | Broken | 23-0119562 | OH | Sus | 31669836 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875883 | 0 | EPSS Ckt | Y | 2023 | NA
SIERRA | NEVADA | SMARTVILLE-1101 | 153791101 | TRANSFORMER | 222075555710 | 20230922 | 818 | 20230922 | 1125 | 2224513 | 187 | Transformer only | Animal | Bird found | 1 | 187 | 39.194 | -121.2692 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0119763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876069 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222799358102 | 20230922 | 852 | 20230922 | 1115 | 2224574 | 143 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 143 | 39.2579 | -121.0124 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0119612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1875960 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222497548565 | 20230922 | 1149 | 20230922 | 1343 | 2224854 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 228 | 38.9969 | -121.1248 | No | Clear;32-90 F | Transformer | Broken | 23-0119824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876086 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OPEN JUMPERS @ CGC 222464057255 | 20230922 | 1414 | 20230922 | 2140 | 2225004 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2230 | 39.2359 | -121.1307 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0119929 | OH | Sus | 31669872 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | Yes | No | 1876115 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4399 | 20230922 | 1648 | 20230922 | 1802 | 2225029 | 74 | Distribution Circuit | Animal | Bird found | 1167 | 78294 | 39.2322 | -121.1973 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0119944 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876120 | 0 | EPSS Ckt | Y | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20230923 | 659 | 20230923 | 1314 | 2225208 | 375 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 664 | 249000 | 38.8415 | -121.0158 | No | Clear;32-90 F |  |  | 23-0119994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1876154 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 76952 | 20230923 | 1211 | 20230923 | 1335 | 2225451 | 84 | Distribution Circuit | Animal | Bird found | 904 | 55368 | 39.253 | -121.1971 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0120043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876219 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 50172 | 20230924 | 1631 | 20230924 | 2136 | 2225949 | 219 | Distribution Circuit | Animal | Bird found | 341 | 30227 | 38.9458 | -121.1226 | No | Clear;32-90 F | Bushing | Burned/flashed | 23-0120161 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1876327 | 0 | EPSS Ckt | Y | 2023 | B C 50(INST)
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32395 | 20230924 | 1843 | 20230924 | 2014 | 2225973 | 91 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 182 | 38.8061 | -121.0221 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0120168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1876336 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 6929 | 20230924 | 2345 | 20230925 | 549 | 2226023 | 364 | Distribution Circuit | 3rd Party | Vehicle | 10 | 3640 | 39.2954 | -121.0152 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0120188 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876352 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222811059660 | 20230925 | 1008 | 20230925 | 1354 | 2226465 | 226 | Transformer only | 3rd Party | Other | 3 | 678 | 39.3005 | -121.008 | No | Clear;32-90 F | Jumper | Broken | 23-0120384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876592 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-2108 | 153702108 | FUSE | 53205 | 20230925 | 1108 | 20230925 | 1439 | 2226543 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 211 | 38.907 | -121.3092 | No | Clear;32-90 F |  |  | 23-0120511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876652 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222667347895 | 20230925 | 1110 | 20230925 | 1142 | 2226547 | 32 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 96 | 38.9778 | -121.0629 | No | Clear;32-90 F | Insulator | Broken | 23-0120394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876597 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7225 | 20230925 | 1152 | 20230925 | 1345 | 2226581 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4070 | 38.9944 | -121.3972 | No | Clear;32-90 F |  |  | 23-0120490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876642 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | SWITCH | 6163 | 20230925 | 1156 | 20230925 | 1313 | 2226601 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 15477 | 39.03 | -120.9656 | No | Clear;32-90 F | Other | Broken | 23-0120418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876603 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 31601 | 20230925 | 1415 | 20230925 | 1421 | 2226764 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 39.3316 | -120.5727 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0120515 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876656 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20230925 | 1628 | 20230925 | 1848 | 2226882 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 18620 | 38.8063 | -120.925 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0120583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876670 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | RECLOSER | 251946 | 20230925 | 1700 | 20230925 | 1951 | 2226905 | 171 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 992 | 167949 | 38.904 | -121.0666 | No | Partly Cloudy;32-90 F |  |  | 23-0120600 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876675 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20819 | 20230925 | 2053 | 20230926 | 300 | 2227011 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6606 | 38.6174 | -120.7157 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0120630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876690 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 8609 | 20230925 | 2251 | 20230925 | 2352 | 2227027 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 671 | 38.9056 | -121.0625 | No | Clear;32-90 F | Fuse | Arcing | 23-0120678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876723 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20230926 | 757 | 20230926 | 915 | 2227257 | 78 | Distribution Circuit | Animal | Squirrel | 594 | 46332 | 39.0443 | -120.9859 | No | Overcast;32-90 F | Transformer (OH) | Normal | 23-0120768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1876801 | 0 | EPSS Ckt | Y | 2023 | AB INST OC
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20230926 | 846 | 20230926 | 1059 | 2227370 | 133 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 533 | 70889 | 39.214 | -120.8098 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0120785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Multi-Fault | 0 | No | No | No | 1876853 | 0 | EPSS Ckt | Y | 2023 | AC SGF
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 5693 | 20230926 | 1119 | 20230926 | 1310 | 2227592 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1665 | 39.2105 | -120.7872 | No | Overcast-Fog-Rain;32-90 F | Fuse | Broken | 23-0120986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1876981 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223427938981 | 20230926 | 1206 | 20230926 | 1233 | 2227546 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 297 | 38.7306 | -120.7993 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 23-0120989 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1876984 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 85873 | 20230926 | 1227 | 20230926 | 1349 | 2227649 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 328 | 38.8933 | -121.0158 | No | Overcast;32-90 F | Woodpin | Broken | 23-0120965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876970 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222469248650 | 20230926 | 1544 | 20230926 | 1956 | 2227815 | 252 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 756 | 38.9966 | -121.1329 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0121136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877019 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 30439 | 20230926 | 1944 | 20230926 | 2105 | 2228017 | 81 | Distribution Circuit | Animal | Squirrel | 2 | 162 | 38.9274 | -121.1556 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877058 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223236337398 | 20230927 | 114 | 20230927 | 134 | 2228125 | 20 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 20 | 38.6883 | -120.8676 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0121243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877089 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6653 | 20230927 | 834 | 20230927 | 1125 | 2228310 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1197 | 39.322 | -120.4288 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0121344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877186 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 3997 | 20230927 | 904 | 20230927 | 1638 | 2228356 | 454 | Distribution Circuit | Animal | Squirrel | 49 | 4486 | 39.0259 | -121.0663 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0121389 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1877267 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223540636167 | 20230927 | 921 | 20230927 | 1003 | 2228414 | 42 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 84 | 38.6523 | -120.7612 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0121376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877254 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222028149356 | 20230927 | 1054 | 20230927 | 1315 | 2228456 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 282 | 39.0199 | -121.2869 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0121394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877271 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30923 | 20230927 | 1240 | 20230927 | 1410 | 2228615 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 450 | 38.8989 | -120.9485 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0121525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877327 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | CGC 1/E/O CGC 222672554611 | 20230927 | 1557 | 20230927 | 1642 | 2228781 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 135 | 39.1624 | -121.0582 | No | Clear;32-90 F | Bushing | Broken | 23-0121708 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1877358 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | SWITCH | 2129 | 20230927 | 1703 | 20230928 | 353 | 2228871 | 650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 14300 | 39.2612 | -121.1987 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0121670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1877368 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 294550 | 20230927 | 2044 | 20230927 | 2150 | 2228961 | 66 | Distribution Circuit | Vegetation | Tree - fell into line | 1181 | 77946 | 38.6674 | -120.9933 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0121777 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877383 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 34871 | 20230928 | 651 | 20230928 | 748 | 2229108 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 2565 | 38.7844 | -121.2544 | No | Clear;32-90 F |  |  | 23-0121859 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1877434 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJS 1 SS OF CGC#223056240560 | 20230928 | 907 | 20230928 | 1214 | 2229283 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 374 | 38.7752 | -120.9282 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0121927 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877530 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | JUMPER | OJS 1 N/O CGC#222561845200 | 20230928 | 930 | 20230928 | 1343 | 2229265 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2277 | 38.9046 | -121.1011 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0121923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877516 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 223039058235 | 20230928 | 1100 | 20230928 | 1210 | 2229452 | 70 | Transformer only | 3rd Party | Vehicle | 1 | 70 | 39.2615 | -120.9292 | No | Clear;32-90 F | Anchor or Guy | Normal | 23-0122201 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877662 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 100000022476 | 20230928 | 2004 | 20230929 | 644 | 2229858 | 640 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 640 | 38.7617 | -120.7092 | No | Clear;32-90 F |  |  | 23-0122313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1877722 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20230928 | 2056 | 20230929 | 1033 | 2229894 | 817 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2501 | 411075 | 38.7138 | -120.9394 | No | Clear;32-90 F |  |  | 23-0122312 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1877719 | 0 | EPSS Ckt | Y | 2023 | BC INST OC DCD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15249 | 20230929 | 532 | 20230929 | 716 | 2230019 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 624 | 38.9265 | -121.2688 | No | Clear;32-90 F |  |  | 23-0122369 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877758 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 2406 | 20230929 | 737 | 20230929 | 820 | 2230065 | 43 | Distribution Circuit | Animal | Bird found | 880 | 37840 | 38.8518 | -121.1656 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0122387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1877768 | 0 | EPSS Ckt | Y | 2023 | A+C+INST
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 127062 | 20230929 | 1043 | 20230929 | 1145 | 2230320 | 62 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 13780 | 38.9818 | -121.0775 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0122525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877918 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJS @ CGC#223000038075 | 20230929 | 1300 | 20230929 | 1507 | 2230488 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 381 | 38.7073 | -120.95 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0122626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877951 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230929 | 1904 | 20230930 | 833 | 2230699 | 809 | Distribution Circuit | Company Initiated | Personnel- company | 203 | 164227 | 39.2562 | -120.7669 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0122758 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877990 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | OCB | 1107/2 | 20230930 | 821 | 20230930 | 1010 | 2231399 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1718 | 187262 | 39.0444 | -121.091 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0122869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878117 | 0 | EPSS Ckt | Y | 2023 | C GRD TIME
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | RECLOSER | 1070 | 20230930 | 1408 | 20230930 | 1548 | 2231686 | 100 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 24500 | 39.0212 | -121.0599 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0122977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878215 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 33433 | 20230930 | 1739 | 20231001 | 1912 | 2231814 | 1533 | Distribution Circuit | Equipment Failure/Involved | Underground | 42 | 39579 | 38.8091 | -121.2464 | No | Overcast;32-90 F | Conductor- Underground | Burned/flashed | 23-0123034 | UG | Sus | 35492960 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878260 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223471034415 | 20230930 | 1952 | 20231001 | 947 | 2231913 | 835 | Transformer only | Vegetation | Tree - fell into line | 1 | 835 | 38.6058 | -120.7878 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0123041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1878268 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | T930513 | 20230930 | 2138 | 20231001 | 1212 | 2231962 | 874 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 874 | 39.1628 | -121.0017 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0123057 | UG | Sus | 45995740 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878286 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 2371 | 20231001 | 921 | 20231001 | 1939 | 2232111 | 618 | Distribution Circuit | Animal | Squirrel | 18 | 2488 | 38.9384 | -121.3162 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1878336 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 2202 | 20231001 | 1154 | 20231001 | 1539 | 2232165 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 524 | 110250 | 38.9718 | -121.1059 | No | Overcast;32-90 F |  |  | 23-0123100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1878339 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20231001 | 1901 | 20231001 | 2005 | 2232280 | 64 | Distribution Circuit | Equipment Failure/Involved | Substation | 203 | 12992 | 39.2562 | -120.7669 | No | Overcast;32-90 F | Relay | Malfunctioning | 23-0123139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1878373 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2704 | 20231002 | 809 | 20231002 | 836 | 2232513 | 27 | Distribution Circuit | Company Initiated | Operating error | 692 | 18684 | 38.8107 | -121.1649 | No | Clear;32-90 F | Recloser | Normal | 23-0095005 | OH | Sus | 74017840 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878482 | 0 | EPSS Ckt | N | 2023 | Ac
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20231002 | 930 | 20231002 | 1217 | 2232709 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2501 | 210018 | 38.7138 | -120.9394 | No | Clear;32-90 F |  |  | 23-0123271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1878544 | 0 | EPSS Ckt | Y | 2023 | A GRD INST OC
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223604736677 | 20231002 | 950 | 20231002 | 1457 | 2232740 | 307 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 307 | 38.6668 | -120.7377 | No | Clear;32-90 F |  |  | 23-0123473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1878634 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S @ HARD TAP SS CGC 223112541295 | 20231002 | 1448 | 20231003 | 147 | 2233273 | 659 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 3 | 1977 | 38.7959 | -120.9086 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0123550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878678 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT 1102 | 152591102 | JUMPER | OJ 2SPAN SS OF 6841 | 20231002 | 1544 | 20231002 | 1730 | 2233088 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 742 | 39.3101 | -120.3386 | No | Partly Cloudy;32-90 F | Jumper | Deteriorated | 23-0123506 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878645 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20231002 | 1625 | 20231003 | 236 | 2233123 | 611 | Distribution Circuit | 3rd Party | Vehicle | 2081 | 507455 | 38.7606 | -120.5589 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0123522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1878652 | 0 | EPSS Ckt | Y | 2023 | A-B- SGF INST OC DCD
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222705049074 | 20231002 | 2030 | 20231003 | 318 | 2233307 | 408 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 816 | 39.0101 | -121.0492 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0123599 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878720 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | JUMPER | OJS 4 SPANS SS OF CGC 222484548225 | 20231003 | 1137 | 20231003 | 1223 | 2233707 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 46 | 38.9856 | -121.1282 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0123790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878937 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20231003 | 1225 | 20231003 | 1502 | 2233770 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 207 | 32499 | 39.274 | -120.9698 | No | Clear;32-90 F |  |  | 23-0123836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1878950 | 1 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20231003 | 1432 | 20231003 | 2036 | 2233883 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 3687 | 38.8458 | -121.482 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124006 | OH | Sus | 31671288 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1878994 | 1 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | SWITCH | 897 | 20231003 | 2114 | 20231004 | 54 | 2234126 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 22440 | 39.232 | -121.1098 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0123751 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879032 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224048238647 | 20231004 | 1 | 20231004 | 130 | 2234145 | 89 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 267 | 38.7191 | -120.5819 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0124121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879070 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 34869 | 20231004 | 733 | 20231004 | 850 | 2234207 | 77 | Distribution Circuit | Animal | Bird found | 77 | 5929 | 38.7977 | -121.2497 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0124230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1879173 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20231004 | 1114 | 20231004 | 1323 | 2234568 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 11610 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879303 | 0 | EPSS Ckt | Y | 2023 | NA
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 48484 | 20231004 | 1859 | 20231004 | 2136 | 2235015 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 894 | 139258 | 39.2545 | -121.1458 | No | Clear;32-90 F |  |  | 23-0124640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1879393 | 0 | EPSS Ckt | Y | 2023 | A-B-GRD
SIERRA | PLACER | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 334242 | 20231005 | 950 | 20231005 | 1013 | 2235301 | 23 | Distribution Circuit | Animal | Other | 56 | 1288 | 38.849 | -120.8683 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879595 | 0 | EPSS Ckt | Y | 2023 | N/A
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 583518 | 20231005 | 1033 | 20231005 | 1930 | 2235608 | 537 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 37 | 7584 | 39.3256 | -121.1123 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | Yes | No | 1879651 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | JUMPER | HIGH SD JUMPER 2 POLE SS OF FUCO 9289 | 20231005 | 1303 | 20231005 | 1708 | 2235758 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 245 | 39.2341 | -121.0608 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0124931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879663 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223065638343 | 20231005 | 1414 | 20231005 | 1731 | 2235814 | 197 | Transformer only | Vegetation | Tree - fell into line | 2 | 394 | 38.7144 | -120.9274 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0125091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1879713 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20231005 | 1657 | 20231005 | 1902 | 2235960 | 125 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1873 | 79094 | 39.0997 | -121.05 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1879710 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | PLACER | CATLETT-1101 | 153761101 | TRANSFORMER | 221526439405 | 20231005 | 1821 | 20231006 | 54 | 2236006 | 393 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 393 | 38.7475 | -121.4657 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125104 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1879723 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222282042597 | 20231006 | 1043 | 20231006 | 1230 | 2236571 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 214 | 38.8334 | -121.2001 | No | Clear;32-90 F | Secondary | Normal | 23-0125454 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1879986 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-2108 | 153702108 | OTHER | T8730 TWD T8733 | 20231006 | 1550 | 20231006 | 1630 | 2236920 | 40 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 440 | 38.907 | -121.3194 | No | Clear;Above 90 | Transformer (UG) | Leaking | 23-0125564 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880060 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | JUMPER | 2SPANS SS CGC 222872532323 | 20231006 | 1819 | 20231006 | 1938 | 2237014 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 79 | 38.5493 | -120.9981 | No | Clear;32-90 F | Other | Broken | 23-0125625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880072 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | OCB | 2110/2 | 20231006 | 1835 | 20231007 | 340 | 2237030 | 545 | Distribution Circuit | Equipment Failure/Involved | Underground | 4388 | 757595 | 38.6555 | -121.0602 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 23-0125626 | UG | Sus | 46002819 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880073 | 0 | EPSS Ckt | N | 2023 | C -INST - GRD
SIERRA | PLACER | PLACER-1101 | 152461101 | FUSE | 34091 | 20231006 | 1900 | 20231006 | 1919 | 2237071 | 19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 38 | 38.8993 | -121.0773 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125632 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880079 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 2406 | 20231006 | 1907 | 20231006 | 2033 | 2237060 | 86 | Distribution Circuit | Animal | Bird found | 880 | 75680 | 38.8518 | -121.1656 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Three Phase Fault | 0 | No | No | No | 1880077 | 0 | EPSS Ckt | Y | 2023 | A-B-C INST OC
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20231006 | 2033 | 20231006 | 2225 | 2237188 | 112 | Distribution Circuit | Company Initiated | Coordination failure | 199 | 22288 | 38.8543 | -121.1728 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Three Phase Fault | 0 | No | No | No | 1880100 | 0 | EPSS Ckt | Y | 2023 | A-B-C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2392 | 20231007 | 228 | 20231007 | 548 | 2237285 | 200 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 551 | 50374 | 39.1451 | -120.9717 | No | Partly Cloudy;32-90 F |  |  | 23-0125665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1880110 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 790882 | 20231007 | 439 | 20231007 | 729 | 2237296 | 170 | Distribution Circuit | Company Initiated | Personnel- company | 21 | 3570 | 39.1663 | -120.9889 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1880123 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7135 | 20231007 | 1820 | 20231007 | 1916 | 2237866 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 187 | 39.2698 | -121.0303 | No | Clear;32-90 F |  |  | 23-0125784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880252 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20231008 | 658 | 20231008 | 1442 | 2238130 | 464 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 870 | 88959 | 38.8963 | -121.1379 | No | Clear;32-90 F |  |  | 23-0125838 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1880299 | 0 | EPSS Ckt | Y | 2023 | A - C - SGF - DCD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20231008 | 856 | 20231008 | 1143 | 2238178 | 167 | Distribution Circuit | Animal | Bird found | 54 | 7770 | 38.9463 | -121.2467 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125855 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1880322 | 0 | EPSS Ckt | Y | 2023 | B & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJS 2 SS OF CGC#223802036905 | 20231009 | 831 | 20231009 | 1350 | 2238650 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1595 | 38.6728 | -120.6689 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0125947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880464 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 1342 | 20231009 | 925 | 20231009 | 1321 | 2238807 | 236 | Distribution Circuit | 3rd Party | Vehicle | 12 | 2832 | 38.8769 | -121.1348 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0125919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880577 | 0 | EPSS Ckt | N | 2023 | N/A
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ'S 2 E/OF CGC 222728247155 | 20231009 | 959 | 20231009 | 1401 | 2238869 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 484 | 38.9573 | -121.0417 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0125935 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880599 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | BURNED OJ HS OF FUCO 30815 | 20231009 | 1339 | 20231009 | 2002 | 2239112 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1532 | 38.8868 | -120.8302 | No | Clear;32-90 F | Jumper | Burned Open | 23-0126225 | OH | Sus | 46004145 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880686 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20231009 | 1435 | 20231009 | 1641 | 2239159 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1599 | 140152 | 38.8931 | -120.9977 | No | Partly Cloudy;32-90 F |  |  | 23-0126164 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1880668 | 0 | EPSS Ckt | Y | 2023 | INST OC B C
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222671556565 | 20231009 | 1655 | 20231009 | 2344 | 2239240 | 409 | Transformer only | Equipment Failure/Involved | Overhead | 17 | 6953 | 39.2159 | -121.0581 | No | Overcast;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0126261 | OH | Sus | 46003938 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880706 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2084 | 20231009 | 1828 | 20231009 | 1839 | 2239348 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 144 | 1584 | 39.0318 | -120.9741 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0126256 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880704 | 0 | EPSS Ckt | N | 2023 | INST OC & B
SIERRA | PLACER | DEL MAR-2105 | 152582105 | TRANSFORMER | 222114040848 | 20231010 | 947 | 20231010 | 1346 | 2239795 | 239 | Transformer only | Animal | Bird found | 5 | 1195 | 38.786 | -121.2592 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0126483 | OH | Sus | 46008393 | NORTH VALLEY AND SIERRA | OCT | Open Circuit | 0 | No | No | No | 1880953 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 3655 | 20231010 | 1510 | 20231010 | 1639 | 2240027 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 2403 | 39.1723 | -121.0215 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0126662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881013 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | T7561 | 20231010 | 1701 | 20231010 | 1728 | 2240201 | 27 | Transformer only | Equipment Failure/Involved | Underground | 4 | 108 | 38.9355 | -121.249 | No | Overcast;32-90 F | Transformer (UG) | Leaking | 23-0126753 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1881030 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | INTERRUPTER | 435472 | 20231010 | 1844 | 20231011 | 238 | 2240246 | 474 | Distribution Circuit | 3rd Party | Vehicle | 49 | 23226 | 38.8609 | -121.2933 | No | Overcast;32-90 F | Switch (UG) | Broken | 23-0126763 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881037 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7127 | 20231011 | 804 | 20231011 | 1040 | 2240448 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 3432 | 39.2694 | -121.0575 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 23-0126874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881110 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 36739 | 20231011 | 947 | 20231011 | 1111 | 2240637 | 84 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 336 | 38.9356 | -121.2469 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0126915 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881237 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | TRANSFORMER | 222495943908 | 20231011 | 1624 | 20231011 | 1707 | 2241204 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 43 | 38.8688 | -121.1243 | No | Clear;32-90 F |  |  | 23-0127221 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1881391 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 7691 | 20231012 | 844 | 20231012 | 1041 | 2241555 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1170 | 38.9892 | -121.2149 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0127377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881531 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 790882 | 20231012 | 1354 | 20231012 | 1517 | 2241975 | 83 | Distribution Circuit | Company Initiated | Personnel- company | 6 | 498 | 39.1663 | -120.9889 | No | Clear;32-90 F | Recloser | Normal | 23-0127620 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1881684 | 0 | EPSS Ckt | Y | 2023 | NONE
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | OTHER | ECHO SUMMIT | 20231013 | 743 | 20231013 | 1749 | 2242362 | 606 | Distribution Circuit | 3rd Party | Other | 214 | 128311 | 0 | 0 | No | Partly Cloudy;Below 32 F | Conductor- Overhead | Normal | 23-0126828 | OH | Sus | 2033539 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1881803 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20231013 | 1322 | 20231013 | 1646 | 2242764 | 204 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1010 | 157777 | 38.6635 | -120.9306 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0128091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1881981 | 0 | EPSS Ckt | Y | 2023 | A-B
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 2208 | 20231013 | 1734 | 20231014 | 1404 | 2242929 | 1230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 402 | 176053 | 39.1986 | -121.0634 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0128186 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882008 | 0 | EPSS Ckt | Y | 2023 | B & GRD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 788953 | 20231013 | 1832 | 20231013 | 2312 | 2242985 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 57400 | 39.5739 | -120.6212 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0128195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882016 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 339792 | 20231014 | 1309 | 20231014 | 1404 | 2243421 | 55 | Distribution Circuit | Animal | Bird found | 86 | 4730 | 38.9563 | -121.1184 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Broken | 23-0128314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882180 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222566060970 | 20231014 | 1906 | 20231014 | 2018 | 2243537 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 216 | 39.338 | -121.0938 | No | Clear;32-90 F |  |  | 23-0128361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882212 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 164068 | 20231015 | 57 | 20231015 | 854 | 2243613 | 477 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 975 | 192945 | 38.9466 | -121.0478 | No | Clear;32-90 F |  |  | 23-0128380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1882235 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20231015 | 1430 | 20231015 | 1538 | 2243803 | 68 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1959 | 121845 | 39.1911 | -120.9965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1882272 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 227062 | 20231015 | 1430 | 20231015 | 1808 | 2243851 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 37278 | 39.1876 | -120.9498 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882284 | 0 | EPSS Ckt | Y | 2023 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20231015 | 1859 | 20231015 | 2046 | 2243940 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 897 | 78179 | 39.2082 | -121.2033 | No | Clear;32-90 F |  |  | 23-0128457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882294 | 0 | EPSS Ckt | Y | 2023 | C - GRD
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20231016 | 910 | 20231016 | 1017 | 2244288 | 67 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 672 | 45024 | 39.2129 | -121.0129 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0128575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1882450 | 0 | EPSS Ckt | Y | 2023 | A+B
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20231016 | 912 | 20231016 | 1128 | 2244321 | 136 | Distribution Circuit | Animal | Squirrel | 409 | 55624 | 38.7121 | -120.9501 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0128578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882462 | 0 | EPSS Ckt | Y | 2023 | B+GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223291237939 | 20231016 | 1351 | 20231016 | 1431 | 2244571 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 80 | 38.7027 | -120.8479 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0128789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882560 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30735 | 20231016 | 1615 | 20231016 | 1621 | 2244751 | 6 | Distribution Circuit | 3rd Party | Other | 1 | 6 | 38.8878 | -121.0105 | No | Partly Cloudy;32-90 F | Secondary | Normal | 23-0128862 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882574 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 88079 | 20231016 | 1912 | 20231016 | 2003 | 2244852 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 153 | 38.9115 | -121.1635 | No | Clear;32-90 F |  |  | 23-0128896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1882589 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18777 | 20231017 | 1001 | 20231017 | 1122 | 2245242 | 81 | Distribution Circuit | Animal | Squirrel | 19 | 1539 | 38.6419 | -120.9537 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0129124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882851 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2453 | 20231017 | 1402 | 20231017 | 1644 | 2245399 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 324 | 38.8228 | -120.7919 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0129181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882878 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 38097 | 20231017 | 2308 | 20231018 | 226 | 2245753 | 198 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 396 | 39.1837 | -120.9215 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0129378 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882954 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20231018 | 700 | 20231018 | 1049 | 2245818 | 229 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 594 | 108583 | 39.0443 | -120.9859 | No | Clear;32-90 F |  |  | 23-0129416 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1882978 | 0 | EPSS Ckt | Y | 2023 | A C INSTA
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S 1 N/OF CGC 223546040325 | 20231018 | 900 | 20231018 | 1220 | 2245961 | 200 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 4 | 800 | 38.7674 | -120.7571 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0129488 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1883067 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20231019 | 805 | 20231019 | 1006 | 2246676 | 121 | Distribution Circuit | Animal | Bird found | 1042 | 84678 | 38.8154 | -120.8221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0130000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1883302 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | PLACER | PENRYN-1107 | 152561107 | JUMPER | OJS 1 SPAN S/OF CGC 222357741616 | 20231019 | 912 | 20231019 | 1155 | 2246778 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 489 | 38.8055 | -121.1732 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0130178 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1883368 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 21007 | 20231019 | 1404 | 20231019 | 1510 | 2246991 | 66 | Distribution Circuit | Animal | Squirrel | 41 | 2703 | 38.6845 | -121.0118 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0130293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1883412 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20231019 | 1819 | 20231020 | 856 | 2247146 | 877 | Distribution Circuit | 3rd Party | Vehicle | 517 | 194027 | 39.153 | -121.0774 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0130364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1883433 | 0 | EPSS Ckt | Y | 2023 | A C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1449 | 20231021 | 811 | 20231021 | 1602 | 2248062 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 33912 | 38.7543 | -120.7732 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0130864 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1883819 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | TRANSFORMER | 222895936449 | 20231021 | 1115 | 20231021 | 1513 | 2248257 | 238 | Transformer only | Company Initiated | Return Circuit Normal | 3 | 714 | 38.6628 | -120.9864 | No | Clear;32-90 F | Transformer | Broken | 23-0130912 | OH | Sus | 31673663 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1883876 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7013 | 20231021 | 1319 | 20231021 | 1425 | 2248324 | 66 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 60 | 3960 | 39.162 | -121.0389 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0130917 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1883884 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 547420 | 20231021 | 1428 | 20231021 | 1623 | 2248351 | 78 | Distribution Circuit | 3rd Party | Customer Equipment | 379 | 29552 | 38.6361 | -121.0601 | No | Partly Cloudy;32-90 F | Circuit Breaker | Normal | 23-0130923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1883892 | 0 | EPSS Ckt | Y | 2023 | A B C GRD
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | TRANSFORMER | 222604238856 | 20231021 | 1728 | 20231022 | 242 | 2248436 | 554 | Distribution Circuit | Animal | Bird found | 3 | 1298 | 38.7301 | -121.0884 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0130953 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1883914 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224577060295 | 20231022 | 1411 | 20231022 | 1817 | 2248979 | 246 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 2 | 492 | 39.3111 | -120.3835 | No | Clear;32-90 F | Service conductor | Broken | 23-0131069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884038 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | RECLOSER | 1402 | 20231022 | 1534 | 20231022 | 1644 | 2249042 | 70 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 945 | 66150 | 38.7201 | -120.861 | No | Overcast;32-90 F |  |  | 23-0131059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884026 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 19752 | 20231022 | 1858 | 20231022 | 1916 | 2249214 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1092 | 19656 | 38.7148 | -120.5815 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0131082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884049 | 0 | EPSS Ckt | Y | 2023 | C GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20231022 | 2253 | 20231023 | 2031 | 2249361 | 777 | Distribution Circuit | Equipment Failure/Involved | Overhead | 409 | 154125 | 38.7121 | -120.9501 | No | Overcast-Fog;32-90 F | Pothead(Riser Termination) | Broken | 23-0131121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884080 | 0 | EPSS Ckt | Y | 2023 | GRD & INST OC
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223978538460 | 20231022 | 2300 | 20231023 | 957 | 2249339 | 657 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 657 | 38.7154 | -120.606 | No | Rain-Overcast-Fog;32-90 F | Transformer | Burned/flashed | 23-0131123 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884081 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222666552164 | 20231023 | 543 | 20231023 | 1104 | 2249491 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 321 | 39.0948 | -121.0617 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 23-0131202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884187 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 4741 | 20231023 | 736 | 20231023 | 1403 | 2249446 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4257 | 38.7615 | -120.5345 | No | Clear;32-90 F | Insulator | Arcing | 23-0131170 | OH | Sus | 46028491 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1884130 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 481660 | 20231023 | 1346 | 20231023 | 1502 | s1884965 | 76 | Distribution Circuit | 3rd Party | Other | 39 | 2964 | 38.8107 | -120.0318 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0130863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1884965 | 0 | EPSS Ckt | N | 2023 | NA
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 20231023 | 2046 | 20231023 | 2230 | 2250224 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 520 | 38.5951 | -120.8115 | No | Clear;32-90 F |  |  | 23-0131602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1884411 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1101 | 152461101 | TRANSFORMER | 222630645046 | 20231024 | 816 | 20231024 | 1416 | 2250423 | 360 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1440 | 38.8998 | -121.0767 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0131747 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884609 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 2728 | 20231024 | 928 | 20231024 | 1223 | 2250607 | 175 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2254 | 207896 | 39.2362 | -121.2206 | No | Clear;32-90 F |  |  | 23-0131727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1884600 | 0 | EPSS Ckt | Y | 2023 | A-C INST OC
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | JUMPER | 32295 HIGH SIDE JUMPERS | 20231024 | 1202 | 20231024 | 1330 | 2250719 | 88 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 176 | 39.2248 | -121.0918 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0131812 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1884641 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 6873 | 20231024 | 1323 | 20231024 | 1425 | 2250815 | 62 | Distribution Circuit | Animal | Bird found | 24 | 1488 | 39.0673 | -121.0342 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0131938 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1884673 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223087339237 | 20231024 | 1703 | 20231024 | 2356 | 2250933 | 413 | Transformer only | Environmental/External | Lightning | 1 | 413 | 38.7393 | -120.9182 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0132047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884697 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20231025 | 1318 | 20231025 | 1401 | 2251677 | 43 | Distribution Circuit | Company Initiated | Personnel- company | 2013 | 68928 | 39.1995 | -121.017 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0132433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884998 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | PLACER | SUMMIT-1102 | 152591102 | OCB | 1102/2 | 20231025 | 1335 | 20231025 | 1712 | 2251701 | 217 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 208 | 45136 | 39.3193 | -120.3785 | No | Overcast;32-90 F |  |  | 23-0132443 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Three Phase Fault | 0 | No | No | No | 1885002 | 0 | EPSS Ckt | Y | 2023 | A-B-C INST
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 20231025 | 1421 | 20231025 | 1849 | 2251735 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 7155 | 39.1757 | -120.9295 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0132553 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885023 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20231025 | 2146 | 20231026 | 733 | 2251958 | 587 | Distribution Circuit | 3rd Party | Vehicle | 1084 | 106721 | 38.8101 | -121.1629 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0132623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | Yes | No | 1885049 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | T433070 | 20231026 | 904 | 20231026 | 919 | 2252124 | 15 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 15 | 38.9702 | -121.2596 | No | Overcast-Fog;32-90 F |  |  | 23-0132767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1885247 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 100000059896 | 20231026 | 1039 | 20231026 | 2218 | 2252456 | 699 | Transformer only | 3rd Party | Vehicle | 1 | 699 | 38.8553 | -120.8418 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0132918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885355 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222624156485 | 20231026 | 1240 | 20231026 | 1505 | 2252536 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 1450 | 39.214 | -121.075 | No | Clear;32-90 F | Secondary | Broken | 23-0132889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885340 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1102 | 153701102 | OTHER | NORTH PHASE WIRE DOWN | 20231026 | 2022 | 20231026 | 2328 | 2252866 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 712 | 132388 | 38.8822 | -121.3027 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0133023 | OH | Sus | 46032475 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | Yes | 1885411 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 2202 | 20231027 | 854 | 20231027 | 1120 | 2253110 | 146 | Distribution Circuit | Animal | Bird found | 524 | 55682 | 38.9718 | -121.1059 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0133136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885539 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 58420 | 20231027 | 1002 | 20231027 | 1418 | 2253245 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 716 | 168456 | 38.8988 | -120.9106 | No | Clear;32-90 F |  |  | 23-0133185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885613 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 495781 | 20231027 | 1431 | 20231027 | 1437 | 2253490 | 6 | Distribution Circuit | 3rd Party | Other | 1 | 6 | 38.6989 | -121.0203 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885688 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222634352998 | 20231027 | 1927 | 20231028 | 50 | 2253683 | 323 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 323 | 39.1182 | -121.0723 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133438 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885720 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJ 1 SPAN SS OF CGC 223816439624 | 20231028 | 756 | 20231028 | 1145 | 2253981 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | 38.7464 | -120.6635 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0133481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885762 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 357568 | 20231028 | 818 | 20231028 | 905 | 2254034 | 47 | Distribution Circuit | Animal | Squirrel | 1280 | 57094 | 39.2214 | -121.067 | No | Clear;32-90 F | Fuse | Normal | 23-0133489 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885791 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222907755137 | 20231028 | 1257 | 20231028 | 1655 | 2254228 | 238 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 238 | 39.1761 | -120.9764 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0133558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885865 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 5097 | 20231028 | 1916 | 20231028 | 2033 | 2254466 | 77 | Distribution Circuit | Animal | Other | 61 | 4697 | 38.781 | -121.1735 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885897 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20231028 | 2157 | 20231029 | 1354 | 2254517 | 957 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 80388 | 39.4883 | -120.8571 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Deteriorated | 23-0133634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885918 | 0 | EPSS Ckt | Y | 2023 | AC
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2234 | 20231028 | 2228 | 20231029 | 842 | 2254524 | 614 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 268 | 69612 | 38.8956 | -121.1358 | No | Clear;32-90 F |  |  | 23-0133640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885923 | 0 | EPSS Ckt | Y | 2023 | BC
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20231029 | 840 | 20231029 | 1234 | 2254710 | 234 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 519 | 95966 | 39.153 | -121.0774 | No | Clear;32-90 F |  |  | 23-0133668 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885954 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 7351 | 20231029 | 903 | 20231029 | 938 | 2254721 | 35 | Distribution Circuit | Animal | Squirrel | 63 | 2205 | 38.9451 | -121.1196 | No | Clear;32-90 F | Fuse | Burned Open | 23-0133672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885966 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 273542 | 20231029 | 1034 | 20231029 | 1420 | 2254799 | 226 | Distribution Circuit | Animal | Squirrel | 19 | 3124 | 38.7126 | -120.9522 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0133679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885973 | 0 | EPSS Ckt | Y | 2023 | INST & C
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222206745775 | 20231029 | 1258 | 20231029 | 1536 | 2254923 | 158 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 316 | 38.9208 | -121.2256 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133711 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885997 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20231029 | 1906 | 20231029 | 2228 | 2255114 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 922 | 186244 | 38.9928 | -120.8828 | No | Clear;32-90 F |  |  | 23-0133740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886033 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20231029 | 2349 | 20231030 | 321 | 2255180 | 212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1666 | 235640 | 39.0162 | -120.8351 | No | Clear;32-90 F |  |  | 23-0133763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886049 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20231030 | 335 | 20231030 | 1108 | 2255198 | 453 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1666 | 753210 | 39.0162 | -120.8351 | No | Clear;32-90 F |  |  | 23-0133774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886055 | 0 | EPSS Ckt | Y | 2023 | SGF/ DCD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20231030 | 904 | 20231030 | 1135 | 2255390 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 649 | 97999 | 39.0757 | -121.1143 | No | Clear;32-90 F |  |  | 23-0133842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1886157 | 0 | EPSS Ckt | Y | 2023 | INST A B
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222691561680 | 20231030 | 1049 | 20231030 | 1209 | 2255365 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 160 | 39.3566 | -121.0481 | No | Clear;32-90 F |  |  | 23-0133980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1886250 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 19712 | 20231030 | 1123 | 20231030 | 1240 | 2255680 | 77 | Distribution Circuit | Animal | Squirrel | 481 | 37037 | 38.7219 | -120.7904 | No | Clear;32-90 F | Fuse | Normal | 23-0133957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886243 | 0 | EPSS Ckt | Y | 2023 | C
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20231030 | 1202 | 20231030 | 1542 | 2255722 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 922 | 164920 | 38.9928 | -120.8828 | No | Clear;32-90 F |  |  | 23-0133774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886254 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223547236844 | 20231030 | 1532 | 20231031 | 205 | 2256005 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1425 | 38.6718 | -120.7587 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0134145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886328 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 41199 | 20231031 | 933 | 20231031 | 1145 | 2256501 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 924 | 38.6937 | -120.8186 | No | Partly Cloudy;32-90 F |  |  | 23-0134297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886575 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 501650 | 20231031 | 1115 | 20231031 | 1227 | 2256633 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 1721 | 38.692 | -120.7038 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 23-0134306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1886586 | 1 | EPSS Ckt | Y | 2023 | NONE
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20231031 | 1627 | 20231031 | 1711 | 2256881 | 44 | Distribution Circuit | Company Initiated | Coordination failure | 798 | 35112 | 38.8695 | -121.02 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0134419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1886648 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20231101 | 348 | 20231101 | 557 | 2257016 | 129 | Distribution Circuit | Animal | Squirrel | 528 | 68112 | 39.2191 | -121.0228 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0134490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1886690 | 0 | EPSS Ckt | Y | 2023 | C/GRD
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 4525 | 20231101 | 355 | 20231101 | 536 | 2257019 | 101 | Distribution Circuit | Animal | Squirrel | 642 | 54650 | 39.0356 | -120.9922 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0134491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1886692 | 0 | EPSS Ckt | Y | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20231101 | 909 | 20231101 | 1039 | 2257224 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 219 | 19710 | 38.8964 | -121.1202 | No | Clear;32-90 F |  |  | 23-0134581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1886828 | 0 | EPSS Ckt | Y | 2023 | B C
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9031 | 20231101 | 1602 | 20231101 | 1609 | 2257757 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 189 | 39.2198 | -121.0125 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0134490 | OH | Sus | 31674453 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1886961 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 417766 | 20231101 | 2218 | 20231102 | 1 | 2257883 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3502 | 39.1992 | -121.187 | No | Clear;32-90 F |  |  | 23-0134945 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1886996 | 0 | EPSS Ckt | Y | 2023 | SGF / DCD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 62737 | 20231101 | 2335 | 20231102 | 816 | 2257892 | 521 | Distribution Circuit | 3rd Party | Vehicle | 250 | 76284 | 38.7514 | -120.7776 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0134964 | OH | Sus | 31675063 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887010 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20231102 | 240 | 20231102 | 559 | 2257937 | 199 | Distribution Circuit | Equipment Failure/Involved | Underground | 1666 | 116362 | 39.0162 | -120.8351 | No | Partly Cloudy;32-90 F | Elbow | Broken | 23-0134965 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887009 | 0 | EPSS Ckt | Y | 2023 | SGF
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 1818 | 20231102 | 1038 | 20231102 | 1421 | 2258333 | 223 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 5718 | 38.9853 | -120.8976 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0134969 | UG | Sus | 46045468 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887222 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21633 | 20231102 | 1258 | 20231102 | 1441 | 2258441 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1339 | 38.6744 | -120.8855 | No | Clear;32-90 F |  |  | 23-0135317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887276 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 875BP | 20231102 | 1828 | 20231102 | 1846 | 2258659 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 35 | 630 | 39.5634 | -120.6434 | No | Overcast;32-90 F | Other | Normal | 23-0056420 | OH | Sus | 31571830 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1887293 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 417766 | 20231103 | 636 | 20231103 | 702 | 2258777 | 26 | Distribution Circuit | Company Initiated | Coordination failure | 34 | 884 | 39.1992 | -121.187 | No | Clear;32-90 F | Recloser | Normal | 23-0135444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887346 | 0 | EPSS Ckt | Y | 2023 | SGF - DCD
SIERRA | PLACER | BELL-1107 | 152701107 | JUMPER | OJ ON TAP TWD CGC 222426246577 | 20231103 | 757 | 20231103 | 1005 | 2258811 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 128 | 38.9414 | -121.1482 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0135468 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887362 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | RECLOSER | 2222 | 20231103 | 1124 | 20231103 | 1141 | 2259143 | 17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 326 | 5542 | 38.7708 | -121.2524 | No | Clear;32-90 F | Insulator | Broken | 23-0135616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887556 | 0 | Non-EPSS | N | 2023 | NONE
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 85766 | 20231103 | 1132 | 20231103 | 1151 | 2259157 | 19 | Distribution Circuit | Company Initiated | Personnel- company | 260 | 4940 | 38.8027 | -120.9071 | No | Clear;32-90 F | Recloser | Normal | 23-0135626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1887564 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 215628 | 20231103 | 1216 | 20231103 | 1310 | 2259200 | 54 | Distribution Circuit | Company Initiated | Personnel- company | 149 | 8046 | 39.3088 | -120.9087 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135648 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887580 | 0 | EPSS Ckt | Y | 2023 | perm fault
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | OCB | 1107/2 | 20231103 | 1534 | 20231103 | 1719 | 2259378 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1848 | 142800 | 38.6933 | -120.826 | No | Clear;32-90 F |  |  | 23-0135733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887616 | 0 | EPSS Ckt | Y | 2023 | INST OC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20231103 | 1615 | 20231103 | 1932 | 2259413 | 197 | Distribution Circuit | 3rd Party | Other | 2740 | 327131 | 38.6943 | -120.6784 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135753 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887620 | 0 | EPSS Ckt | Y | 2023 | SGF DCD B-C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 8875 | 20231103 | 1740 | 20231104 | 1124 | 2259468 | 1064 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 2128 | 39.2123 | -121.2338 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 23-0135782 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887631 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20231103 | 1956 | 20231104 | 251 | 2259560 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 897 | 80543 | 39.2082 | -121.2033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0135803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1887642 | 0 | EPSS Ckt | Y | 2023 | AGRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20231104 | 1148 | 20231104 | 1314 | 2259963 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1720 | 38.8769 | -121.017 | No | Clear;32-90 F |  |  | 23-0135904 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887786 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | RECLOSER | 556218 | 20231104 | 1244 | 20231104 | 1714 | 2259998 | 270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 647 | 174690 | 38.6342 | -120.9454 | No | Clear;32-90 F |  |  | 23-0135901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887783 | 0 | EPSS Ckt | Y | 2023 | B-C INST
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 1342 | 20231104 | 1351 | 20231104 | 1443 | 2260026 | 52 | Distribution Circuit | Company Initiated | Personnel- company | 612 | 31824 | 38.8769 | -121.1348 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887790 | 0 | EPSS Ckt | Y | 2023 | NONE
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 215628 | 20231104 | 1527 | 20231104 | 1607 | 2260063 | 40 | Distribution Circuit | Company Initiated | Personnel- company | 153 | 6120 | 39.3088 | -120.9087 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887798 | 0 | EPSS Ckt | Y | 2023 | b lockout
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20231104 | 1601 | 20231104 | 2338 | 2260108 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 449 | 192046 | 39.0473 | -121.0486 | No | Partly Cloudy;32-90 F | Regulator | Failed/Faulted | 23-0135928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887804 | 0 | EPSS Ckt | Y | 2023 | A GRD
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20231104 | 1806 | 20231104 | 1951 | 2260218 | 105 | Distribution Circuit | Animal | Bird found | 1560 | 144648 | 38.8328 | -120.8176 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0135938 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1887811 | 0 | EPSS Ckt | Y | 2023 | a-b
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222609253197 | 20231105 | 924 | 20231105 | 1350 | 2260423 | 266 | Transformer only | Animal | Squirrel | 2 | 532 | 39.124 | -121.0813 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887898 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | SMARTVILLE-1101 | 153791101 | JUMPER | OJ 2 SPAN SS CGC 222072456770 | 20231105 | 1059 | 20231105 | 1300 | 2260455 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 847 | 39.2232 | -121.2708 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0136002 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1887903 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2416 | 20231105 | 1436 | 20231105 | 1916 | 2260558 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1494 | 119571 | 39.1593 | -121.0399 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0136013 | OH | Sus | 31675402 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887912 | 0 | EPSS Ckt | Y | 2023 | C+GRD
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 593454 | 20231105 | 2133 | 20231106 | 148 | 2260717 | 255 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 376 | 95880 | 38.6058 | -121.0236 | No | Overcast;32-90 F |  |  | 23-0136060 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887951 | 0 | EPSS Ckt | Y | 2023 | a+grd
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 9722 | 20231106 | 1 | 20231106 | 1114 | 2260832 | 582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3557 | 669009 | 38.6412 | -120.6587 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0136081 | OH | Sus | 31675406 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1887962 | 0 | EPSS Ckt | Y | 2023 | SGF+DCD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20231106 | 125 | 20231106 | 301 | 2260959 | 96 | Distribution Circuit | Company Initiated | Coordination failure | 1019 | 80219 | 38.7759 | -120.4031 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0136097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887975 | 0 | EPSS Ckt | Y | 2023 | A+GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20231106 | 459 | 20231106 | 525 | 2261001 | 26 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1295 | 33670 | 38.7617 | -120.5592 | No | Overcast-Fog;32-90 F |  |  | 23-0136105 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887984 | 0 | EPSS Ckt | Y | 2023 | sgf+dcd
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7729 | 20231106 | 613 | 20231106 | 816 | 2261030 | 123 | Distribution Circuit | Animal | Bird found | 15 | 1845 | 38.9951 | -121.3166 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0136123 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1888009 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2569 | 20231106 | 646 | 20231106 | 1540 | 2261056 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 55907 | 38.8008 | -120.141 | No | Overcast-Fog-Drizzle;32-90 F | Lightning Arrestor | Broken | 23-0136201 | OH | Sus | 31675437 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888155 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | OTHER | WIRE DOWN 1 W/OF CGC 221645544867 | 20231106 | 1059 | 20231106 | 1509 | 2261509 | 250 | Distribution Circuit | Animal | Bird found | 192 | 42260 | 38.897 | -121.4234 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0136249 | OH | Sus | 31675388 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | Yes | Yes | 1888180 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20231106 | 1715 | 20231106 | 1746 | 2261959 | 31 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2740 | 72984 | 38.6943 | -120.6784 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 23-0136451 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Multi-Fault | 0 | No | No | No | 1888264 | 0 | EPSS Ckt | Y | 2023 | b-c sgf- dcd
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1449 | 20231107 | 933 | 20231107 | 1314 | 2262406 | 221 | Distribution Circuit | 3rd Party | Vehicle | 72 | 15912 | 38.7543 | -120.7732 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0136613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1888428 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222817055956 | 20231107 | 1133 | 20231107 | 2034 | 2262867 | 541 | Transformer only | 3rd Party | Other | 1 | 541 | 39.1989 | -121.007 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888604 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20231107 | 1404 | 20231108 | 923 | 2262990 | 1159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 901 | 358108 | 38.9732 | -121.0141 | No | Partly Cloudy;32-90 F |  |  | 23-0136800 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888619 | 0 | EPSS Ckt | Y | 2023 | sgf dcd
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 2489 | 20231108 | 700 | 20231108 | 1500 | s1888936 | 445 | Distribution Circuit | Equipment Failure/Involved | Underground | 221 | 26715 | 38.8229 | -121.2558 | No | Clear;32-90 F | Bushing | Broken | 23-0137113 | UG | Sus | 46050920 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888936 | 1 | EPSS Ckt | Y | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32621 | 20231108 | 840 | 20231108 | 1046 | 2263731 | 126 | Distribution Circuit | Animal | Squirrel | 1982 | 135579 | 39.2311 | -121.0586 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0136994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888856 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | JUMPER | OJ'S @ CGC 22238646795 | 20231108 | 1005 | 20231108 | 1223 | 2263760 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 276 | 38.9486 | -121.2142 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0137011 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1888875 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 2426 | 20231108 | 1509 | 20231108 | 1627 | 2264426 | 78 | Distribution Circuit | Animal | Bird found | 1846 | 112697 | 39.2042 | -121.2005 | No | Clear;32-90 F | Capacitor | Normal | 23-0137222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1888992 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20231108 | 1714 | 20231108 | 2148 | 2264541 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 215913 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 23-0137255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1889002 | 0 | EPSS Ckt | Y | 2023 | B-C
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7559 | 20231108 | 1740 | 20231109 | 133 | 2264583 | 473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1892 | 38.8023 | -121.4251 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0137263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1889006 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | OTHER | WIRE DOWN AT 33251 ON MAIN LINE | 20231109 | 744 | 20231109 | 2006 | 2264802 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1250 | 749160 | 39.1498 | -120.9028 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0137367 | OH | Sus | 46053749 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | Yes | Yes | 1889087 | 1 | EPSS Ckt | Y | 2023
SIERRA | PLACER | DEL MAR-2110 | 152582110 | OTHER | J199 TWD J275 | 20231109 | 1458 | 20231109 | 1511 | 2265319 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 159 | 2067 | 38.8187 | -121.2555 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0137113 | UG | Sus | 46050920 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1889321 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 2489 | 20231109 | 1525 | 20231109 | 1534 | 2265339 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 62 | 558 | 38.8229 | -121.2558 | No | Partly Cloudy;32-90 F | Conductor- Underground | Normal | 23-0137113 | UG | Sus | 46050920 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1889324 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 30003 | 20231109 | 1712 | 20231109 | 1853 | 2265442 | 101 | Distribution Circuit | 3rd Party | Customer Equipment | 8 | 808 | 39.2235 | -121.0489 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0137642 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1889338 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SUMMIT-1101 | 152591101 | RECLOSER | 742 | 20231110 | 525 | 20231110 | 2201 | 2265832 | 674 | Distribution Circuit | Equipment Failure/Involved | Underground | 152 | 43374 | 39.3236 | -120.3792 | No | Overcast;Below 32 F | Connector or Splice (UG) | Burned/flashed | 23-0137710 | UG | Sus | 46055755 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1889409 | 0 | EPSS Ckt | Y | 2023 | INST B GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20231110 | 631 | 20231110 | 1232 | 2265862 | 361 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1220 | 383140 | 38.6406 | -120.7047 | No | Partly Cloudy;32-90 F |  |  | 23-0137717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1889417 | 0 | EPSS Ckt | Y | 2023 | A B
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | 3 SS/OF CGC 223575336273 | 20231110 | 934 | 20231110 | 1306 | 2266094 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 212 | 38.6574 | -120.749 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0137798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889533 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2740 | 20231110 | 1444 | 20231110 | 1654 | 2266360 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 450 | 49890 | 39.0342 | -120.9744 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0137961 | OH | Sus | 46055806 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1889627 | 0 | EPSS Ckt | Y | 2023 | A GRD INST OC
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OCB | 1104/2 | 20231111 | 948 | 20231111 | 1042 | 2266715 | 54 | Distribution Circuit | Animal | Squirrel | 2564 | 123896 | 39.2314 | -121.0346 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0138072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1889739 | 0 | EPSS Ckt | Y | 2023 | INST OC GRD
SIERRA | PLACER | SUMMIT-1102 | 152591102 | FUSE | 6845 | 20231111 | 1127 | 20231111 | 1227 | 2266760 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 300 | 39.3035 | -120.3349 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 23-0138091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889751 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 36764 | 20231111 | 1130 | 20231111 | 1141 | 2266773 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 593 | 6523 | 38.787 | -120.206 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0138094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889755 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 992864 | 20231111 | 1142 | 20231111 | 1628 | 2266774 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 709 | 19417 | 38.8042 | -120.1031 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0138094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889756 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2228 | 20231111 | 1300 | 20231111 | 1432 | 2266793 | 92 | Distribution Circuit | Animal | Squirrel | 263 | 24196 | 39.2009 | -121.209 | No | Clear;32-90 F | Fuse | Burned Open | 23-0138099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1889759 | 0 | EPSS Ckt | Y | 2023 | B GRD
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | FUSE | 18887 | 20231111 | 1340 | 20231111 | 1754 | 2266806 | 254 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 2474 | 38.5556 | -120.9916 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0138107 | OH | Sus | 46055984 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889764 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | JUMPER | OJ 4 SPAN W/OF 1219 | 20231111 | 1530 | 20231111 | 1754 | 2266837 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2592 | 39.321 | -120.6263 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0138108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889776 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 6161 | 20231112 | 1440 | 20231112 | 1715 | 2267254 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 638 | 7306 | 38.7769 | -120.2659 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0138208 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889888 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 13139 | 20231112 | 2120 | 20231113 | 238 | 2267371 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 678 | 29256 | 38.7749 | -120.2823 | No | Partly Cloudy;32-90 F | Switch (OH) | Broken | 23-0138208 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889940 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | SWITCH | 19931 | 20231113 | 752 | 20231113 | 834 | 2267473 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 84 | 38.6282 | -120.9849 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0138295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889971 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 39337 | 20231113 | 755 | 20231113 | 915 | 2267479 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 1760 | 38.8528 | -121.1541 | No | Clear;32-90 F |  |  | 23-0138346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890078 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 542186 | 20231113 | 1151 | 20231113 | 1249 | 2267857 | 58 | Distribution Circuit | Company Initiated | Personnel- company | 92 | 5336 | 39.2144 | -120.8088 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0138434 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890169 | 0 | EPSS Ckt | Y | 2023 | A & C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 215628 | 20231113 | 1246 | 20231113 | 1313 | 2267919 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 130 | 3510 | 39.3088 | -120.9087 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0138458 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890183 | 0 | EPSS Ckt | Y | 2023 | A & B
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRIP-SAVER | 8233 | 20231113 | 1509 | 20231113 | 1643 | 2268044 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 4538 | 39.3422 | -121.0615 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Multi-Fault | 0 | No | No | No | 1890219 | 0 | EPSS Ckt | N | 2023 | AB
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 4095 | 20231113 | 1705 | 20231113 | 2056 | 2268123 | 231 | Distribution Circuit | Equipment Failure/Involved | Underground | 44 | 4094 | 38.7517 | -121.348 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0138547 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1890226 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222888145420 | 20231113 | 1916 | 20231114 | 216 | 2268346 | 420 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1260 | 38.9092 | -120.986 | No | Clear;32-90 F | Transformer (OH) | Arcing | 23-0138589 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1890246 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20231113 | 2138 | 20231114 | 2 | 2268499 | 144 | Distribution Circuit | Animal | Bird found | 582 | 53057 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0138623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890275 | 0 | EPSS Ckt | Y | 2023 | AB
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20231114 | 802 | 20231114 | 826 | 2268622 | 24 | Distribution Circuit | Company Initiated | Personnel- company | 1954 | 46896 | 39.1995 | -121.017 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138706 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1890308 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | JUMPER | OJ @ CGC 223227036480 | 20231114 | 912 | 20231114 | 1207 | 2268822 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 525 | 38.6626 | -120.8701 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0138748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1890416 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 215628 | 20231114 | 933 | 20231114 | 953 | 2268873 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 155 | 3100 | 39.3088 | -120.9087 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890441 | 0 | EPSS Ckt | N | 2023 | A / B
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20231114 | 1002 | 20231114 | 1203 | 2268962 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1153 | 55153 | 38.6779 | -120.8495 | No | Clear;32-90 F |  |  | 23-0138781 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1890461 | 0 | EPSS Ckt | Y | 2023 | INST OC - A - GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | JUMPER | 8971 HIGH SIDE JUMPERS | 20231114 | 2010 | 20231114 | 2246 | 2269317 | 156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1248 | 39.1726 | -121.0835 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0139060 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1890550 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222772557385 | 20231115 | 1105 | 20231115 | 1304 | 2269789 | 119 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 357 | 39.2381 | -121.0219 | No | Overcast;32-90 F |  |  | 23-0139374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1890820 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 18445 | 20231115 | 1410 | 20231115 | 1446 | 2270020 | 36 | Distribution Circuit | Animal | Squirrel | 1 | 36 | 38.6662 | -120.9244 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0139479 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1890850 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1431 | 20231115 | 2005 | 20231115 | 2319 | 2270443 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 3104 | 38.7464 | -120.7505 | No | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 23-0139652 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1890919 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20231116 | 640 | 20231116 | 708 | 2270593 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3053 | 76526 | 38.7716 | -120.8148 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 23-0139750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | No | No | 1890976 | 0 | EPSS Ckt | Y | 2023 | INST - A - B - C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9581 | 20231116 | 651 | 20231116 | 837 | 2270622 | 106 | Distribution Circuit | Animal | Bird found | 16 | 1696 | 38.8968 | -120.9676 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0139795 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891003 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223325344657 | 20231116 | 719 | 20231116 | 927 | 2270634 | 128 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 128 | 38.8867 | -120.8332 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0139836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891038 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6407 | 20231116 | 1043 | 20231116 | 1056 | 2270805 | 13 | Distribution Circuit | Company Initiated | Other Circuits | 132 | 1716 | 39.2088 | -120.8165 | No | Overcast-Drizzle;32-90 F | Other | Normal | 23-0139890 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891053 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6377 | 20231116 | 1154 | 20231116 | 1221 | 2270837 | 27 | Distribution Circuit | Company Initiated | Other Circuits | 114 | 3078 | 39.2023 | -120.8368 | No | Overcast-Drizzle;32-90 F | Other | Normal | 23-0139933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891060 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 4437 | 20231116 | 1154 | 20231116 | 1303 | 2270894 | 69 | Distribution Circuit | Company Initiated | Other Circuits | 1 | 69 | 39.2062 | -120.8381 | No | Partly Cloudy-Drizzle;32-90 F | Other | Normal | 23-0139974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891077 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 9593 | 20231116 | 1330 | 20231116 | 1339 | 2270922 | 9 | Distribution Circuit | Company Initiated | Other Circuits | 59 | 531 | 39.2173 | -120.8092 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0140018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891088 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222286945757 | 20231116 | 1641 | 20231117 | 10 | 2270995 | 449 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 898 | 38.9202 | -121.1972 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140177 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891111 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223740245740 | 20231116 | 1836 | 20231117 | 238 | 2271070 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1928 | 38.9151 | -120.6864 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140221 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891142 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | RECLOSER | 13312 | 20231116 | 2158 | 20231117 | 909 | 2271153 | 671 | Distribution Circuit | 3rd Party | Vehicle | 273 | 34487 | 38.7435 | -120.7341 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0140225 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | Yes | No | 1891145 | 0 | EPSS Ckt | N | 2023 | ABC
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | OTHER | T8556 TWD T8565 | 20231117 | 1021 | 20231117 | 1140 | 2271510 | 79 | Distribution Circuit | Equipment Failure/Involved | Underground | 59 | 4661 | 38.8634 | -121.3177 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0140295 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891328 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15345 | 20231117 | 1129 | 20231117 | 1354 | 2271556 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 870 | 38.9262 | -121.3953 | No | Partly Cloudy;32-90 F |  |  | 23-0140519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891366 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20231118 | 723 | 20231118 | 835 | 2272069 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 360 | 38.8986 | -120.8986 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0140797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891513 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223009955266 | 20231118 | 1035 | 20231118 | 1456 | 2272418 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 522 | 39.1796 | -120.941 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891564 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 9735 | 20231118 | 1146 | 20231118 | 1627 | 2272504 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7587 | 39.137 | -121.1004 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0140862 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891565 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 33331 | 20231118 | 1211 | 20231118 | 1332 | 2272559 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 1296 | 38.7432 | -121.1662 | No | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0140880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891578 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222330745307 | 20231118 | 1227 | 20231118 | 1258 | 2272485 | 31 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 62 | 38.9078 | -121.1822 | No | Overcast-Drizzle;32-90 F |  |  | 23-0140886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1891583 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | OTHER | WIRE DOWN AT CATLETT AND AITKIN | 20231119 | 306 | 20231119 | 1102 | 2273420 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 14157 | 38.8462 | -121.377 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141056 | OH | Sus | 46061766 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | Yes | Yes | 1891729 | 1 | Non-EPSS | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222597055340 | 20231119 | 1210 | 20231119 | 1320 | 2273568 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 70 | 39.1826 | -121.0846 | No | Clear;32-90 F | Service conductor | Broken | 23-0141095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891765 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13717 | 20231119 | 1849 | 20231119 | 2222 | 2273702 | 213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 14271 | 38.6007 | -120.7101 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0141133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891799 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRIP-SAVER | 18935 | 20231120 | 900 | 20231120 | 938 | 2274070 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 188 | 7144 | 38.6729 | -120.8939 | No | Clear;32-90 F |  |  | 23-0141253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891923 | 0 | EPSS Ckt | N | 2023 | POS # 1 & 3
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6129 | 20231120 | 924 | 20231120 | 1041 | 2274121 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 5547 | 38.9854 | -121.0048 | No | Clear;32-90 F |  |  | 23-0141282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891948 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER 1102 | 152461102 | FUSE | 33593 | 20231120 | 1318 | 20231120 | 1834 | 2274382 | 316 | Distribution Circuit | Animal | Squirrel | 4 | 848 | 38.8951 | -121.0925 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141519 | OH | Sus | 31676816 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1892006 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2559 | 20231120 | 1335 | 20231120 | 2205 | 2274442 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 36092 | 38.8019 | -120.1111 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141469 | OH | Sus | 31676775 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1891990 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | TRANSFORMER | T0608 | 20231120 | 1630 | 20231121 | 301 | 2274561 | 631 | Transformer only | Equipment Failure/Involved | Underground | 15 | 9465 | 38.6761 | -120.9906 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0141551 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1892014 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 7681 | 20231121 | 903 | 20231121 | 940 | 2274870 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 7799 | 38.9107 | -121.0629 | No | Partly Cloudy;32-90 F |  |  | 23-0141729 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892140 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10247 | 20231121 | 919 | 20231121 | 1418 | 2274934 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2691 | 38.809 | -120.9089 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Broken | 23-0141766 | OH | Sus | 46063363 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892162 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | JUMPER | OJ SS OF CGC# 222505041637 | 20231121 | 1013 | 20231121 | 1147 | 2274931 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 94 | 38.8064 | -121.1226 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0141720 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1892134 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 18361 | 20231121 | 1556 | 20231121 | 1635 | 2275244 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 663 | 38.7328 | -120.8979 | No | Clear;32-90 F |  |  | 23-0142003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892217 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12257 | 20231122 | 930 | 20231122 | 950 | 2275640 | 20 | Distribution Circuit | Animal | Squirrel | 1 | 20 | 38.769 | -120.6206 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 23-0142265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892344 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222682756442 | 20231122 | 939 | 20231122 | 1550 | 2275557 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 371 | 39.2126 | -121.0543 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0142346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892365 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5633 | 20231124 | 832 | 20231124 | 919 | 2276425 | 47 | Distribution Circuit | Animal | Squirrel | 21 | 972 | 38.9612 | -121.0828 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892541 | 1 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11919 | 20231124 | 1012 | 20231124 | 1113 | 2276491 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1037 | 38.6761 | -120.9496 | No | Clear;32-90 F |  |  | 23-0142633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892558 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | OCB | 1103/2 | 20231125 | 2021 | 20231126 | 506 | 2277186 | 525 | Distribution Circuit | 3rd Party | Vehicle | 1155 | 57351 | 38.6597 | -120.9473 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0142855 | OH | Sus | 35513680 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1892702 | 0 | EPSS Ckt | N | 2023 | n/a
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 31087 | 20231127 | 920 | 20231127 | 935 | 2278022 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 45 | 38.7364 | -121.1976 | No | Clear;32-90 F |  |  | 23-0143082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1893006 | 1 | Non-EPSS | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6415 | 20231127 | 1210 | 20231127 | 1249 | 2278141 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 624 | 39.2132 | -120.7803 | No | Clear;32-90 F | Insulator | Broken | 23-0143133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1893027 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | TRANSFORMER | 222946537175 | 20231127 | 1321 | 20231127 | 1636 | 2278229 | 195 | Transformer only | Animal | Squirrel | 1 | 195 | 38.6829 | -120.9691 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0143259 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1893078 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | JUMPER | 8417 HS JUMPERS | 20231128 | 1226 | 20231128 | 1448 | 2279014 | 142 | Distribution Circuit | Animal | Squirrel | 1 | 142 | 38.7224 | -120.7917 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 23-0143528 | OH | Sus | 46071958 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1893380 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 8609 | 20231128 | 1344 | 20231128 | 1436 | 2279059 | 52 | Distribution Circuit | Animal | Bird found | 7 | 382 | 38.9056 | -121.0625 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0143557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1893385 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | JUMPER | OJS 1 SS OF 1687 GOULART RANCH RD | 20231128 | 2018 | 20231128 | 2225 | 2279275 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 254 | 38.8587 | -121.1527 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0143627 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1893414 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20231129 | 1945 | 20231130 | 256 | 2280262 | 431 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 32 | 13792 | 39.2791 | -120.9786 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0144031 | OH | Sus | 46073898 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1893772 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 21525 | 20231130 | 1130 | 20231130 | 1442 | 2280781 | 192 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 192 | 38.7033 | -120.856 | No | Overcast;32-90 F |  |  | 23-0144360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1894069 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4821 | 20231130 | 1523 | 20231130 | 1545 | 2280957 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 264 | 39.2427 | -121 | No | Overcast;32-90 F | Other | Broken | 23-0144382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1894074 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 30393 | 20231130 | 1923 | 20231130 | 2021 | 2281078 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 58 | 39.0117 | -121.0337 | No | Overcast;32-90 F |  |  | 23-0144435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1894096 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20231201 | 651 | 20231201 | 908 | 2281184 | 137 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 54 | 7398 | 38.9463 | -121.2467 | No | Fog;32-90 F |  |  | 23-0144576 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894243 | 0 | EPSS Ckt | N | 2023 | a-b
SIERRA | PLACER | BELL-1109 | 152701109 | JUMPER | OJ 1 SPAN SS OF CGC 2122645247252 | 20231201 | 942 | 20231201 | 1429 | 2281431 | 287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 861 | 38.9606 | -121.0713 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0144602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894302 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 32149 | 20231201 | 1557 | 20231202 | 109 | 2281797 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 552 | 39.0632 | -121.0331 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0144856 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894437 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 824151 | 20231201 | 1726 | 20231201 | 1822 | 2281856 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 7952 | 39.417 | -120.7995 | No | Overcast-Fog;32-90 F | Insulator | Broken | 23-0144819 | OH | Sus | 40227004 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894426 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7091 | 20231202 | 617 | 20231202 | 809 | 2281973 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2016 | 38.7603 | -120.5804 | No | Overcast-Drizzle;32-90 F |  |  | 23-0144890 | OH | Sus | 46077621 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894499 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11437 | 20231202 | 955 | 20231202 | 1018 | 2282120 | 23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 2622 | 38.7111 | -120.9456 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0144907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894551 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222345352267 | 20231202 | 1041 | 20231202 | 1245 | 2282150 | 124 | Transformer only | Animal | Other | 2 | 248 | 39.0988 | -121.1747 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0144939 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1894577 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 3643 | 20231202 | 1321 | 20231202 | 1838 | 2282278 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 23269 | 38.7363 | -121.196 | No | Clear;32-90 F | Woodpin | Broken | 23-0144953 | OH | Sus | 46077553 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894589 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7091 | 20231202 | 1358 | 20231202 | 1652 | 2282290 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2204 | 38.7603 | -120.5804 | No | Overcast;32-90 F | Insulator | Broken | 23-0144960 | OH | Sus | 31677962 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894591 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | SWITCH | 77273 | 20231203 | 622 | 20231203 | 910 | 2282620 | 168 | Distribution Circuit | 3rd Party | Vehicle | 287 | 45034 | 38.7386 | -120.7799 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 23-0145003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894639 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222837444167 | 20231203 | 954 | 20231203 | 1108 | 2282699 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 38.8768 | -121.0041 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 23-0145023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1894673 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222596561680 | 20231203 | 1017 | 20231203 | 1706 | 2282713 | 409 | Transformer only | Animal | Squirrel | 1 | 409 | 39.3572 | -121.0828 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0145027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1894677 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18985 | 20231203 | 1222 | 20231203 | 1304 | 2282732 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 462 | 38.7208 | -120.9784 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 23-0145029 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894679 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7735 | 20231203 | 1306 | 20231203 | 1407 | 2282746 | 61 | Distribution Circuit | Animal | Bird found | 47 | 2867 | 39.2513 | -121.1905 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0145034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894684 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223666537695 | 20231204 | 840 | 20231204 | 936 | 2283227 | 56 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 112 | 38.6943 | -120.7165 | No | Clear;32-90 F |  |  | 23-0145174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1894929 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | JUMPER | OJ'S SS OF CGC223402550690 @ LINE AND BUCK | 20231204 | 1051 | 20231204 | 1306 | 2283459 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 135 | 39.0584 | -120.8126 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0145197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1894962 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20231204 | 1431 | 20231204 | 1639 | 2283682 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1536 | 39.1679 | -120.9656 | No | Clear;32-90 F |  |  | 23-0145342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1895042 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20231204 | 1442 | 20231204 | 1548 | 2283660 | 66 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1056 | 38.8734 | -121.238 | No | Clear;32-90 F |  |  | 23-0145321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1895032 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2697 | 20231204 | 1913 | 20231204 | 2128 | 2283835 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1885 | 90603 | 39.2501 | -120.9991 | No | Clear;32-90 F | Insulator | Broken | 23-0145390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895057 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | SWITCH | 1665 | 20231205 | 1101 | 20231205 | 1147 | 2284328 | 46 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 6072 | 38.9024 | -121.0682 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0145515 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895317 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 31825 | 20231205 | 1508 | 20231205 | 1721 | 2284536 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 133 | 39.2609 | -121.0002 | No | Partly Cloudy;32-90 F | Other | Broken | 23-0145630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895369 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222987556615 | 20231205 | 2129 | 20231206 | 312 | 2284722 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 39.2165 | -120.9469 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0145727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1895432 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ SS CGC 223241054370 | 20231206 | 922 | 20231206 | 1106 | 2284964 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 416 | 39.1591 | -120.8602 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0145804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895536 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9455 | 20231207 | 714 | 20231207 | 1709 | 2285962 | 595 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2975 | 38.9464 | -121.2285 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0146293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1895996 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | SWITCH | 391 | 20231207 | 1021 | 20231207 | 1109 | 2286095 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 4416 | 38.7525 | -121.1619 | No | Partly Cloudy-Fog;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0146126 | OH | Sus | 45906638 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895927 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224087740115 | 20231207 | 1420 | 20231208 | 201 | 2286329 | 701 | Transformer only | 3rd Party | Vehicle | 4 | 2804 | 38.7591 | -120.5673 | No | Overcast;Below 32 F | Pole-Wood | Broken | 23-0146285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1895994 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 172971 | 20231207 | 1523 | 20231208 | 343 | 2286441 | 740 | Distribution Circuit | 3rd Party | Vehicle | 63 | 46620 | 39.0349 | -121.0987 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0146301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1896004 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222647557627 | 20231207 | 1613 | 20231208 | 345 | 2286409 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 8106 | 39.245 | -121.066 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0146318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896016 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 6865 | 20231207 | 1619 | 20231207 | 1941 | 2286417 | 202 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 166 | 33532 | 39.2277 | -121.1902 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0146296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895998 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222338043187 | 20231208 | 535 | 20231208 | 918 | 2286636 | 223 | Transformer only | 3rd Party | Vehicle | 1 | 223 | 38.8496 | -121.1802 | No | Clear;32-90 F | Transformer | Broken- wire on object | 23-0146417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1896139 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9809 | 20231208 | 1147 | 20231208 | 1241 | 2287057 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1026 | 39.1984 | -121.0317 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0146497 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1896255 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9523 | 20231208 | 1718 | 20231208 | 1937 | 2287365 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1807 | 39.1619 | -121.0023 | No | Clear;32-90 F |  |  | 23-0146604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1896329 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 3341 | 20231209 | 932 | 20231209 | 1026 | 2287831 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 3078 | 39.0901 | -120.9493 | No | Clear;32-90 F |  |  | 23-0146650 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896469 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5229 | 20231209 | 943 | 20231209 | 1152 | 2287845 | 129 | Distribution Circuit | Animal | Squirrel | 40 | 5160 | 38.913 | -121.2561 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0146654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1896474 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 21873 | 20231209 | 1246 | 20231209 | 1451 | 2287957 | 125 | Distribution Circuit | Animal | Bird found | 77 | 9625 | 38.7228 | -121.0138 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0146669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1896506 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5895 | 20231210 | 1522 | 20231210 | 1612 | 2288437 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 150 | 38.8982 | -120.956 | No | Partly Cloudy;32-90 F |  |  | 23-0146759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1896616 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 18678 | 20231210 | 1931 | 20231210 | 2236 | 2288520 | 185 | Distribution Circuit | Equipment Failure/Involved | Underground | 49 | 6923 | 38.6903 | -121.0039 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 23-0146800 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896660 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | TRANSFORMER | 223399539151 | 20231210 | 2129 | 20231211 | 1032 | 2288635 | 783 | Distribution Circuit | 3rd Party | Vehicle | 174 | 27252 | 38.7359 | -120.8092 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0146801 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896694 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 8141 | 20231211 | 1036 | 20231211 | 1436 | 2289173 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 8880 | 38.6796 | -120.873 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0146858 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1896851 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222566551353 | 20231211 | 1701 | 20231211 | 1751 | 2289516 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 50 | 39.073 | -121.0973 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0146926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1896930 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5229 | 20231211 | 1725 | 20231211 | 2009 | 2289525 | 164 | Distribution Circuit | Animal | Bird found | 27 | 4376 | 38.913 | -121.2561 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0146931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896935 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | FUSE | 1765 | 20231211 | 1952 | 20231212 | 516 | 2289590 | 564 | Distribution Circuit | Equipment Failure/Involved | Underground | 185 | 45841 | 38.7998 | -121.2622 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0146957 | UG | Sus | 35516679 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896962 | 1 | Non-EPSS | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223137536170 | 20231212 | 308 | 20231212 | 905 | 2289668 | 357 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1071 | 38.6551 | -120.9016 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0146975 | OH | Sus | 46087679 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1896987 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | TRANSFORMER | T1639 | 20231212 | 545 | 20231212 | 1745 | 2289683 | 720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 7538 | 38.7967 | -121.2646 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1897119 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | TRANSFORMER | 222494545720 | 20231212 | 907 | 20231212 | 1144 | 2289867 | 157 | Transformer only | Company Initiated | Personnel- company | 2 | 314 | 38.9188 | -121.1241 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0141792 | OH | Sus | 31663919 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1897107 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 960916 | 20231212 | 936 | 20231212 | 1110 | 2289919 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 894 | 45003 | 39.2538 | -121.1981 | No | Clear;32-90 F |  |  | 23-0147022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1897146 | 0 | EPSS Ckt | N | 2023 | C GRD
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5459 | 20231212 | 1033 | 20231212 | 1108 | 2289977 | 35 | Distribution Circuit | Animal | Squirrel | 1 | 35 | 38.9276 | -121.0814 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0147051 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1897172 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 89455 | 20231212 | 1913 | 20231212 | 2245 | 2290318 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4240 | 38.8195 | -121.1398 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0147130 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897244 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2110 | 20231212 | 2106 | 20231213 | 441 | 2290378 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 852 | 53628 | 39.2017 | -121.0784 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0147139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897274 | 0 | EPSS Ckt | N | 2023 | NONE
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 7509 | 20231213 | 249 | 20231213 | 432 | 2290469 | 103 | Distribution Circuit | Animal | Other | 2 | 206 | 38.8795 | -121.2244 | No | Fog;32-90 F | Conductor- Overhead | Normal | 23-0147160 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1897290 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 35897 | 20231213 | 722 | 20231213 | 835 | 2290524 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 38.9129 | -121.0612 | No | Clear;32-90 F |  |  | 23-0147182 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1897356 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S 2SPAN S/OF 223880737477 | 20231213 | 815 | 20231213 | 1507 | 2290553 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 412 | 38.6866 | -120.6427 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0147176 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897315 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1467 | 20231213 | 1803 | 20231213 | 2233 | 2291239 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 14580 | 38.7047 | -120.7076 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0147303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897580 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222678356737 | 20231213 | 1943 | 20231213 | 2026 | 2291380 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 172 | 39.2207 | -121.0558 | No | Clear;32-90 F |  |  | 23-0147333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1897609 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222702854982 | 20231213 | 2230 | 20231214 | 401 | 2291295 | 331 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 137 | 16163 | 39.1723 | -121.0477 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0147359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897634 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224031035195 | 20231214 | 1012 | 20231214 | 1109 | 2291798 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 38.6243 | -120.59 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 23-0147433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1897849 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 32773 | 20231214 | 1100 | 20231214 | 1505 | 2291840 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 245 | 39.1348 | -121.0522 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147427 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897836 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1109 | 152701109 | SWITCH | P795 | 20231214 | 1148 | 20231214 | 1535 | 2291892 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 11804 | 38.9524 | -121.0571 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0147416 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897859 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 889 | 20231215 | 734 | 20231215 | 742 | 2292277 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 1136 | 39.3653 | -120.7935 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897999 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | JUMPER | OJ 5 POLES N/OF 32297 | 20231215 | 845 | 20231215 | 959 | 2292241 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 74 | 39.2256 | -121.0894 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0147529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897979 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 20231215 | 856 | 20231215 | 1446 | 2292355 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4900 | 39.4642 | -120.8458 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898061 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31407 | 20231215 | 904 | 20231215 | 1257 | 2292232 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2330 | 39.2779 | -120.9453 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897973 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ TWD CGC 222901738740 | 20231215 | 926 | 20231215 | 1405 | 2292299 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 279 | 38.7263 | -120.9857 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147534 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898015 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7949 | 20231216 | 901 | 20231216 | 1336 | 2292968 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 275 | 39.5664 | -120.693 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0147630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898257 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4775 | 20231216 | 1942 | 20231216 | 2202 | 2293379 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3082 | 39.2375 | -121.0096 | No | Clear;32-90 F |  |  | 23-0147687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898411 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | TRANSFORMER | T3257 | 20231217 | 124 | 20231217 | 1436 | 2293446 | 792 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1584 | 38.7438 | -121.2093 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0147717 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | No | No | 1898445 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 3125 | 20231217 | 1630 | 20231217 | 2321 | 2293837 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 7398 | 38.8521 | -121.1708 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0147788 | OH | Sus | 31679762 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1898539 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222417852269 | 20231217 | 2124 | 20231217 | 2235 | 2293944 | 71 | Transformer only | 3rd Party | Vehicle | 3 | 213 | 39.0984 | -121.1495 | No | Overcast;32-90 F | Fuse | Normal | 23-0147815 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898575 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7255 | 20231218 | 101 | 20231218 | 1157 | 2293994 | 656 | Distribution Circuit | 3rd Party | Vehicle | 8 | 5248 | 39.2693 | -121.1123 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0147819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898579 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7881 | 20231218 | 140 | 20231218 | 423 | 2294007 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3260 | 38.897 | -121.4236 | No | Overcast-Fog-Drizzle-Lightning;32-90 F |  |  | 23-0147826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Three Phase Fault | 0 | No | No | No | 1898587 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222628346068 | 20231218 | 223 | 20231218 | 1314 | 2294028 | 651 | Transformer only | Environmental/External | Lightning | 3 | 1953 | 38.9277 | -121.0773 | No | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0147881 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898673 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 39733 | 20231218 | 252 | 20231218 | 1340 | 2294031 | 648 | Distribution Circuit | Environmental/External | Lightning | 12 | 7776 | 38.9277 | -121.0758 | No | Partly Cloudy-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0147843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898609 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 39731 | 20231218 | 740 | 20231218 | 911 | 2294282 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 182 | 38.9277 | -121.0777 | No | Partly Cloudy-Rain;32-90 F |  |  | 23-0147858 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898638 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6429 | 20231218 | 950 | 20231218 | 1142 | 2294380 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1456 | 39.2069 | -120.8114 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 23-0147880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898672 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9483 | 20231218 | 955 | 20231218 | 1025 | 2294387 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 180 | 39.1902 | -120.9675 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 23-0147882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898674 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | SPAULDING-1101 | 152251101 | SWITCH | 1213 | 20231218 | 1048 | 20231218 | 1241 | 2294455 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 226 | 39.3072 | -120.668 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Deteriorated | 23-0147852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898691 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20231218 | 1150 | 20231218 | 1220 | 2294480 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 960 | 39.2791 | -120.9786 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Deteriorated | 23-0147899 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898708 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 30125 | 20231218 | 1408 | 20231218 | 1600 | 2294776 | 112 | Distribution Circuit | Equipment Failure/Involved | Underground | 26 | 2912 | 38.929 | -121.0751 | No | Overcast-Drizzle;32-90 F | Other | Deteriorated | 23-0147936 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898744 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15235 | 20231218 | 1633 | 20231218 | 1759 | 2294941 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 516 | 39.0139 | -121.3189 | No | Overcast-Drizzle;32-90 F |  |  | 23-0147969 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898778 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 823805 | 20231218 | 2137 | 20231219 | 428 | 2295188 | 411 | Distribution Circuit | 3rd Party | Vehicle | 449 | 18702 | 39.0568 | -120.9613 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148011 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1898825 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7255 | 20231219 | 925 | 20231219 | 1034 | 2295496 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 552 | 39.2693 | -121.1123 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0148072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898908 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 20791 | 20231219 | 959 | 20231219 | 1042 | 2295555 | 43 | Distribution Circuit | 3rd Party | Vehicle | 44 | 1892 | 38.7304 | -120.9223 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0148086 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898949 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 19712 | 20231219 | 1132 | 20231219 | 1226 | 2295658 | 54 | Distribution Circuit | Animal | Squirrel | 481 | 25974 | 38.7219 | -120.7904 | No | Overcast-Fog-Rain;32-90 F | Insulator | Normal | 23-0148096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898959 | 0 | EPSS Ckt | N | 2023 | A GRD
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | TRANSFORMER | 223386938644 | 20231219 | 1405 | 20231219 | 1506 | 2295796 | 61 | Transformer only | Animal | Squirrel | 1 | 61 | 38.7219 | -120.8134 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Fuse | Burned Open | 23-0148124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898986 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4401 | 20231219 | 1503 | 20231219 | 1555 | 2295857 | 52 | Distribution Circuit | Animal | Bird found | 24 | 1248 | 39.2289 | -121.1889 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0148134 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898997 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18811 | 20231219 | 1716 | 20231219 | 1849 | 2295968 | 93 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 1674 | 38.6908 | -120.8589 | No | Overcast-Fog;32-90 F |  |  | 23-0148157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1899019 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 3107 | 20231219 | 1751 | 20231220 | 128 | 2296024 | 457 | Distribution Circuit | Environmental/External | Lightning | 77 | 8154 | 38.7479 | -121.3369 | No | Overcast-Heavy Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148156 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1899018 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 21697 | 20231219 | 1815 | 20231219 | 2321 | 2296041 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2754 | 38.7549 | -120.8291 | No | Overcast-Fog-Drizzle;32-90 F | Cutout- fuse holder | Broken | 23-0148150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1899012 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 35463 | 20231219 | 1843 | 20231219 | 2158 | 2296064 | 195 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 585 | 38.7954 | -121.4695 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0148189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1899056 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32621 | 20231220 | 808 | 20231220 | 1616 | 2296319 | 488 | Distribution Circuit | Animal | Squirrel | 187 | 26091 | 39.2311 | -121.0586 | No | Overcast-Fog;32-90 F | Fuse | Failed/Faulted | 23-0148218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899112 | 1 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | TRANSFORMER | 221889939386 | 20231220 | 847 | 20231220 | 1610 | 2296339 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1329 | 38.746 | -121.3383 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148240 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899168 | 0 | Non-EPSS | N | 2023
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | OTHER | T6086 TWD T6087 | 20231220 | 2040 | 20231220 | 2140 | 2297099 | 60 | Distribution Circuit | 3rd Party | Vehicle | 11 | 660 | 38.7874 | -121.1448 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Broken | 23-0148278 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1899295 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 4051 | 20231221 | 950 | 20231221 | 1035 | 2297527 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 6003 | 38.7764 | -121.2474 | No | Partly Cloudy;32-90 F |  |  | 23-0148463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899447 | 1 | Non-EPSS | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7601 | 20231222 | 848 | 20231222 | 1044 | 2298182 | 116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1856 | 39.1991 | -121.0034 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0148574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1899596 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223370050950 | 20231222 | 1711 | 20231222 | 1826 | 2298565 | 75 | Transformer only | Animal | Squirrel | 1 | 75 | 39.0594 | -120.8144 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0148613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899673 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | DEL MAR-2106 | 152582106 | SWITCH | 2419 | 20231222 | 1745 | 20231222 | 1933 | 2298578 | 108 | Distribution Circuit | Equipment Failure/Involved | Underground | 95 | 10260 | 38.7811 | -121.21 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0148606 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1899672 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223369237615 | 20231224 | 851 | 20231224 | 916 | 2299088 | 25 | Distribution Circuit | 3rd Party | Vehicle | 4 | 100 | 38.6934 | -120.8207 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0148744 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899811 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 32073 | 20231224 | 1557 | 20231224 | 1633 | 2299219 | 36 | Distribution Circuit | Animal | Squirrel | 11 | 396 | 38.8222 | -121.164 | No | Clear;32-90 F | Fuse | Burned Open | 23-0148766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1899838 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 18875 | 20231225 | 1409 | 20231225 | 1525 | 2299494 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 86 | 6536 | 38.8221 | -120.8809 | No | Clear;32-90 F |  |  | 23-0148834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1899905 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33769 | 20231227 | 1012 | 20231227 | 1353 | 2300571 | 221 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 54 | 11934 | 39.1578 | -121.0255 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0148983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1900151 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223122041900 | 20231227 | 1415 | 20231227 | 1421 | 2300789 | 6 | Distribution Circuit | 3rd Party | Vandalism | 1 | 6 | 38.8109 | -120.9061 | No | Overcast;32-90 F | Other | Broken | 23-0149021 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1900191 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | TRANSFORMER | T713881 | 20231227 | 1439 | 20231227 | 1452 | 2300822 | 13 | Transformer only | 3rd Party | Other | 12 | 156 | 38.8572 | -121.2857 | No | Overcast-Rain;32-90 F | Transformer (UG) | Deteriorated | 23-0149032 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900203 | 0 | Non-EPSS | N | 2023
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223074036850 | 20231227 | 1810 | 20231227 | 1859 | 2300933 | 49 | Transformer only | Animal | Bird found | 1 | 49 | 38.6738 | -120.9244 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0149043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900217 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223979239880 | 20231228 | 1453 | 20231228 | 2115 | 2301453 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 764 | 38.7531 | -120.6056 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0149135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900391 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | OTHER | T963294 TWD T713881 | 20231228 | 2105 | 20231228 | 2206 | 2301622 | 61 | Distribution Circuit | 3rd Party | Vehicle | 28 | 1708 | 38.8574 | -121.285 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Broken | 23-0149133 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1900423 | 0 | Non-EPSS | N | 2023
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4227 | 20231229 | 948 | 20231229 | 1025 | 2301815 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 333 | 39.2426 | -121.112 | No | Overcast;32-90 F |  |  | 23-0149203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900492 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 30413 | 20231229 | 1051 | 20231229 | 1623 | 2301880 | 332 | Distribution Circuit | 3rd Party | Vehicle | 26 | 8632 | 38.9419 | -121.1111 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0149207 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1900498 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 17361 | 20231229 | 1405 | 20231229 | 1919 | 2302038 | 314 | Distribution Circuit | 3rd Party | Vehicle | 29 | 9106 | 39.0051 | -121.34 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0149244 | OH | Sus | 35520275 | NORTH VALLEY AND SIERRA | DEC | Three Phase Fault | 0 | No | Yes | No | 1900541 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 100000015487 | 20231229 | 1459 | 20231229 | 1730 | 2302086 | 151 | Transformer only | Vegetation | Tree - fell into line | 1 | 151 | 38.7584 | -120.5655 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0149253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1900551 | 0 | EPSS Ckt | N | 2023
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 44565 | 20231230 | 129 | 20231230 | 920 | 2302372 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 942 | 38.9338 | -121.1818 | No | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0149303 | OH | Sus | 46104730 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1900601 | 0 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 30539 | 20231230 | 908 | 20231230 | 1526 | 2302616 | 378 | Distribution Circuit | 3rd Party | Vehicle | 1415 | 20421 | 39.1001 | -121.0945 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0149345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900654 | 1 | EPSS Ckt | N | 2023
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8167 | 20231231 | 1030 | 20231231 | 1325 | 2303170 | 175 | Distribution Circuit | 3rd Party | Vehicle | 4 | 700 | 39.098 | -121.1506 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0149465 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1900784 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223626541661 | 20231231 | 1735 | 20231231 | 2033 | 2303312 | 178 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 178 | 38.8027 | -120.7298 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0149495 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1900816 | 0 | EPSS Ckt | N | 2023
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223726036195 | 20240102 | 53 | 20240102 | 403 | 2304450 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 190 | 38.6527 | -120.6969 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0005849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1900948 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 30297 | 20240102 | 858 | 20240102 | 1541 | 2304611 | 403 | Distribution Circuit | Animal | Squirrel | 5 | 1859 | 39.2206 | -121.0724 | No | Overcast;32-90 F | Lightning Arrestor | Broken | 24-0005935 | OH | Sus | 31680628 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901033 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222685062240 | 20240102 | 1213 | 20240103 | 331 | 2304857 | 918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2754 | 39.3724 | -121.0507 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0006118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901091 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 386572 | 20240102 | 1616 | 20240102 | 1648 | 2305063 | 32 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 276 | 8832 | 38.6242 | -120.9097 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0006188 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1901103 | 0 | EPSS Ckt | N | 2024 | A-C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31045 | 20240102 | 1804 | 20240103 | 328 | 2305150 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2256 | 38.9363 | -120.905 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0006234 | OH | Sus | 31680654 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1901133 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | OTHER | 604920 | 20240102 | 2310 | 20240103 | 1145 | 2305571 | 755 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12655 | 39.3083 | -120.54 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0006296 | OH | Sus | 46125271 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | Yes | 1901195 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6407 | 20240103 | 949 | 20240103 | 1712 | 2306237 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 21768 | 39.2088 | -120.8165 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 24-0006364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901339 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224097639774 | 20240103 | 959 | 20240103 | 1008 | 2306249 | 9 | Transformer only | Environmental/External | Ice or snow | 2 | 18 | 38.7496 | -120.5637 | No | Overcast-Fog;32-90 F | Fuse | Broken | 24-0006414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901326 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 9593 | 20240103 | 1004 | 20240103 | 1432 | s1901362 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 12983 | 39.2173 | -120.8092 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0006364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901362 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20240103 | 2113 | 20240103 | 2311 | 2306710 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1888 | 38.8734 | -121.238 | No | Fog;32-90 F |  |  | 24-0006670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901430 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 20167 | 20240104 | 1111 | 20240104 | 1421 | 2307098 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 877 | 38.6992 | -120.8515 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0006924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1901619 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 32099 | 20240104 | 1311 | 20240104 | 1332 | 2307170 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 147 | 38.7997 | -121.1643 | No | Clear;32-90 F | Insulator | Broken | 24-0006947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1901625 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | OCB | 1112/2 | 20240105 | 1137 | 20240105 | 1222 | 2307922 | 45 | Distribution Circuit | Animal | Squirrel | 2109 | 39553 | 38.7313 | -120.7839 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0007364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1901860 | 0 | EPSS Ckt | N | 2024 | a-b-c time oc
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5047 | 20240105 | 1208 | 20240105 | 1343 | 2307952 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 2660 | 38.8257 | -121.158 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0007381 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1901863 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222749053146 | 20240105 | 1847 | 20240106 | 29 | 2308204 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 342 | 39.122 | -121.0328 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0007504 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1901895 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1102 | 153701102 | TRANSFORMER | 221995944685 | 20240105 | 2003 | 20240105 | 2153 | 2308222 | 110 | Transformer only | Environmental/External | Fire- Forest/Grass | 3 | 330 | 38.8914 | -121.2997 | No | Clear;32-90 F | Service conductor | Burned Open | 24-0007543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901928 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6123 | 20240106 | 1226 | 20240106 | 1645 | 2308696 | 210 | Distribution Circuit | 3rd Party | Other | 904 | 42868 | 38.9793 | -121.0075 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0007624 | OH | Sus | 46131898 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1902006 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | FUSE | 1587 | 20240107 | 1020 | 20240107 | 2119 | 2309169 | 659 | Distribution Circuit | Equipment Failure/Involved | Underground | 142 | 30311 | 38.8162 | -121.2692 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0007749 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902120 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 5445 | 20240108 | 908 | 20240108 | 1816 | 2309613 | 548 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 12690 | 38.8893 | -121.0758 | No | Overcast;32-90 F | Elbow | Broken | 24-0007915 | UG | Sus | 46132477 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902339 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20240108 | 1415 | 20240108 | 1557 | 2309995 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1250 | 120755 | 39.1444 | -120.908 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Arcing | 24-0008110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902407 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222451044800 | 20240108 | 1519 | 20240108 | 2139 | 2310052 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 380 | 38.8942 | -121.1404 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0008182 | OH | Sus | 35521897 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902418 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 32801 | 20240108 | 1523 | 20240108 | 2319 | 2310074 | 476 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1415 | 50095 | 39.1338 | -121.0726 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0008166 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1902415 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223405056270 | 20240108 | 1705 | 20240108 | 1718 | 2310133 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 35 | 39.2054 | -120.7994 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0008110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902421 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | BROKEN OPEN JUMPER | 20240108 | 1804 | 20240109 | 1116 | 2310162 | 1032 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 84286 | 38.8399 | -120.8193 | No | Clear;32-90 F | Jumper | Broken | 24-0008249 | OH | Sus | 46134602 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1902465 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9455 | 20240109 | 810 | 20240109 | 946 | 2310324 | 96 | Distribution Circuit | Animal | Squirrel | 5 | 480 | 38.9464 | -121.2285 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0008339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1902591 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 8307 | 20240109 | 1039 | 20240109 | 2212 | 2310786 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7623 | 39.5203 | -120.9971 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0008430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1902670 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | FUSE | 8317 | 20240110 | 1016 | 20240110 | 1444 | 2311604 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 19028 | 38.6523 | -120.9663 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 24-0008773 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1902931 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 20240110 | 1851 | 20240110 | 2157 | 2312216 | 186 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 25854 | 38.895 | -120.9113 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0009295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903069 | 0 | EPSS Ckt | N | 2024 | B C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | INTERRUPTER | 395390 | 20240110 | 1932 | 20240110 | 2153 | 2312267 | 141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2584 | 348457 | 38.8888 | -121.0166 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0009309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1903079 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20240110 | 1956 | 20240110 | 2141 | 2312330 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1470 | 38.7941 | -120.8199 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0009339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903103 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ 1 SS OF CGC 222637261169 | 20240110 | 2040 | 20240111 | 235 | 2312354 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2485 | 39.3432 | -121.0682 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Deteriorated | 24-0009317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1903086 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223278439353 | 20240110 | 2046 | 20240111 | 1010 | 2312366 | 804 | Transformer only | Vegetation | Tree - fell into line | 1 | 804 | 38.742 | -120.852 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0009398 | OH | Sus | 46141054 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1903151 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 386572 | 20240110 | 2047 | 20240110 | 2303 | 2312369 | 136 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 276 | 37536 | 38.6242 | -120.9097 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0009323 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903090 | 0 | EPSS Ckt | N | 2024 | A- C
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 183495 | 20240110 | 2050 | 20240111 | 1134 | 2312376 | 884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 79028 | 38.6733 | -120.8368 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Insulator | Broken | 24-0009396 | OH | Sus | 31681527 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1903149 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 481660 | 20240110 | 2054 | 20240115 | 1031 | 2312777 | 6522 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 54727 | 38.8107 | -120.0318 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0009593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1903359 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 97061 | 20240110 | 2056 | 20240110 | 2347 | 2312382 | 171 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 41 | 7011 | 38.7477 | -120.797 | No | Partly Cloudy-Fog-Rain;32-90 F |  |  | 24-0009374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903129 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | OLETA-1101 | 163541101 | FUSE | 12055 | 20240110 | 2102 | 20240111 | 150 | 2312388 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 8064 | 38.5385 | -120.965 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0009387 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903139 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6805 | 20240111 | 750 | 20240111 | 1058 | 2312676 | 188 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 32 | 6019 | 39.3184 | -120.3291 | No | Clear-Strong Winds;Below 32 F |  |  | 24-0009596 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1903361 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | JUMPER | OJ'S 1/P/S/OF CGC 223350438162 | 20240111 | 1103 | 20240111 | 1439 | 2312993 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 216 | 38.708 | -120.8266 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0009606 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1903362 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20240112 | 951 | 20240112 | 1020 | 2313769 | 29 | Distribution Circuit | 3rd Party | Vehicle | 1085 | 31465 | 38.8101 | -121.1629 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0010084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1903616 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7207 | 20240113 | 1743 | 20240113 | 1924 | 2314978 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 4040 | 38.9788 | -121.3691 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0010543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903834 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1102 | 152591102 | OTHER | WIRE DOWN SS OF 6841 | 20240113 | 1745 | 20240114 | 1411 | 2315114 | 1226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 30681 | 39.3107 | -120.339 | No | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0010623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1903914 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21349 | 20240113 | 1914 | 20240113 | 2101 | 2315007 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2247 | 38.5625 | -120.7507 | No | Clear;32-90 F |  |  | 24-0010563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903854 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 132649 | 20240113 | 2001 | 20240113 | 2108 | 2315034 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1206 | 38.8699 | -121.1311 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0010560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903851 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20240114 | 15 | 20240114 | 1458 | 2315147 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 36941 | 39.0914 | -121.0565 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0010639 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1903933 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21349 | 20240114 | 210 | 20240114 | 622 | 2315183 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 5292 | 38.5625 | -120.7507 | No | Overcast-Fog;32-90 F | Lightning Arrestor | Burned/flashed | 24-0010647 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903941 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1102 | 153701102 | TRANSFORMER | T1113 | 20240114 | 403 | 20240114 | 2014 | 2315192 | 971 | Distribution Circuit | Equipment Failure/Involved | Underground | 29 | 8549 | 38.8867 | -121.3059 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 24-0010648 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903953 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 2625 | 20240114 | 915 | 20240114 | 1029 | 2315256 | 74 | Distribution Circuit | Animal | Squirrel | 47 | 3499 | 38.8145 | -121.2367 | No | Overcast-Fog;32-90 F | Cutout- fuse holder | Normal | 24-0010672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903964 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 41039 | 20240114 | 1328 | 20240114 | 1430 | 2315409 | 62 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 85 | 5293 | 38.9304 | -121.075 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0010698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1903978 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 96915 | 20240114 | 1855 | 20240114 | 2043 | 2315550 | 108 | Distribution Circuit | Animal | Bird found | 9 | 972 | 39.0663 | -121.1299 | No | Overcast-Fog;32-90 F | Fuse | Normal | 24-0010734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904002 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21349 | 20240114 | 2128 | 20240114 | 2318 | 2315580 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2310 | 38.5625 | -120.7507 | No | Clear;32-90 F |  |  | 24-0010743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1904013 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 6077 | 20240115 | 1431 | 20240115 | 1540 | 2315866 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1035 | 38.8105 | -121.1644 | No | Partly Cloudy;32-90 F |  |  | 24-0010814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904069 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ @ CGC 222387056730 | 20240116 | 1118 | 20240116 | 1135 | 2316465 | 17 | Distribution Circuit | Company Initiated | Improper Construction | 13 | 217 | 39.2222 | -121.1582 | No | Overcast;32-90 F | Jumper | Normal | 24-0011026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1904293 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 224149771652 | 20240116 | 1410 | 20240117 | 1624 | 2316644 | 1574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4722 | 39.624 | -120.5255 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0011302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1904365 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY SUB | 15210 | OCB | 52G | 20240116 | 1700 | 20240116 | 1709 | 2316854 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1278 | 39.3638 | -120.7923 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0128857 | OH | Sus | 31624660 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1904367 | 0 | Non-EPSS | N | 2024 | NA
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9781 | 20240117 | 1133 | 20240117 | 1448 | 2317579 | 195 | Distribution Circuit | Company Initiated | Improper Construction | 3 | 585 | 39.1825 | -121.0273 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0011578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1904622 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 5137 | 20240117 | 1632 | 20240117 | 1757 | 2317934 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1445 | 39.191 | -121.0958 | No | Partly Cloudy;32-90 F |  |  | 24-0011872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904681 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 11823 | 20240117 | 1651 | 20240118 | 37 | 2317949 | 466 | Distribution Circuit | 3rd Party | Vehicle | 15 | 6990 | 38.7456 | -120.5647 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0011713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1904678 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 222706347536 | 20240118 | 1023 | 20240118 | 1151 | 2318361 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 72 | 6282 | 38.968 | -121.0491 | No | Partly Cloudy;32-90 F |  |  | 24-0012147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904813 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 337536 | 20240118 | 1045 | 20240118 | 1204 | 2318382 | 79 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 127 | 10033 | 38.6781 | -120.7635 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0012107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904802 | 0 | EPSS Ckt | N | 2024 | B & C
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7121 | 20240118 | 1138 | 20240118 | 1242 | 2318433 | 64 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 3520 | 39.285 | -121.0576 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0012165 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1904823 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 721041 | 20240118 | 1147 | 20240118 | 1602 | 2318410 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 255 | 38.6908 | -120.7353 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0012129 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1904809 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ'S 1 SOUTH OF CGC 223590037135 | 20240118 | 1200 | 20240118 | 1518 | 2318391 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 396 | 38.6788 | -120.7435 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0012110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1904804 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20431 | 20240119 | 1055 | 20240119 | 1250 | 2319152 | 115 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 345 | 38.6704 | -120.7821 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0012631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905087 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7385 | 20240119 | 1812 | 20240119 | 1941 | 2319401 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 6141 | 39.2623 | -121.0131 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0012801 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905138 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 5375 | 20240119 | 2017 | 20240120 | 356 | 2319463 | 459 | Distribution Circuit | 3rd Party | Vehicle | 54 | 24786 | 38.9318 | -121.1252 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0012822 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1905160 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8481 | 20240120 | 1651 | 20240121 | 839 | 2320064 | 948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 2927 | 38.9905 | -121.0159 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Broken | 24-0013002 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905283 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20240120 | 2039 | 20240121 | 850 | 2320155 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 49049 | 39.0317 | -121.0046 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Other | Broken | 24-0013018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905291 | 0 | EPSS Ckt | N | 2024 | A-C
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | FUSE | 18887 | 20240121 | 709 | 20240121 | 1028 | 2320288 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 8756 | 38.5556 | -120.9916 | No | Overcast-Fog-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0013062 | OH | Sus | 46166421 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1905331 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 697216 | 20240121 | 1157 | 20240121 | 1608 | 2320423 | 251 | Distribution Circuit | 3rd Party | Vehicle | 87 | 21837 | 38.9366 | -121.1763 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0013074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1905358 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20240121 | 1206 | 20240121 | 1255 | 2320426 | 49 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 16 | 784 | 38.8734 | -121.238 | No | Partly Cloudy;32-90 F |  |  | 24-0013099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905361 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 912421 | 20240121 | 1218 | 20240121 | 1258 | 2320417 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 80 | 39.1011 | -121.132 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0013097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905360 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222287055839 | 20240122 | 505 | 20240122 | 908 | 2320897 | 243 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 243 | 39.1971 | -121.1938 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0013197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905446 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222451657837 | 20240122 | 658 | 20240122 | 746 | 2320972 | 48 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 48 | 39.2521 | -121.1365 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 24-0013239 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1905465 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7585 | 20240122 | 903 | 20240122 | 1012 | 2321127 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1173 | 38.7722 | -121.4512 | No | Overcast-Drizzle;32-90 F |  |  | 24-0013341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905543 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6637 | 20240122 | 937 | 20240123 | 250 | 2321199 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 10330 | 39.3147 | -120.4586 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0013434 | OH | Sus | 46170544 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905582 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 34489 | 20240122 | 1105 | 20240122 | 1412 | 2321323 | 187 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 6545 | 39.3122 | -120.5012 | No | Clear;32-90 F |  |  | 24-0013507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1905609 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223036355670 | 20240122 | 1359 | 20240122 | 1454 | 2321517 | 55 | Transformer only | 3rd Party | Vehicle | 1 | 55 | 39.1904 | -120.9291 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 24-0013533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905616 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222307256581 | 20240122 | 1425 | 20240122 | 1634 | 2321450 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 129 | 39.218 | -121.1867 | No | Overcast-Fog;32-90 F |  |  | 24-0013524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905614 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | TRANSFORMER | T2157 | 20240122 | 2037 | 20240123 | 446 | 2321869 | 489 | Distribution Circuit | 3rd Party | Vehicle | 87 | 21963 | 38.7766 | -121.24 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Broken | 24-0013622 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1905666 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | OCB | 2105/2/NORM | 20240123 | 640 | 20240123 | 802 | 2321974 | 82 | Distribution Circuit | Animal | Other | 287 | 23534 | 39.2354 | -121.269 | No | Partly Cloudy-Fog;32-90 F | PT/CCVT | Burned/flashed | 24-0013686 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905690 | 0 | EPSS Ckt | N | 2024 | PH TIME OC GRD
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | TRANSFORMER | T6293 | 20240123 | 900 | 20240123 | 1226 | 2322115 | 206 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 206 | 38.7781 | -121.1607 | No | Partly Cloudy-Fog;32-90 F | Transformer | Normal | 24-0008603 | OH | Sus | 35421297 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1905772 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 36693 | 20240123 | 1641 | 20240124 | 18 | 2322552 | 457 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1828 | 39.201 | -121.0915 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0014077 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1905893 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20240124 | 1111 | 20240124 | 1147 | 2323077 | 36 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 16 | 576 | 38.8734 | -121.238 | No | Overcast-Fog;32-90 F |  |  | 24-0014405 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906069 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20240124 | 1149 | 20240124 | 1452 | 2323125 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 4272 | 38.6658 | -120.7503 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0014572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906101 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222708761275 | 20240124 | 1603 | 20240124 | 1700 | 2323367 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 114 | 39.3453 | -121.0428 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 24-0014678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906114 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 77845 | 20240125 | 843 | 20240125 | 1045 | 2323784 | 122 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1342 | 38.8325 | -121.1363 | No | Overcast-Fog;32-90 F |  |  | 24-0015017 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1906372 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ'S 1 SS/OF CGC 223549637409 | 20240125 | 1043 | 20240125 | 1338 | 2323738 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 175 | 38.6866 | -120.7591 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0014887 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1906217 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32995 | 20240125 | 1753 | 20240125 | 2111 | 2324325 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 49104 | 39.253 | -121.1151 | No | Overcast;32-90 F |  |  | 24-0015327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1906447 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 720679 | 20240126 | 1018 | 20240126 | 1202 | 2324771 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 7280 | 38.9681 | -121.0491 | No | Overcast;32-90 F |  |  | 24-0015585 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1906680 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20240126 | 1109 | 20240126 | 1233 | 2324831 | 84 | Distribution Circuit | Vegetation | Tree - branch fell on line | 778 | 50271 | 38.7523 | -120.6821 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0015561 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1906672 | 0 | EPSS Ckt | N | 2024 | A B TIME OC
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 4883 | 20240126 | 1237 | 20240126 | 1544 | 2324937 | 187 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 187 | 39.2192 | -121.0598 | No | Overcast;32-90 F | Other | Bent or Twisted | 24-0015615 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1906691 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | SHADY GLEN-1102 | 152431102 | RECLOSER | 51484 | 20240126 | 1244 | 20240126 | 1329 | 2324957 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 276 | 12420 | 39.1909 | -120.9998 | No | Overcast;32-90 F | Insulator | Broken | 24-0015479 | OH | Sus | 2033539 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1906693 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223110737517 | 20240127 | 1317 | 20240127 | 1653 | 2325634 | 216 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 216 | 38.6916 | -120.911 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0015878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906861 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | OCB | 1106/2 | 20240128 | 1316 | 20240128 | 1327 | 2326414 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1700 | 18700 | 38.7444 | -121.161 | No | Clear;32-90 F |  |  | 24-0015972 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1906932 | 0 | EPSS Ckt | N | 2024 | SET A RLY
SIERRA | PLACER | BELL-1110 | 152701110 | SWITCH | 2093 | 20240128 | 1727 | 20240128 | 1830 | 2326504 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1260 | 38.9443 | -121.0987 | No | Clear;32-90 F | Sectionalizer | Broken | 24-0016000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1906944 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 222627749033 | 20240128 | 1919 | 20240129 | 1148 | 2326625 | 989 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1978 | 39.0094 | -121.0767 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016025 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906967 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | TRANSFORMER | T326607 | 20240129 | 1321 | 20240129 | 1410 | 2327387 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 245 | 38.8552 | -121.2852 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0016281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907242 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OCB | 1104/2 | 20240129 | 1333 | 20240130 | 49 | 2327394 | 676 | Distribution Circuit | Equipment Failure/Involved | Underground | 2565 | 135615 | 39.2314 | -121.0346 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0016277 | UG | Sus | 46174292 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907240 | 0 | EPSS Ckt | N | 2024 | B GRD TIME OC
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | SWITCH | 7561 | 20240129 | 1425 | 20240129 | 2340 | 2327433 | 555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3330 | 39.0098 | -121.0768 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0016315 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907246 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222704058743 | 20240129 | 1708 | 20240129 | 1850 | 2327558 | 102 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 102 | 39.2755 | -121.0458 | No | Clear;32-90 F |  |  | 24-0016407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1907282 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2103 | 152442103 | OTHER | T491788 TWD T326607 | 20240129 | 2126 | 20240129 | 2223 | 2327674 | 57 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1083 | 38.8552 | -121.2858 | No | Partly Cloudy-Fog;32-90 F | Transformer (UG) | Broken | 24-0016389 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907307 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222745549110 | 20240129 | 2141 | 20240129 | 2232 | 2327677 | 51 | Transformer only | Animal | Squirrel | 1 | 51 | 39.0112 | -121.0345 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0016444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907311 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33267 | 20240130 | 1011 | 20240130 | 1218 | 2328073 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 254 | 39.1822 | -120.9716 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0016548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907465 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5355 | 20240130 | 1430 | 20240130 | 2308 | 2328422 | 518 | Distribution Circuit | 3rd Party | Vehicle | 25 | 10346 | 38.8863 | -121.2198 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0016833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907572 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5925 | 20240130 | 1536 | 20240130 | 1652 | 2328452 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 456 | 39.0331 | -120.797 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0016829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907570 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 4427 | 20240130 | 1724 | 20240130 | 1917 | 2328585 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 113 | 39.2553 | -121.0182 | No | Partly Cloudy;32-90 F |  |  | 24-0016903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907589 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJS 1 SP N/OF CGC 223592035005 | 20240131 | 816 | 20240131 | 1200 | 2329002 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 224 | 38.6215 | -120.7436 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0017063 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907703 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ'S 2 SPANS W/OF CGC 222055955886 | 20240131 | 850 | 20240131 | 1024 | 2329015 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 188 | 39.1993 | -121.2769 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0017069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907715 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | OCB | 1102/2 | 20240131 | 1107 | 20240201 | 1125 | 2329460 | 1458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 85826 | 39.314 | -120.4961 | No | Partly Cloudy-Strong Winds;32-90 F | Insulator | Broken | 24-0017236 | OH | Sus | 46175757 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1907858 | 0 | EPSS Ckt | N | 2024 | BC TIME OC & INST OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30573 | 20240131 | 1453 | 20240131 | 1722 | 2329881 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 5513 | 38.8208 | -121.0293 | No | Overcast;32-90 F |  |  | 24-0017525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1907962 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 92653 | 20240131 | 1505 | 20240131 | 1930 | 2330078 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 795 | 38.8468 | -121.2056 | No | Partly Cloudy;32-90 F |  |  | 24-0017606 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1908022 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 132649 | 20240131 | 1558 | 20240131 | 1648 | 2329974 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 900 | 38.8699 | -121.1311 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 24-0017533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1907965 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | RECLOSER | 50142 | 20240131 | 1647 | 20240131 | 2151 | 2330035 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 60540 | 38.767 | -121.1548 | No | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0017500 | OH | Sus | 31682696 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1907976 | 0 | EPSS Ckt | N | 2024 | A-B-C
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20240131 | 1653 | 20240201 | 1500 | 2330046 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 79410 | 38.8543 | -121.1728 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0017541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1907967 | 0 | EPSS Ckt | N | 2024 | A&B
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5381 | 20240131 | 1658 | 20240131 | 2142 | 2330050 | 284 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 10508 | 38.9235 | -121.1807 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0017686 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1908081 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 307494 | 20240131 | 1700 | 20240201 | 1352 | 2330057 | 1252 | Distribution Circuit | 3rd Party | Other | 276 | 165950 | 38.934 | -121.1793 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Multi-Fault | 0 | No | Yes | No | 1907971 | 0 | EPSS Ckt | N | 2024 | TIME OC A-B-C GRD
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 132649 | 20240131 | 1705 | 20240131 | 2034 | 2330077 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 3762 | 38.8699 | -121.1311 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 24-0017564 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1907981 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18773 | 20240131 | 1716 | 20240131 | 1820 | 2330087 | 64 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 5806 | 38.6472 | -120.9436 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0017581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1907999 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 3409 | 20240131 | 1719 | 20240131 | 2010 | 2330093 | 171 | Distribution Circuit | Animal | Bird found | 44 | 7524 | 39.1127 | -120.961 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0017637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1908041 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4487 | 20240131 | 1721 | 20240201 | 1624 | 2330095 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 25428 | 38.9132 | -120.9627 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0017595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1908011 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | SWITCH | 36013 | 20240131 | 1731 | 20240201 | 100 | 2330114 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2245 | 39.216 | -121.0636 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1908000 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222353244085 | 20240131 | 1732 | 20240201 | 1303 | 2330122 | 1171 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4684 | 38.8742 | -121.1741 | No | Rain-Overcast-Fog;32-90 F | Jumper | Broken | 24-0017699 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1908093 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 30845 | 20240131 | 2031 | 20240201 | 1355 | 2330264 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 19836 | 39.0929 | -120.9445 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0017656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1908054 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | MTR#1007739630 | 20240201 | 251 | 20240201 | 1133 | 2330811 | 522 | Transformer only | Vegetation | Tree - fell into line | 1 | 522 | 39.1128 | -121.0907 | No | Overcast-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0017788 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1908180 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 297538 | 20240201 | 310 | 20240201 | 1203 | 2330747 | 533 | Distribution Circuit | 3rd Party | Vehicle | 30 | 11830 | 39.2336 | -121.0286 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0017755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908153 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9789 | 20240201 | 319 | 20240201 | 1317 | 2330773 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 5076 | 39.212 | -121.0191 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0017769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1908168 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 33351 | 20240201 | 655 | 20240201 | 814 | 2330850 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2686 | 38.7983 | -121.2287 | No | Clear;32-90 F |  |  | 24-0017826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908189 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222856858079 | 20240201 | 1041 | 20240201 | 1130 | 2331201 | 49 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 49 | 39.2575 | -120.9918 | No | Overcast;32-90 F |  |  | 24-0018024 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1908308 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 79841 | 20240201 | 1054 | 20240201 | 1222 | 2331223 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 440 | 38.7853 | -121.1688 | No | Clear;32-90 F |  |  | 24-0018051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908316 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | SWITCH | 853463 | 20240201 | 1430 | 20240201 | 1444 | 2331497 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 13 | 182 | 38.9505 | -121.2239 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0017545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1908352 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJS 2 SS OF CGC#222748156571 | 20240201 | 1444 | 20240201 | 1827 | 2331555 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2230 | 39.2155 | -121.0289 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0018184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1908351 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 34489 | 20240201 | 1623 | 20240201 | 1847 | 2331710 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 5040 | 39.3122 | -120.5012 | No | Clear;Below 32 F |  |  | 24-0018343 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908410 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20240201 | 2114 | 20240202 | 1222 | 2331958 | 908 | Distribution Circuit | 3rd Party | Vehicle | 521 | 27070 | 38.9452 | -121.1218 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0018365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908434 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9863 | 20240202 | 14 | 20240202 | 20 | 2331990 | 6 | Distribution Circuit | Animal | Squirrel | 1 | 6 | 38.8561 | -121.029 | No | Overcast-Fog-Drizzle;32-90 F | Cutout- fuse holder | Normal | 24-0018382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908443 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223266742573 | 20240202 | 609 | 20240202 | 1013 | 2332127 | 244 | Transformer only | Vegetation | Tree - fell into line | 1 | 244 | 38.8302 | -120.8543 | No | Overcast-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0018543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1908590 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222353244085 | 20240202 | 901 | 20240202 | 959 | 2332307 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 232 | 38.8742 | -121.1741 | No | Overcast-Fog-Drizzle;32-90 F | Bushing | Broken | 24-0018488 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908557 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7765 | 20240202 | 914 | 20240202 | 1041 | 2332287 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 5568 | 39.2018 | -121.1976 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Leaking | 24-0018481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908534 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240202 | 1225 | 20240202 | 1252 | 2332548 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2683 | 72441 | 38.6943 | -120.6784 | No | Partly Cloudy-Fog-Rain;32-90 F | Recloser | Arcing | 24-0018665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908619 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18851 | 20240202 | 1513 | 20240203 | 928 | 2332888 | 1095 | Distribution Circuit | Environmental/External | Lightning | 28 | 3684 | 38.732 | -120.9653 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0018841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1908702 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | JUMPER | 50514 | 20240202 | 1523 | 20240202 | 1646 | 2332892 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 787 | 65321 | 38.8385 | -121.3225 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Burned/flashed | 24-0018785 | OH | Sus | 31683277 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908675 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 34253 | 20240202 | 1650 | 20240202 | 1959 | 2333159 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 535 | 38.8748 | -121.1175 | No | Partly Cloudy;32-90 F |  |  | 24-0018842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908703 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5343 | 20240203 | 813 | 20240203 | 1458 | 2333432 | 405 | Distribution Circuit | Equipment Failure/Involved | Underground | 11 | 4322 | 38.8734 | -121.238 | No | Overcast;32-90 F | Elbow | Failed/Faulted | 24-0018933 | UG | Sus | 46178275 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1908833 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 32685 | 20240204 | 1023 | 20240204 | 1123 | 2337147 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 1260 | 38.8542 | -121.1917 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0019563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909431 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9991 | 20240204 | 1100 | 20240204 | 1503 | 2337719 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4860 | 38.9124 | -120.8292 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909630 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20240204 | 1245 | 20240204 | 1424 | 2339391 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 16434 | 38.7712 | -120.9325 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0019954 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909786 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20240204 | 1310 | 20240204 | 1357 | 2339783 | 47 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 802 | 37694 | 38.8695 | -121.02 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0019802 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1909646 | 0 | EPSS Ckt | N | 2024 | A B C TIME
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 55666 | 20240204 | 1328 | 20240207 | 1856 | 2340143 | 4648 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 348835 | 38.7296 | -121.0893 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019845 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1909683 | 0 | EPSS Ckt | N | 2024 | B C & GRD
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 39029 | 20240204 | 1331 | 20240204 | 1827 | 2340014 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2072 | 38.8259 | -121.1838 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0019965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909798 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 30089 | 20240204 | 1338 | 20240204 | 1438 | 2340181 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1080 | 38.7913 | -121.2364 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0019969 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909803 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | RECLOSER | 2222 | 20240204 | 1358 | 20240204 | 1533 | 2340864 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 329 | 31255 | 38.7708 | -121.2524 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0019947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909779 | 0 | Non-EPSS | N | 2024 | B & C
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20240204 | 1406 | 20240204 | 1737 | 2340980 | 211 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 16880 | 38.6542 | -121.0356 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910371 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20240204 | 1418 | 20240204 | 1718 | 2341327 | 180 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 7740 | 38.748 | -121.4698 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910098 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9987 | 20240204 | 1418 | 20240204 | 1702 | 2341326 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 3936 | 38.919 | -120.9164 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0020452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910278 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | FUSE | 30095 | 20240204 | 1420 | 20240207 | 1111 | 2341364 | 4131 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 444026 | 38.7671 | -121.154 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020290 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910119 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 8449 | 20240204 | 1430 | 20240204 | 1511 | 2341668 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 3854 | 38.8102 | -121.1961 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909926 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | OCB | 1103/2 | 20240204 | 1433 | 20240205 | 1045 | 2341764 | 1212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1313 | 1122912 | 38.7878 | -121.2314 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1909856 | 0 | Non-EPSS | N | 2024 | B GRD TIME
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20240204 | 1435 | 20240205 | 1138 | 2342197 | 1263 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 209658 | 38.7712 | -120.9325 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020207 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910033 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38885 | 20240204 | 1437 | 20240204 | 1640 | 2341854 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2091 | 38.8234 | -121.116 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0020375 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910203 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | OTHER | WIRE DOWN AT 5667 TWD TX | 20240204 | 1437 | 20240206 | 1801 | 2341839 | 3082 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1885 | 598563 | 38.9277 | -121.0751 | Yes | Partly Cloudy-Strong Winds;32-90 F | Jumper | Broken- wire on ground | 24-0020953 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1910773 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 12147 | 20240204 | 1441 | 20240204 | 1851 | 2341914 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 16500 | 38.7521 | -121.0505 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020646 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910465 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 166282 | 20240204 | 1442 | 20240207 | 1809 | 2342069 | 4527 | Distribution Circuit | Vegetation | Tree - fell into line | 1140 | 1175877 | 39.068 | -121.0335 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0020047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | No | No | 1909876 | 0 | EPSS Ckt | N | 2024 | A B C
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 7709 | 20240204 | 1447 | 20240206 | 1833 | 2365310 | 3106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 220526 | 39.0742 | -121.007 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0023639 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913043 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | OCB | 1101/2 | 20240204 | 1448 | 20240205 | 2319 | 2342172 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 979 | 893279 | 38.8902 | -121.0988 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1909897 | 0 | EPSS Ckt | N | 2024 | none
SIERRA | PLACER | LINCOLN-1105 | 153701105 | OCB | 1105/2 | 20240204 | 1450 | 20240204 | 1456 | 2342227 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1835 | 11010 | 38.9006 | -121.2943 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0020076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1909904 | 0 | Non-EPSS | N | 2024 | A C TIME
SIERRA | PLACER | CATLETT-1102 | 153761102 | OTHER | WIRE DOWN ELDERST AND LOWELL ST. | 20240204 | 1452 | 20240207 | 1519 | 2342232 | 4347 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 89967 | 38.7493 | -121.4779 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1910681 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 30089 | 20240204 | 1452 | 20240207 | 1704 | 2342216 | 4452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 80136 | 38.7913 | -121.2364 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910006 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18843 | 20240204 | 1453 | 20240204 | 1600 | 2344926 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 938 | 38.5359 | -120.6968 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0020310 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910139 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 685276 | 20240204 | 1453 | 20240207 | 1614 | 2342362 | 4401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 802247 | 38.9848 | -121.2917 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1909912 | 0 | EPSS Ckt | N | 2024 | B C GRD
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20240204 | 1459 | 20240207 | 2012 | 2342512 | 4630 | Distribution Circuit | Equipment Failure/Involved | Overhead | 675 | 2009619 | 38.9847 | -121.366 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020122 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1909951 | 0 | EPSS Ckt | N | 2024 | A-C-TIME OC -GRD
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7721 | 20240204 | 1459 | 20240207 | 2008 | 2359218 | 4629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 23145 | 39.0138 | -121.327 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1911624 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15319 | 20240204 | 1459 | 20240207 | 2009 | 2359658 | 4630 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 18520 | 38.9922 | -121.3167 | Yes | Overcast-Strong Winds;32-90 F | Insulator | Broken | 24-0021989 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1911710 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OJS 3 S/O 16223 | 20240204 | 1459 | 20240208 | 1914 | 2361033 | 6015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6015 | 38.9869 | -121.3165 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1912049 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6303 | 20240204 | 1500 | 20240204 | 1630 | 2342523 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 7470 | 39.0896 | -120.9657 | Yes | Overcast;32-90 F |  |  | 24-0020356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910184 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3729 | 20240204 | 1501 | 20240208 | 1802 | 2342491 | 5941 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 344578 | 39.1397 | -121.0574 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910223 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | FUSE | 5959 | 20240204 | 1501 | 20240206 | 1751 | 2355087 | 3050 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 134200 | 38.7432 | -121.1638 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0023683 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913082 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7671 | 20240204 | 1504 | 20240207 | 1455 | 2341174 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 189684 | 38.8956 | -121.4145 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0023414 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | No | No | 1912871 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2708 | 20240204 | 1506 | 20240209 | 1740 | 2342699 | 5726 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 226558 | 38.7961 | -121.1633 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020111 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1909940 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7553 | 20240204 | 1511 | 20240208 | 1327 | 2342845 | 5656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16968 | 38.7728 | -121.4233 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0026243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915113 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | ROCKLIN-1101 | 152061101 | FUSE | 30423 | 20240204 | 1514 | 20240207 | 2004 | 2342986 | 4610 | Distribution Circuit | Vegetation | Tree - fell into line | 321 | 475710 | 38.7878 | -121.2196 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021201 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911029 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2234 | 20240204 | 1518 | 20240208 | 1512 | 2347069 | 4045 | Distribution Circuit | Vegetation | Tree - fell into line | 1180 | 2002074 | 38.8956 | -121.1358 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0020448 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1910274 | 0 | EPSS Ckt | N | 2024 | A-B-C TIME OC GRD
SIERRA | PLACER | WISE-1102 | 152271102 | JUMPER | OJ'S @ CGC 222420845020 | 20240204 | 1518 | 20240208 | 1730 | 2359185 | 5892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 35352 | 38.9 | -121.1507 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911611 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222277146465 | 20240204 | 1518 | 20240209 | 1237 | 2361777 | 7039 | Transformer only | Vegetation | Tree - fell into line | 2 | 14078 | 38.9395 | -121.2008 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0022617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912244 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222367355612 | 20240204 | 1520 | 20240207 | 1319 | 2365619 | 4199 | Transformer only | Vegetation | Tree - fell into line | 1 | 4199 | 39.1903 | -121.1656 | Yes | Overcast;32-90 F | Service conductor | Broken | 24-0023746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913133 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 236062 | 20240204 | 1523 | 20240207 | 1748 | 2343408 | 4465 | Distribution Circuit | Vegetation | Tree - fell into line | 1502 | 1594401 | 38.7471 | -120.6442 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1910016 | 0 | EPSS Ckt | N | 2024 | A-B-C
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 31535 | 20240204 | 1525 | 20240207 | 1113 | 2343269 | 4068 | Distribution Circuit | Equipment Failure/Involved | Overhead | 110 | 447480 | 38.7923 | -121.2397 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910113 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | RECLOSER | 1252 | 20240204 | 1525 | 20240207 | 2045 | 2340660 | 4515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 638 | 845270 | 38.8967 | -121.4874 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020183 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1910009 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | OTHER | WIRE DOWN AT CGC 222350755826 | 20240204 | 1525 | 20240207 | 2032 | 2349154 | 4627 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 309131 | 39.1981 | -121.1704 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | Yes | 1910380 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | BURNED OPEN JUMPER SS OF FUCO 4261 | 20240204 | 1525 | 20240208 | 1508 | 2344049 | 5743 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 136424 | 39.1647 | -121.1509 | Yes | Overcast-Strong Winds;32-90 F | Jumper | Burned Open | 24-0020622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1910442 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 8551 | 20240204 | 1526 | 20240208 | 1800 | 2343327 | 5914 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 271135 | 38.7465 | -121.1707 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0023351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912826 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-1103 | 152581103 | RECLOSER | 2716 | 20240204 | 1527 | 20240205 | 1439 | 2343804 | 1392 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 98832 | 38.811 | -121.2075 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020268 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910097 | 0 | EPSS Ckt | N | 2024 | B GRD
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222308742326 | 20240204 | 1530 | 20240209 | 1305 | 2360884 | 7055 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 7055 | 38.8259 | -121.1906 | Yes | Strong Winds-Clear;32-90 F | Transformer | Failed/Faulted | 24-0022362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912014 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 30239 | 20240204 | 1530 | 20240206 | 1059 | 2361101 | 2609 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 26090 | 38.8325 | -121.1869 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022413 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912063 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN 1101 | 152161101 | TRANSFORMER | 222667944871 | 20240204 | 1531 | 20240204 | 1805 | 2344074 | 154 | Transformer only | Vegetation | Tree - bark fell into line | 7 | 1078 | 38.8949 | -121.0637 | Yes | Strong Winds-Partly Cloudy-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0020600 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910420 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1101 | 152161101 | TRANSFORMER | 222664544880 | 20240204 | 1531 | 20240207 | 2026 | 2357177 | 4615 | Transformer only | Vegetation | Tree - fell into line | 7 | 32305 | 38.8951 | -121.0649 | Yes | Strong Winds-Partly Cloudy-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0022564 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912191 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 19910 | 20240204 | 1532 | 20240205 | 1124 | 2343724 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 505408 | 38.6313 | -120.8542 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Service conductor | Broken | 24-0020260 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910089 | 0 | EPSS Ckt | N | 2024 | BC
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222753854067 | 20240204 | 1535 | 20240208 | 1841 | 2359383 | 5946 | Transformer only | Vegetation | Tree - fell into line | 1 | 5946 | 39.1469 | -121.0304 | Yes | Overcast-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 24-0021925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911656 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 98319 | 20240204 | 1536 | 20240204 | 1910 | 2343899 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 15987 | 38.9311 | -121.0956 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0020559 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910382 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | OCB | 1106/2 | 20240204 | 1536 | 20240207 | 1657 | 2343779 | 2557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2061 | 4068561 | 38.8448 | -121.1664 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0020223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910049 | 0 | EPSS Ckt | N | 2024 | GRD & INST OC
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 5281 | 20240204 | 1536 | 20240209 | 1258 | 2352101 | 7042 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 119714 | 38.8362 | -121.1807 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1910635 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 5055 | 20240204 | 1536 | 20240207 | 1427 | 2360333 | 4251 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 361335 | 38.8166 | -121.1989 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911854 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 35247 | 20240204 | 1536 | 20240207 | 1139 | 2361175 | 4083 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 62637 | 38.8393 | -121.1744 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0022447 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912089 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 31571 | 20240204 | 1538 | 20240208 | 1938 | 2358794 | 6000 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10764 | 38.8107 | -121.1931 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911528 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20240204 | 1538 | 20240207 | 1800 | 2344134 | 4462 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 1350175 | 38.9732 | -121.0141 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020252 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910081 | 0 | EPSS Ckt | N | 2024 | B C TIME
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222863949097 | 20240204 | 1538 | 20240207 | 1705 | 2360337 | 4407 | Transformer only | Vegetation | Tree - fell into line | 2 | 8814 | 39.0104 | -120.9934 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Secondary | Broken | 24-0022180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911856 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6123 | 20240204 | 1538 | 20240207 | 2018 | 2360382 | 4600 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 349600 | 38.9793 | -121.0075 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911873 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 31719 | 20240204 | 1539 | 20240208 | 1448 | 2360293 | 5709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 39963 | 38.9922 | -120.9985 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0022168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911846 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 3533 | 20240204 | 1540 | 20240207 | 1711 | 2344062 | 4411 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 44110 | 39.0175 | -121.0603 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021009 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910831 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 9503 | 20240204 | 1540 | 20240209 | 1743 | 2344101 | 7323 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 44406 | 39.056 | -120.9978 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910297 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20240204 | 1543 | 20240206 | 1114 | 2344396 | 2611 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 168929 | 39.0715 | -120.9763 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912609 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | RECLOSER | 6128 | 20240204 | 1546 | 20240208 | 1320 | 2344735 | 5609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1123 | 2193468 | 38.8246 | -121.3507 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910146 | 0 | Non-EPSS | N | 2024 | C - GRD
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | TRANSFORMER | 221728342485 | 20240204 | 1546 | 20240209 | 1425 | 2365699 | 7119 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 21357 | 38.8317 | -121.3939 | Yes | Overcast-Drizzle;32-90 F | Transformer | Deteriorated | 24-0023785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913166 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | TRANSFORMER | 222397739692 | 20240204 | 1549 | 20240209 | 1352 | 2344587 | 7083 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 21249 | 38.7534 | -121.1601 | Yes | Strong Winds-Clear;32-90 F | Transformer | Broken | 24-0023885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913256 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31153 | 20240204 | 1551 | 20240209 | 1808 | 2344612 | 7337 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8297 | 38.8427 | -120.8271 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020910 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910729 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7225 | 20240204 | 1551 | 20240205 | 1908 | 2344682 | 1637 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 54 | 88398 | 38.9944 | -121.3972 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0022671 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912306 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 173478 | 20240204 | 1553 | 20240205 | 1542 | 2345101 | 1429 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 168622 | 39.0043 | -121.0288 | Yes | Clear-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910165 | 0 | EPSS Ckt | N | 2024 | C GRD TIME OC
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8483 | 20240204 | 1553 | 20240207 | 1607 | 2358836 | 4334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 316382 | 39.0185 | -121.0227 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021793 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911544 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 4763 | 20240204 | 1553 | 20240205 | 1542 | 2359807 | 1429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 32867 | 39.0194 | -121.0298 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0022023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911738 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5781 | 20240204 | 1553 | 20240206 | 1335 | 2359833 | 2742 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 296136 | 39.0181 | -121.0298 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911741 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | OJ AT CGC 222759049555 | 20240204 | 1553 | 20240209 | 1539 | 2360668 | 7186 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 57488 | 39.0231 | -121.03 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911953 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7767 | 20240204 | 1554 | 20240207 | 1816 | 2344747 | 4462 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 116012 | 39.1996 | -121.1929 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910412 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 215201 | 20240204 | 1556 | 20240209 | 1851 | 2364030 | 7375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 109427 | 38.7512 | -121.4391 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1913035 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | OCB | 1105/2 | 20240204 | 1556 | 20240207 | 1637 | 2344925 | 4361 | Distribution Circuit | Vegetation | Tree - fell into line | 1837 | 1769236 | 38.9006 | -121.2943 | Yes | Clear-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910148 | 0 | Non-EPSS | N | 2024 | A C TIME
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 16155 | 20240204 | 1556 | 20240207 | 1612 | 2357383 | 4336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 8061 | 38.8681 | -121.3593 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911365 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1374 | 20240204 | 1557 | 20240209 | 1409 | 2345212 | 7092 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 3178058 | 39.0987 | -121.0518 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1910198 | 0 | EPSS Ckt | N | 2024 | A B C TIME OC
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | JUMPER | OJ 1 POLE LD SD OF SB 6875 | 20240204 | 1557 | 20240209 | 1752 | 2351068 | 7315 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 80465 | 39.1041 | -121.0591 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1910545 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | TRANSFORMER | 222372640188 | 20240204 | 1559 | 20240207 | 1138 | 2345416 | 4059 | Transformer only | Vegetation | Tree - branch fell on line | 5 | 20295 | 38.767 | -121.1688 | Yes | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913439 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 583890 | 20240204 | 1602 | 20240204 | 1804 | 2345146 | 122 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3904 | 38.6772 | -120.7472 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910417 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20240204 | 1603 | 20240205 | 1857 | 2345237 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 7206 | 38.6196 | -120.7647 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910512 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20240204 | 1609 | 20240208 | 1655 | s1910200 | 5799 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 1029291 | 38.8543 | -121.1728 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910200 | 0 | EPSS Ckt | N | 2024 | A B
SIERRA | PLACER | BELL-1108 | 152701108 | OCB | 1108/2 | 20240204 | 1612 | 20240205 | 2105 | 2345847 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 3431 | 3903479 | 38.947 | -121.0912 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1910172 | 0 | EPSS Ckt | N | 2024 | A-B-C TIME OC
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 39511 | 20240204 | 1612 | 20240208 | 1252 | 2360630 | 5560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 55600 | 38.9664 | -121.104 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0020344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911941 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 5763 | 20240204 | 1612 | 20240207 | 1546 | 2360650 | 4294 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 94468 | 38.9747 | -121.1072 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911949 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222616448158 | 20240204 | 1612 | 20240208 | 1550 | 2362126 | 5738 | Transformer only | Vegetation | Tree - fell into line | 2 | 11476 | 38.9851 | -121.0809 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Secondary | Broken | 24-0022722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912357 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 37061 | 20240204 | 1614 | 20240204 | 2119 | 2345750 | 305 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 7625 | 38.8005 | -121.02 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0020466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910292 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222611248305 | 20240204 | 1616 | 20240208 | 1612 | 2354738 | 5756 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 11512 | 38.9892 | -121.0827 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0021106 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1910929 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 30845 | 20240204 | 1618 | 20240209 | 1820 | 2345995 | 7322 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 128350 | 39.0929 | -120.9445 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1913578 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 20240204 | 1619 | 20240208 | 1612 | 2346047 | 5753 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 46024 | 38.9807 | -120.9404 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911928 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ @ 222343356030 | 20240204 | 1623 | 20240209 | 1445 | 2365039 | 7102 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 42612 | 39.2024 | -121.1742 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023585 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912993 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6053 | 20240204 | 1624 | 20240206 | 1151 | 2346301 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 117820 | 38.84 | -120.8753 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910524 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2140 | 20240204 | 1626 | 20240209 | 1145 | 2347868 | 5458 | Distribution Circuit | Vegetation | Tree - fell into line | 1411 | 2804549 | 39.2895 | -120.9854 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020479 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910303 | 0 | EPSS Ckt | N | 2024 | B - C
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 33351 | 20240204 | 1627 | 20240205 | 1049 | 2358562 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 37468 | 38.7983 | -121.2287 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0021723 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911488 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 33347 | 20240204 | 1630 | 20240205 | 1049 | 2358294 | 1099 | Distribution Circuit | Vegetation | Tree - branch fell on line | 220 | 241780 | 38.7998 | -121.2394 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911447 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 8787 | 20240204 | 1630 | 20240209 | 1410 | 2352244 | 7060 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 41700 | 38.8804 | -121.2379 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910649 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20240204 | 1634 | 20240207 | 1134 | 2346933 | 4020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1146 | 1491413 | 39.2034 | -121.0788 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020495 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910319 | 0 | EPSS Ckt | N | 2024 | INST C GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7835 | 20240204 | 1634 | 20240209 | 1457 | 2350854 | 7103 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 160085 | 39.1992 | -121.0863 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910522 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222438744395 | 20240204 | 1634 | 20240205 | 2012 | 2361994 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6632 | 38.8823 | -121.1443 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Secondary | Normal | 24-0022670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912305 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20240204 | 1637 | 20240206 | 1813 | 2365167 | 2976 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 175584 | 39.1894 | -120.9612 | Yes | Overcast-Fog;32-90 F |  |  | 24-0023710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913102 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20240204 | 1638 | 20240206 | 1115 | 2351372 | 2557 | Distribution Circuit | Equipment Failure/Involved | Overhead | 271 | 689295 | 38.887 | -121.2381 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910578 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 744292 | 20240204 | 1639 | 20240205 | 1958 | 2361991 | 1639 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 123 | 201597 | 38.8941 | -121.2922 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0020759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912316 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1102 | 153701102 | OCB | 1102/2 | 20240204 | 1639 | 20240207 | 1659 | 2348464 | 4340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3311 | 4922393 | 38.9006 | -121.2942 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0020522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1910345 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9403 | 20240204 | 1639 | 20240208 | 1645 | 2350551 | 5766 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 386322 | 38.9264 | -121.2465 | Yes | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020676 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1910495 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 9457 | 20240204 | 1639 | 20240209 | 1650 | 2355596 | 7211 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 1293493 | 38.9014 | -121.1816 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1911092 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20240204 | 1644 | 20240205 | 1026 | 2347360 | 1062 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 56286 | 38.8428 | -121.029 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910419 | 0 | EPSS Ckt | N | 2024 | A-B
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222149156125 | 20240204 | 1644 | 20240207 | 1353 | 2360381 | 4149 | Transformer only | Vegetation | Tree - fell into line | 1 | 4149 | 39.205 | -121.2429 | Yes | Clear-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 24-0022199 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911870 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5085 | 20240204 | 1644 | 20240205 | 1616 | 2360953 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 101664 | 38.7933 | -121.1712 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020111 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912025 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5381 | 20240204 | 1644 | 20240207 | 1934 | 2359931 | 4490 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 166130 | 38.9235 | -121.1807 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1911759 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | FUSE | 5773 | 20240204 | 1645 | 20240207 | 1205 | 2347151 | 4040 | Distribution Circuit | 3rd Party | Kite | 39 | 157560 | 39.0112 | -121.1042 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0024139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913401 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5461 | 20240204 | 1648 | 20240209 | 1247 | 2357781 | 6959 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 69590 | 38.9085 | -121.2688 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021575 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911390 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | TRANSFORMER | 222410239966 | 20240204 | 1651 | 20240207 | 1300 | 2351404 | 4089 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 16356 | 38.7609 | -121.1557 | Yes | Clear-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0024292 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913495 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20240204 | 1652 | 20240209 | 1325 | 2347833 | 6993 | Distribution Circuit | Vegetation | Tree - fell into line | 3667 | 6576077 | 39.1995 | -121.017 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910362 | 0 | EPSS Ckt | N | 2024 | B G SGF
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222932054852 | 20240204 | 1652 | 20240209 | 1018 | 2361110 | 6806 | Transformer only | Vegetation | Tree - fell into line | 3 | 20418 | 39.1684 | -120.9675 | Yes | Overcast-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 24-0022419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912067 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6697 | 20240204 | 1652 | 20240207 | 2023 | 2362000 | 4531 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 126868 | 39.1942 | -120.9935 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0022674 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912309 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 31249 | 20240204 | 1652 | 20240209 | 1345 | 2362205 | 7013 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 98182 | 39.1913 | -120.9959 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912400 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20240204 | 1652 | 20240207 | 1404 | 2364057 | 4152 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 232512 | 39.1731 | -120.9738 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0023248 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912747 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ 3 SS OF CGC 222998054815 | 20240204 | 1652 | 20240209 | 1228 | 2364739 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6936 | 39.1682 | -120.9427 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912921 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | SHADY GLEN-1102 | 152431102 | FUSE | 8951 | 20240204 | 1652 | 20240206 | 1637 | 2365109 | 2865 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 20055 | 39.1794 | -120.976 | Yes | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0023605 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913009 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4705 | 20240204 | 1655 | 20240207 | 1237 | 2364879 | 4062 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 56868 | 39.1879 | -121.2035 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0023539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912957 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | JUMPER | OJ @ CGC 222692358318 | 20240204 | 1656 | 20240208 | 1601 | 2360955 | 5705 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34230 | 39.2641 | -121.0501 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912028 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 943883 | 20240204 | 1659 | 20240205 | 1626 | 2359823 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 97083 | 39.2667 | -121.0539 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022025 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911740 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38885 | 20240204 | 1700 | 20240207 | 947 | 2360233 | 3887 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 66079 | 38.8234 | -121.116 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0022150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911830 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5407 | 20240204 | 1700 | 20240209 | 1813 | 2348094 | 7273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 58184 | 38.898 | -121.0954 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0023721 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1913114 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | JUMPER | OJ'S @ CGC 222476045018 TWD EOL | 20240204 | 1700 | 20240209 | 2123 | 2366718 | 7463 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 34136 | 38.8999 | -121.1307 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024076 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1913363 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 3675 | 20240204 | 1702 | 20240206 | 1446 | 2347973 | 2744 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 43904 | 39.0552 | -121.1498 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0023497 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912924 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222653247738 | 20240204 | 1704 | 20240209 | 1141 | 2348305 | 6877 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 13754 | 38.9736 | -121.0682 | Yes | Strong Winds-Partly Cloudy-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0024567 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913644 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | OTHER | BROKEN POLE WIRE DOWN AT CGC 222147855827 | 20240204 | 1705 | 20240207 | 1948 | 2348090 | 4483 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 71466 | 39.1973 | -121.2439 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1910840 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5783 | 20240204 | 1706 | 20240206 | 2052 | 2348122 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 338554 | 38.9562 | -121.0712 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022272 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911924 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 8637 | 20240204 | 1708 | 20240205 | 2030 | 2348171 | 1642 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 75532 | 38.9053 | -121.0693 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0022696 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912330 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | FUSE | 5951 | 20240204 | 1709 | 20240206 | 1414 | 2348185 | 2705 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 159595 | 38.7451 | -121.1585 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912901 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38849 | 20240204 | 1713 | 20240205 | 1616 | 2360207 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7427 | 38.8114 | -121.13 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911827 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 38605 | 20240204 | 1713 | 20240208 | 1827 | 2357554 | 5834 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17502 | 38.893 | -121.1121 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0023790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1913171 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3689 | 20240204 | 1718 | 20240207 | 1603 | 2368129 | 4245 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 29715 | 39.261 | -121.1929 | Yes | Clear;32-90 F |  |  | 24-0024519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913612 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 5377 | 20240204 | 1719 | 20240206 | 2034 | 2348508 | 3075 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 144525 | 38.9408 | -121.1445 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023748 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913134 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20240204 | 1722 | 20240209 | 1048 | 2348718 | 6590 | Distribution Circuit | Vegetation | Tree - fell into line | 719 | 1024705 | 39.2132 | -121.0136 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0020958 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1910778 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9789 | 20240204 | 1723 | 20240208 | 1636 | 2348717 | 5713 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 148538 | 39.212 | -121.0191 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0020614 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1910435 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7585 | 20240204 | 1726 | 20240207 | 1211 | 2348836 | 4005 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 68085 | 38.7722 | -121.4512 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913260 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20240204 | 1729 | 20240208 | 2006 | 2349137 | 5704 | Distribution Circuit | Vegetation | Tree - fell into line | 3639 | 6793777 | 39.2082 | -121.2033 | Yes | Overcast-Rain-Strong Winds;32-90 F | Switch (OH) | Broken- wire on ground | 24-0020688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1910508 | 0 | EPSS Ckt | N | 2024 | A - B - C
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222483249986 | 20240204 | 1732 | 20240207 | 808 | 2349113 | 3756 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 7512 | 39.0347 | -121.1265 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0023980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913316 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6341 | 20240204 | 1732 | 20240206 | 1627 | 2349359 | 2815 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 109785 | 39.125 | -120.9435 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0021241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911070 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | OCB | 2109/2 | 20240204 | 1732 | 20240204 | 2236 | 2349365 | 304 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3488 | 870500 | 38.6597 | -120.947 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0020653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910473 | 0 | EPSS Ckt | N | 2024 | A-C TIME
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223056537915 | 20240204 | 1732 | 20240207 | 1710 | 2354959 | 4298 | Transformer only | Vegetation | Tree - fell into line | 2 | 8596 | 38.7038 | -120.9303 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0021154 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910979 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33241 | 20240204 | 1733 | 20240206 | 1823 | 2354271 | 2930 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 26370 | 39.1274 | -120.9453 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910856 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ AT CGC 222980153417 | 20240204 | 1733 | 20240208 | 1548 | 2365514 | 5655 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 50895 | 39.1287 | -120.9504 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023708 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913100 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 32033 | 20240204 | 1734 | 20240209 | 1318 | 2349436 | 6944 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 39920 | 39.0016 | -120.8905 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 24-0021722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911487 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 9617 | 20240204 | 1742 | 20240207 | 953 | 2349551 | 3851 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 103977 | 38.7769 | -121.191 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0024062 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913358 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 38353 | 20240204 | 1744 | 20240206 | 1636 | 2362164 | 2812 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 78736 | 39.2011 | -121.171 | Yes | Overcast-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0022738 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912373 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20240204 | 1746 | 20240206 | 1600 | 2349646 | 2774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 81151 | 38.7309 | -120.8421 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911481 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1449 | 20240204 | 1749 | 20240206 | 1419 | 2349673 | 2670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 71559 | 38.7543 | -120.7732 | Yes | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0021589 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911399 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18543 | 20240204 | 1759 | 20240205 | 917 | 2350014 | 918 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 14688 | 38.7517 | -120.6921 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911404 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 9957 | 20240204 | 1800 | 20240207 | 2038 | 2350049 | 4478 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 143296 | 38.9987 | -121.0098 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020854 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910673 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5671 | 20240204 | 1806 | 20240208 | 1058 | 2350237 | 5332 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 285028 | 38.9203 | -121.0865 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022651 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912284 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | OCB | 1101/2 | 20240204 | 1808 | 20240207 | 2022 | 2350348 | 4454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2081 | 1262428 | 38.8853 | -121.0674 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0020658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1910478 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 9123 | 20240204 | 1809 | 20240208 | 1830 | 2350270 | 5781 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 75153 | 39.2845 | -121.0567 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912169 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | RECLOSER | 930180 | 20240204 | 1813 | 20240204 | 2058 | 2350716 | 165 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 1485 | 38.7516 | -121.4321 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0021030 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1910853 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 7571 | 20240204 | 1819 | 20240208 | 1259 | 2350582 | 5440 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 163200 | 38.9985 | -120.8694 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021811 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911558 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20240204 | 1822 | 20240208 | 1529 | 2350650 | 5587 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 121717 | 38.748 | -121.4698 | Yes | Partly Cloudy-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 24-0023566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912975 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 6241 | 20240204 | 1825 | 20240208 | 1126 | 2350765 | 5341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 127348 | 39.0289 | -121.0036 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913042 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | RECLOSER | 91288 | 20240204 | 1830 | 20240206 | 1033 | 2352009 | 1256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2855 | 3433742 | 38.655 | -120.9992 | Yes | Clear-Strong Winds;32-90 F | Insulator | Burned/flashed | 24-0020977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910798 | 0 | EPSS Ckt | N | 2024 | A-C-GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 35369 | 20240204 | 1834 | 20240207 | 1000 | 2351150 | 3806 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 670103 | 39.238 | -120.9727 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Deteriorated | 24-0023757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913141 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 20240204 | 1837 | 20240205 | 1332 | 2351159 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 30282 | 39.0098 | -120.8455 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 24-0021929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911661 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | OCB | 1103/2 | 20240204 | 1838 | 20240208 | 1638 | 2351235 | 5640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2871 | 2885929 | 39.0444 | -121.0912 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911051 | 0 | EPSS Ckt | N | 2024 | INST OC- SGF- GRD
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 34655 | 20240204 | 1845 | 20240206 | 2009 | 2352017 | 2964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 74100 | 38.7488 | -121.177 | Yes | Clear-Strong Winds;32-90 F | Lightning Arrestor | Broken | 24-0023740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913128 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 20240204 | 1853 | 20240209 | 846 | 2351552 | 6593 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1165 | 3206443 | 39.3313 | -121.1015 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910623 | 0 | EPSS Ckt | N | 2024 | B-C INST OC
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 21873 | 20240204 | 1854 | 20240205 | 957 | 2351519 | 903 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 69531 | 38.7228 | -121.0138 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911499 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 5949 | 20240204 | 1856 | 20240209 | 1235 | 2351538 | 6819 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 158693 | 38.7432 | -121.1613 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0023515 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912937 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4579 | 20240204 | 1900 | 20240208 | 1116 | 2364590 | 5296 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 301872 | 39.1908 | -121.1827 | Yes | Overcast-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0023439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912884 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6893 | 20240204 | 1904 | 20240208 | 1159 | 2358155 | 5335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 26675 | 39.1462 | -121.0309 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911427 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 4219 | 20240204 | 1904 | 20240208 | 1320 | 2359397 | 5416 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 482024 | 39.1549 | -121.0265 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021927 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911658 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | OTHER | 222783857282 | 20240204 | 1907 | 20240208 | 1922 | 2364912 | 5775 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 100715 | 39.2351 | -121.0187 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023555 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1912969 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6139 | 20240204 | 1908 | 20240208 | 1446 | 2352044 | 5498 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 80928 | 39.066 | -120.9803 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912771 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 20240204 | 1911 | 20240205 | 1631 | 2352144 | 1280 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 225280 | 38.9133 | -120.9318 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910717 | 0 | EPSS Ckt | N | 2024 | A LOCKOUT
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20240204 | 1915 | 20240205 | 2121 | 2357805 | 1566 | Distribution Circuit | Vegetation | Tree - fell into line | 998 | 1098510 | 38.8154 | -120.8221 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911394 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 1/P/E OF CGC 223271242720 | 20240204 | 1915 | 20240208 | 1716 | 2364891 | 5639 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5804 | 38.8348 | -120.8532 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912963 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | RECLOSER | 946229 | 20240204 | 1919 | 20240208 | 1412 | 2352879 | 5453 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 29953 | 38.9274 | -121.1027 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910705 | 0 | EPSS Ckt | N | 2024 | B
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7105 | 20240204 | 1921 | 20240208 | 1801 | 2352531 | 5680 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 532240 | 39.2847 | -121.0584 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022530 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912159 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 8327 | 20240204 | 1924 | 20240208 | 1458 | 2349037 | 5494 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 252724 | 39.2447 | -121.07 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1915045 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6155 | 20240204 | 1928 | 20240208 | 1353 | 2352683 | 5425 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 151900 | 39.0105 | -120.9802 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0023680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1913079 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 2718 | 20240204 | 1929 | 20240207 | 1843 | 2352798 | 4274 | Distribution Circuit | Vegetation | Tree - fell into line | 1169 | 2153746 | 39.2349 | -121.2209 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911138 | 0 | EPSS Ckt | N | 2024 | A - C - TIME
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222178157916 | 20240204 | 1929 | 20240209 | 834 | 2352713 | 6545 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6545 | 39.2541 | -121.2314 | Yes | Strong Winds-Clear;32-90 F | Transformer | Broken- wire on ground | 24-0022800 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912434 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7231 | 20240204 | 1929 | 20240206 | 2035 | 2362140 | 2946 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8838 | 39.2323 | -121.1121 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Broken | 24-0022727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912362 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 31487 | 20240204 | 1929 | 20240207 | 1006 | 2364874 | 3757 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 93925 | 39.1978 | -121.2133 | Yes | Clear;32-90 F |  |  | 24-0023537 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912955 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7263 | 20240204 | 1931 | 20240208 | 1724 | 2352952 | 5633 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 163680 | 39.2147 | -121.0803 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912655 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32285 | 20240204 | 1933 | 20240206 | 2155 | 2352808 | 3022 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 81594 | 39.2286 | -121.0968 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0023835 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913210 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF CGC 223399739220 | 20240204 | 1933 | 20240206 | 1453 | 2354344 | 2600 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17850 | 38.7377 | -120.8089 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1910874 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6185 | 20240204 | 1933 | 20240206 | 1408 | 2352513 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 27469 | 39.0561 | -120.9817 | Yes | Overcast-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0023416 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912872 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4703 | 20240204 | 1934 | 20240207 | 1504 | 2364881 | 4050 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 141750 | 39.1865 | -121.202 | Yes | Clear;32-90 F | Secondary | Broken | 24-0023543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912960 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 38371 | 20240204 | 1934 | 20240208 | 1146 | 2352829 | 5292 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 127008 | 39.4746 | -121.033 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0023303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912789 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ AT CGC 222642053414 TWD HARD TAP | 20240204 | 1940 | 20240209 | 1449 | 2355248 | 6909 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20727 | 39.1292 | -121.0698 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911041 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 7279 | 20240204 | 1942 | 20240207 | 1838 | 2352961 | 4256 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 846944 | 39.2143 | -121.054 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022125 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911812 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31961 | 20240204 | 1943 | 20240205 | 1453 | 2352963 | 1150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 25300 | 39.0205 | -120.8162 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022214 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911882 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 6837 | 20240204 | 1946 | 20240207 | 1457 | 2353086 | 4031 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 205145 | 38.9977 | -121.0232 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912909 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11859 | 20240204 | 1950 | 20240206 | 1845 | 2353150 | 2815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 219570 | 38.6748 | -120.9573 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0021641 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911433 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4599 | 20240204 | 1951 | 20240207 | 1051 | 2364884 | 3780 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 83160 | 39.1816 | -121.1961 | Yes | Clear;32-90 F |  |  | 24-0023545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912962 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 18309 | 20240204 | 1955 | 20240206 | 1657 | 2360988 | 2702 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 75694 | 38.8458 | -121.482 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Insulator | Broken | 24-0022379 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912031 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 3289 | 20240204 | 2000 | 20240206 | 1330 | 2353355 | 2490 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 67230 | 39.0485 | -121.0594 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0023403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912865 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13739 | 20240204 | 2003 | 20240205 | 928 | 2355857 | 805 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 38640 | 38.6002 | -120.6709 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0021651 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911440 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31037 | 20240204 | 2020 | 20240206 | 1522 | 2351604 | 2582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 7746 | 38.9311 | -120.9039 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023442 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912887 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | RECLOSER | 1826 | 20240204 | 2039 | 20240205 | 2202 | 2353950 | 1523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 771 | 1174233 | 38.7523 | -121.1933 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022681 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912317 | 0 | EPSS Ckt | N | 2024 | A - B
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223687139291 | 20240204 | 2043 | 20240205 | 938 | 2354021 | 775 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 8525 | 38.7381 | -120.7085 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1911489 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 3555 | 20240204 | 2054 | 20240209 | 1409 | 2358982 | 6795 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 74745 | 39.173 | -121.094 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021822 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911568 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 41415 | 20240204 | 2056 | 20240206 | 1157 | 2354243 | 2341 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 25751 | 39.132 | -121.0472 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0023296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912783 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9571 | 20240204 | 2057 | 20240209 | 1719 | 2360868 | 6982 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27928 | 39.2184 | -120.9641 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912011 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 7541 | 20240204 | 2104 | 20240206 | 1312 | 2354389 | 2408 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 77056 | 39.2752 | -120.9619 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0023400 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912863 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 37539 | 20240204 | 2106 | 20240209 | 1529 | 2359127 | 6863 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 13726 | 39.2798 | -120.9348 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023460 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912900 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7101 | 20240204 | 2107 | 20240208 | 1554 | 2359806 | 5447 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 968770 | 39.2691 | -121.0572 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911737 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 591351 | 20240204 | 2138 | 20240206 | 1337 | 2356847 | 2399 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 132811 | 39.3222 | -120.3792 | Yes | Snow-Strong Winds |  |  | 24-0023384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912850 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 9543 | 20240204 | 2140 | 20240207 | 1536 | 2358139 | 3956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1334 | 410844 | 39.1408 | -121.0528 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0021631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1911428 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 34701 | 20240204 | 2143 | 20240205 | 1951 | 2351154 | 1328 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 35856 | 39.1468 | -120.9002 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0022699 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912333 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4483 | 20240204 | 2146 | 20240205 | 946 | 2354985 | 720 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 25200 | 38.9059 | -120.9756 | Yes | Overcast-Strong Winds;32-90 F |  |  | 24-0021728 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1911492 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 30665 | 20240204 | 2148 | 20240205 | 1740 | 2355062 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8344 | 38.9094 | -121.0916 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Secondary | Broken | 24-0022502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912139 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 5609 | 20240204 | 2200 | 20240206 | 1624 | 2355107 | 2544 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 145008 | 38.9365 | -121.0951 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0023586 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912994 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5791 | 20240204 | 2203 | 20240207 | 1828 | 2355108 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 233985 | 39.0075 | -121.0402 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912814 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | SHADY GLEN-1101 | 152431101 | FUSE | 8305 | 20240204 | 2204 | 20240208 | 1138 | 2355138 | 5134 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 66742 | 39.0883 | -120.9922 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912241 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20240204 | 2208 | 20240205 | 1740 | 2355575 | 1172 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 59772 | 39.0543 | -120.7583 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0022465 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912104 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222656756790 | 20240204 | 2212 | 20240209 | 1708 | 2352900 | 6896 | Transformer only | Vegetation | Tree - fell into line | 9 | 62064 | 39.2223 | -121.0633 | Yes | Overcast-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912846 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 32741 | 20240204 | 2219 | 20240208 | 1550 | 2355240 | 5371 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 220211 | 39.1444 | -121.0626 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022283 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911935 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240204 | 2222 | 20240208 | 1410 | s1911859 | 5268 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 311064 | 39.1986 | -121.0343 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1911859 | 0 | EPSS Ckt | N | 2024 | A-B-C
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10321 | 20240204 | 2230 | 20240206 | 1023 | 2355520 | 2153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 193770 | 38.8032 | -120.9308 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911473 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 34489 | 20240204 | 2242 | 20240206 | 1529 | 2355499 | 2447 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 85645 | 39.3122 | -120.5012 | Yes | Overcast-Snow-Strong Winds;Below 32 F |  |  | 24-0023533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912951 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 2112 | 20240204 | 2253 | 20240205 | 1315 | 2355539 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 194812 | 39.2413 | -121.0566 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken | 24-0021344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911178 | 0 | EPSS Ckt | N | 2024 | B / GRD
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRIP-SAVER | 34069 | 20240204 | 2259 | 20240205 | 1951 | 2355548 | 1252 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 171 | 214092 | 39.2028 | -121.2764 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0022668 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912303 | 0 | EPSS Ckt | N | 2024 | A & B
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 2208 | 20240204 | 2323 | 20240207 | 1958 | 2354808 | 4053 | Distribution Circuit | Equipment Failure/Involved | Overhead | 403 | 983002 | 39.1986 | -121.0634 | Yes | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1911180 | 0 | EPSS Ckt | N | 2024 | A-B-C
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 32573 | 20240205 | 219 | 20240209 | 1820 | 2357879 | 6721 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6721 | 39.2129 | -121.0583 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1913412 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 31833 | 20240205 | 257 | 20240208 | 1410 | 2356420 | 4993 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 34951 | 39.2693 | -120.9941 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023588 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912996 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | OCB | 1107/2 | 20240205 | 507 | 20240207 | 1112 | 2356899 | 3245 | Distribution Circuit | Environmental/External | Lightning | 1710 | 515182 | 39.0444 | -121.091 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1911332 | 0 | EPSS Ckt | N | 2024 | A B C TOC
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 37579 | 20240205 | 559 | 20240209 | 1422 | 2363254 | 6263 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 87682 | 38.8244 | -121.4606 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 24-0026896 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1915549 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 30151 | 20240205 | 708 | 20240206 | 1144 | 2357353 | 1716 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 193908 | 38.7387 | -121.1707 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0023226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912732 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222991058975 | 20240205 | 714 | 20240206 | 1705 | 2357396 | 2031 | Transformer only | Vegetation | Tree - fell into line | 4 | 8124 | 39.2815 | -120.9447 | No | Overcast-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0023652 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913061 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 309031 | 20240205 | 750 | 20240208 | 1336 | 2357281 | 4666 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 158644 | 38.767 | -121.1602 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0021592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1911401 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222186055912 | 20240205 | 801 | 20240208 | 1543 | 2357755 | 4782 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4782 | 39.1995 | -121.2301 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0024334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913521 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OJS 1 SS/OF CGC 221719445965 | 20240205 | 819 | 20240209 | 1700 | 2357901 | 6281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6281 | 38.9264 | -121.3975 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0027095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1915645 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 30617 | 20240205 | 845 | 20240207 | 2120 | 2348293 | 3635 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 61795 | 38.9632 | -121.1496 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021854 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911593 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | TRANSFORMER | 221863144663 | 20240205 | 845 | 20240209 | 1150 | s1915565 | 5945 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5945 | 38.8913 | -121.3463 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1915565 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 51349 | 20240205 | 846 | 20240206 | 940 | 2358117 | 1494 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1494 | 38.9403 | -121.1077 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0023074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912637 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 898212 | 20240205 | 906 | 20240207 | 1955 | 2359784 | 3529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 458770 | 39.0994 | -120.9559 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0023055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1912626 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 18759 | 20240205 | 1024 | 20240205 | 1444 | 2359755 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 5714 | 38.6598 | -121.0006 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0022195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911867 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222516151850 | 20240205 | 1107 | 20240206 | 1002 | 2363572 | 1375 | Transformer only | Vegetation | Tree - fell into line | 1 | 1375 | 39.0868 | -121.1148 | No | Partly Cloudy;32-90 F | Secondary | Broken- wire on ground | 24-0023138 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912673 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 100000062320 | 20240205 | 1134 | 20240207 | 2024 | 2359266 | 3410 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 10230 | 39.0405 | -121.0576 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) |  | 24-0024728 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913768 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222598052955 | 20240205 | 1143 | 20240208 | 1855 | 2359328 | 4752 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9504 | 39.117 | -121.0856 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913085 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7595 | 20240205 | 1304 | 20240207 | 1844 | 2359826 | 3178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 6408 | 38.8243 | -121.45 | No | Overcast;32-90 F |  |  | 24-0024629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913691 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | OTHER | WIRE DOWN 1 LD SIDE 604920 | 20240205 | 1313 | 20240209 | 1241 | 2364100 | 5728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 108832 | 39.3082 | -120.5402 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0023257 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912754 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 3457 | 20240205 | 1531 | 20240207 | 1732 | 2360632 | 3001 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 198066 | 38.9166 | -121.0984 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022693 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912327 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20240205 | 1555 | 20240205 | 1945 | 2360805 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 722 | 116486 | 38.6615 | -120.9109 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0022339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1911992 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31013 | 20240205 | 1633 | 20240208 | 1236 | 2361034 | 4083 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4083 | 38.911 | -120.9312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022395 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912048 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5297 | 20240205 | 1635 | 20240205 | 2121 | 2361059 | 286 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 177 | 50622 | 38.8113 | -121.1139 | No | Partly Cloudy;32-90 F |  |  | 24-0022783 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912419 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15261 | 20240205 | 1638 | 20240208 | 2001 | 2361591 | 4523 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 63322 | 38.9264 | -121.2561 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1912226 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 70867 | 20240205 | 1724 | 20240208 | 1630 | 2361315 | 4266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 63990 | 38.9992 | -121.137 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912790 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 30627 | 20240205 | 1730 | 20240206 | 1043 | 2361347 | 1033 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 18594 | 38.9961 | -121.1202 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0023128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912666 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5229 | 20240205 | 1753 | 20240209 | 1424 | 2361453 | 5551 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 47008 | 38.913 | -121.2561 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912423 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15293 | 20240205 | 1805 | 20240208 | 936 | 2361530 | 3811 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 19055 | 38.9265 | -121.2878 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0026078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915039 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7301 | 20240205 | 1810 | 20240206 | 1403 | 2361553 | 1193 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 15509 | 39.0208 | -121.2768 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0023436 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912882 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20240205 | 1821 | 20240206 | 1140 | 2361657 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1726 | 148248 | 38.643 | -120.6953 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912220 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 2371 | 20240205 | 1856 | 20240206 | 1931 | 2363117 | 1475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 26550 | 38.9384 | -121.3162 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0023765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913148 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5385 | 20240205 | 1906 | 20240206 | 1737 | 2361896 | 1351 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 33775 | 38.9478 | -121.197 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0023660 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913065 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7223 | 20240205 | 2036 | 20240206 | 1053 | s1912369 | 857 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 48849 | 39.23 | -121.1382 | No | Clear;32-90 F |  |  | 24-0022734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1912369 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 8449 | 20240205 | 2220 | 20240209 | 1521 | 2363023 | 5341 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 111685 | 38.8102 | -121.1961 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | Yes | No | 1912806 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 8909 | 20240205 | 2302 | 20240206 | 834 | 2362613 | 572 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 73 | 41756 | 38.8547 | -121.1079 | No | Rain-Strong Winds-Overcast-Fog;32-90 F |  |  | 24-0022999 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912582 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5119 | 20240205 | 2302 | 20240206 | 1721 | 2362589 | 1099 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 61544 | 38.8102 | -121.1543 | No | Clear;32-90 F |  |  | 24-0023649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913057 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 31057 | 20240205 | 2312 | 20240206 | 1949 | 2363018 | 1237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 19792 | 38.7967 | -121.1163 | No | Clear;32-90 F | Service conductor | Broken | 24-0023791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913172 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 5435 | 20240205 | 2354 | 20240206 | 1211 | 2362667 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 40535 | 38.8793 | -121.1264 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0023135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912671 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 5999 | 20240206 | 235 | 20240209 | 1413 | 2363261 | 5018 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30108 | 39.316 | -120.6138 | No | Partly Cloudy-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0023255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912752 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 91405 | 20240206 | 302 | 20240208 | 1352 | 2362781 | 3530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 17650 | 38.8824 | -121.1029 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023090 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912647 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21349 | 20240206 | 354 | 20240206 | 637 | 2362871 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3423 | 38.5625 | -120.7507 | No | Clear;32-90 F |  |  | 24-0022936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912559 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 37181 | 20240206 | 522 | 20240208 | 1803 | 2362981 | 3641 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14564 | 38.8617 | -121.1231 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024277 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1913482 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 4283 | 20240206 | 539 | 20240207 | 925 | 2362997 | 1666 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 7 | 11662 | 38.8357 | -121.0954 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0024041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913345 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5247 | 20240206 | 607 | 20240206 | 1907 | 2363027 | 780 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 11700 | 38.853 | -121.1528 | No | Overcast-Fog;32-90 F |  |  | 24-0023775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913157 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | TRANSFORMER | 222196141251 | 20240206 | 718 | 20240206 | 1507 | 2363156 | 469 | Transformer only | 3rd Party | Customer Equipment | 7 | 3283 | 38.7966 | -121.2305 | No | Clear;32-90 F | Other | Broken | 24-0023557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912971 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 96301 | 20240206 | 718 | 20240207 | 1345 | 2363157 | 1827 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3654 | 38.9776 | -121.023 | No | Overcast-Fog;32-90 F |  |  | 24-0024293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913498 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 5893 | 20240206 | 740 | 20240209 | 1237 | 2363456 | 4617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 38711 | 38.8974 | -121.1804 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913795 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31155 | 20240206 | 759 | 20240208 | 2007 | s1915272 | 3608 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3608 | 38.8405 | -120.8244 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1915272 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20240206 | 910 | 20240206 | 921 | 2363321 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1300 | 14300 | 38.7617 | -120.5592 | No | Overcast;32-90 F | Jumper | Arcing | 24-0023064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1912630 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 583890 | 20240206 | 1015 | 20240206 | 1840 | 2359478 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16160 | 38.6772 | -120.7472 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken | 24-0023174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1912699 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21149 | 20240206 | 1141 | 20240206 | 1455 | 2364160 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 775 | 38.6069 | -120.7093 | No | Overcast;32-90 F |  |  | 24-0023501 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1912929 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 9413 | 20240206 | 1217 | 20240208 | 1831 | 2364283 | 3228 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 207628 | 38.8989 | -121.2185 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912968 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 35259 | 20240206 | 1306 | 20240206 | 1911 | 2364456 | 365 | Distribution Circuit | Environmental/External | Lightning | 35 | 12775 | 38.8265 | -121.1909 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023745 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913132 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4701 | 20240206 | 1435 | 20240209 | 1741 | 2365445 | 4506 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 40554 | 39.1821 | -121.198 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0023753 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1913137 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8137 | 20240206 | 1648 | 20240209 | 1550 | 2365274 | 4262 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 392104 | 39.365 | -121.0833 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0026901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1915551 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 41039 | 20240206 | 1847 | 20240206 | 2043 | 2365602 | 116 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 128 | 14848 | 38.9304 | -121.075 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0023827 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913202 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | TRANSFORMER | 222419539270 | 20240206 | 1954 | 20240209 | 1351 | 2365721 | 3957 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 15828 | 38.7416 | -121.1526 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0024582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913654 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 20240206 | 2033 | 20240208 | 1908 | 2365575 | 2795 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16770 | 39.3753 | -121.0378 | No | Clear;32-90 F | Insulator | Broken | 24-0023876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913247 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | RECLOSER | 85762 | 20240206 | 2243 | 20240207 | 1211 | 2365940 | 808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 33128 | 38.7734 | -121.4692 | No | Clear;32-90 F | Insulator | Broken | 24-0023901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913267 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 63307 | 20240207 | 422 | 20240208 | 1825 | 2366089 | 2283 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6849 | 38.8464 | -121.1825 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1915254 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | T8924 | 20240207 | 932 | 20240209 | 1111 | 2366600 | 2979 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 2979 | 38.9257 | -121.0855 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 24-0024529 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913619 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222483249986 | 20240207 | 933 | 20240207 | 1332 | 2366652 | 239 | Transformer only | Vegetation | Tree - fell into line | 2 | 478 | 39.0347 | -121.1265 | No | Partly Cloudy-Drizzle;32-90 F | Other | Normal | 24-0024301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913504 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | TRANSFORMER | 221978041950 | 20240207 | 1046 | 20240209 | 1744 | 2366904 | 3298 | Transformer only | Vegetation | Tree - fell into line | 5 | 16490 | 38.8165 | -121.307 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0024719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913764 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 7555 | 20240207 | 1122 | 20240207 | 1128 | 2365261 | 6 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 8 | 38.8022 | -121.4041 | No | Overcast-Drizzle;32-90 F |  |  | 24-0024195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913435 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | TRANSFORMER | 222420540227 | 20240207 | 1155 | 20240207 | 1504 | 2367130 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1701 | 38.768 | -121.152 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0024221 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913450 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 4231 | 20240207 | 1202 | 20240207 | 1327 | 2367140 | 85 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 425 | 39.2435 | -120.9629 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Normal | 24-0024332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913519 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 2202 | 20240207 | 1256 | 20240207 | 1304 | 2367316 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 489 | 3912 | 38.9718 | -121.1059 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0024284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913489 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 32813 | 20240207 | 1358 | 20240208 | 1855 | 2367593 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1737 | 39.1189 | -121.0837 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024355 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1913531 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 37209 | 20240207 | 1426 | 20240207 | 1903 | 2367716 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5263 | 38.8547 | -121.0903 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0024402 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913552 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | OTHER | WIRE DOWN AT MTR 1004190587 | 20240207 | 1456 | 20240208 | 1203 | 2368766 | 1267 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16853 | 38.8978 | -121.2077 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024736 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1913771 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | TRANSFORMER | 222291839060 | 20240207 | 1520 | 20240207 | 1607 | 2367881 | 47 | Transformer only | Vegetation | Tree - fell into line | 1 | 47 | 38.7362 | -121.1977 | No | Overcast;32-90 F | Service conductor | Broken- wire on ground | 24-0024518 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913611 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221638744605 | 20240207 | 1554 | 20240209 | 1244 | 2368245 | 2690 | Transformer only | Environmental/External | Water | 1 | 2690 | 38.8899 | -121.4262 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Burned Open | 24-0024571 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1913647 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7799 | 20240207 | 1910 | 20240208 | 1550 | 2368684 | 1240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 7440 | 38.9412 | -121.2288 | No | Overcast-Fog;32-90 F |  |  | 24-0026307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915143 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222963152226 | 20240207 | 2022 | 20240208 | 1348 | 2368788 | 1046 | Transformer only | Vegetation | Tree - fell into line | 10 | 10460 | 39.0962 | -120.9572 | No | Clear;32-90 F | Transformer | Broken | 24-0025984 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1914978 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 7555 | 20240207 | 2138 | 20240207 | 2223 | 2368968 | 45 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 180 | 38.8022 | -121.4041 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0024995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1914024 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 3711 | 20240207 | 2203 | 20240208 | 855 | 2368952 | 652 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 48248 | 38.9084 | -121.1642 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0026017 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1914999 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222312543500 | 20240208 | 640 | 20240209 | 1634 | 2369143 | 2034 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 4068 | 38.8581 | -121.1887 | No | Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0026065 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915032 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 38567 | 20240208 | 1030 | 20240208 | 1048 | 2369775 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 36 | 38.9378 | -121.11 | No | Overcast;32-90 F | Conductor- Overhead | Together | 24-0026172 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915079 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJ'S 1 W/OF CGC 222849842257 | 20240208 | 1030 | 20240209 | 1212 | 2369724 | 1542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1542 | 38.8228 | -121.0022 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0026939 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1915569 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15277 | 20240208 | 1238 | 20240208 | 1933 | 2370116 | 415 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 830 | 38.9265 | -121.3264 | No | Overcast;32-90 F |  |  | 24-0026560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915280 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222476045018 | 20240208 | 1323 | 20240209 | 2120 | 2370231 | 1917 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 1917 | 38.8997 | -121.1306 | No | Overcast;32-90 F |  |  | 24-0026833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915511 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 9283 | 20240208 | 1517 | 20240208 | 1555 | 2370445 | 38 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 912 | 39.2525 | -121.0762 | No | Overcast;32-90 F |  |  | 24-0026445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915202 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15321 | 20240208 | 1747 | 20240209 | 1529 | 2370785 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1737 | 38.9881 | -121.3168 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0026541 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915267 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7765 | 20240208 | 2014 | 20240208 | 2126 | 2370940 | 72 | Distribution Circuit | Vegetation | Tree - grew into line | 64 | 4608 | 39.2018 | -121.1976 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0026572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915292 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20240208 | 2130 | 20240208 | 2335 | 2371012 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 8087 | 39.0715 | -120.9763 | No | Fog;Below 32 F |  |  | 24-0026752 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915465 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 40507 | 20240209 | 704 | 20240209 | 818 | 2371164 | 74 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 666 | 38.8738 | -121.1401 | No | Partly Cloudy;32-90 F |  |  | 24-0026828 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915506 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222428652203 | 20240209 | 1056 | 20240209 | 1152 | 2371416 | 56 | Transformer only | Vegetation | Tree - fell into line | 1 | 56 | 39.0967 | -121.1455 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0026994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915592 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 3429 | 20240209 | 1155 | 20240209 | 1246 | 2371500 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 153 | 38.9994 | -120.8524 | No | Partly Cloudy;32-90 F |  |  | 24-0026999 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915594 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | TRANSFORMER | 222177041206 | 20240209 | 1542 | 20240209 | 1948 | 2372082 | 246 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 984 | 38.7953 | -121.2373 | No | Clear;32-90 F | Bus | Burned/flashed | 24-0027159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1915683 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 20240210 | 911 | 20240210 | 1208 | 2372543 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1416 | 38.9807 | -120.9404 | No | Clear;32-90 F |  |  | 24-0027375 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915841 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21349 | 20240211 | 242 | 20240211 | 914 | 2373082 | 392 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 8232 | 38.5625 | -120.7507 | No | Partly Cloudy;32-90 F |  |  | 24-0027578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916012 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222886060235 | 20240211 | 744 | 20240211 | 1216 | 2373110 | 272 | Transformer only | Vegetation | Tree - fell into line | 1 | 272 | 39.3158 | -120.9815 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0027579 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1916013 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 34489 | 20240211 | 1255 | 20240211 | 1501 | 2373320 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 4410 | 39.3122 | -120.5012 | No | Clear;32-90 F |  |  | 24-0027628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1916048 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20240211 | 1605 | 20240211 | 1728 | 2373406 | 83 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 14774 | 38.7138 | -120.6231 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027643 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1916063 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 34489 | 20240212 | 1047 | 20240212 | 2338 | 2373908 | 771 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 26985 | 39.3122 | -120.5012 | No | Clear;32-90 F | Insulator | Broken | 24-0027940 | OH | Sus | 46189636 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916265 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | TRANSFORMER | 222852567560 | 20240212 | 1436 | 20240212 | 1643 | 2374177 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 127 | 39.5182 | -120.9899 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0028078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916311 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | SWITCH | 643 | 20240213 | 1353 | 20240213 | 1510 | 2375319 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 23331 | 38.7868 | -121.2324 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0028357 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1916594 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 41345 | 20240213 | 1513 | 20240214 | 1114 | 2375478 | 1201 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1201 | 39.0118 | -120.8419 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0028604 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1916639 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 13753 | 20240213 | 1830 | 20240214 | 130 | 2375445 | 420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 29820 | 38.6649 | -120.9887 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0028593 | OH | Sus | 31684238 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1916625 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222560861010 | 20240213 | 2307 | 20240214 | 449 | 2375726 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 342 | 39.339 | -121.0954 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028636 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916667 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222118455512 | 20240214 | 1151 | 20240214 | 1250 | 2376256 | 59 | Transformer only | Animal | Squirrel | 1 | 59 | 39.1887 | -121.2523 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0028929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916860 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | TRANSFORMER | 221561841318 | 20240214 | 1200 | 20240214 | 1533 | 2376123 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 213 | 38.7998 | -121.4528 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916857 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10919 | 20240214 | 1200 | 20240214 | 1230 | 2376313 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 60 | 38.6969 | -120.8257 | No | Overcast;32-90 F |  |  | 24-0028937 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916862 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | JUMPER | OJ 1 POLE SS OF CGC 223141138683 | 20240214 | 1238 | 20240214 | 1552 | 2376276 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2522 | 38.7231 | -120.8998 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0028899 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1916854 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222409554690 | 20240214 | 1510 | 20240214 | 2341 | 2376445 | 511 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 511 | 39.1653 | -121.1509 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0029143 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916913 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20240214 | 1924 | 20240215 | 215 | 2376694 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 778 | 260550 | 38.7523 | -120.6821 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0029198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | No | No | 1916927 | 0 | EPSS Ckt | N | 2024 | A B C TIME OC
SIERRA | PLACER | SUMMIT-1101 | 152591101 | RECLOSER | 48632 | 20240214 | 2147 | 20240215 | 128 | 2376787 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 337 | 24597 | 39.32 | -120.379 | No | Overcast-Fog-Snow-Strong Winds;Below 32 F |  |  | 24-0029243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1916965 | 0 | EPSS Ckt | N | 2024 | B C
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 33999 | 20240215 | 1935 | 20240216 | 140 | 2377622 | 365 | Distribution Circuit | Animal | Other | 4 | 1460 | 39.0624 | -120.9581 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0029697 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917138 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ 2 N/W OF CGC# 223650934985 | 20240216 | 829 | 20240216 | 835 | 2378009 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6 | 38.6219 | -120.7225 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0029835 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917313 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1102 | 152161102 | TRANSFORMER | 222661745194 | 20240216 | 831 | 20240217 | 755 | 2377886 | 1404 | Transformer only | Company Initiated | Personnel- company | 1 | 1404 | 38.9038 | -121.0658 | No | Partly Cloudy;32-90 F | Transformer | Deteriorated | 24-0027890 | OH | Sus | 35494308 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1917240 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6043 | 20240216 | 834 | 20240216 | 1537 | 2378058 | 423 | Distribution Circuit | Company Initiated | Personnel- company | 77 | 32487 | 38.9764 | -120.8906 | No | Partly Cloudy;32-90 F |  |  | 24-0004995 | OH | Sus | 35496650 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1917329 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | SWITCH | 51655 | 20240216 | 1339 | 20240216 | 1437 | 2378288 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 1450 | 38.7335 | -120.7624 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0029954 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917388 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 20175 | 20240216 | 1413 | 20240216 | 1452 | 2378329 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 702 | 38.7381 | -120.7123 | No | Partly Cloudy;32-90 F |  |  | 24-0030034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917398 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1102 | 152161102 | FUSE | 8607 | 20240216 | 2050 | 20240216 | 2105 | 2378589 | 15 | Distribution Circuit | 3rd Party | Vehicle | 165 | 2475 | 38.9072 | -121.0661 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0030093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917427 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5327 | 20240216 | 2214 | 20240216 | 2325 | 2378611 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3195 | 38.9512 | -121.2285 | No | Partly Cloudy;32-90 F |  |  | 24-0030119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917447 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7013 | 20240216 | 2351 | 20240217 | 1257 | 2378645 | 786 | Distribution Circuit | 3rd Party | Vehicle | 60 | 47160 | 39.162 | -121.0389 | No | Overcast;32-90 F | Anchor or Guy | Broken | 24-0030126 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917451 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S 1 SPAN NW/OF CGC 223603033685 | 20240217 | 810 | 20240217 | 1141 | 2378697 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 211 | 38.5854 | -120.7416 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0030140 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917463 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8479 | 20240217 | 1924 | 20240218 | 1438 | 2379199 | 1154 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 60008 | 38.9916 | -121.0154 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1917565 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223353745365 | 20240217 | 2044 | 20240218 | 1120 | 2379260 | 876 | Transformer only | Equipment Failure/Involved | Underground | 3 | 2628 | 38.906 | -120.8225 | No | Overcast-Drizzle;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0030402 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917669 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 8423 | 20240217 | 2209 | 20240218 | 1656 | 2379291 | 1123 | Distribution Circuit | Equipment Failure/Involved | Underground | 55 | 61765 | 38.8173 | -121.1918 | No | Overcast-Drizzle;32-90 F | Elbow | Failed/Faulted | 24-0030344 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917624 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18299 | 20240218 | 1331 | 20240218 | 1556 | 2379651 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 4640 | 38.5987 | -120.9874 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0030464 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917708 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20240218 | 1401 | 20240218 | 1457 | 2379689 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 2352 | 38.6321 | -120.9241 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 24-0030473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917712 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | TRANSFORMER | T2061 | 20240218 | 1947 | 20240218 | 2059 | 2380039 | 72 | Transformer only | 3rd Party | Other | 2 | 144 | 38.9507 | -121.0867 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0030528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1917767 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 6927 | 20240218 | 2103 | 20240218 | 2237 | 2380124 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1692 | 39.1578 | -121.1009 | No | Overcast-Rain-Lightning;32-90 F |  |  | 24-0030570 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1917810 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222611053775 | 20240218 | 2154 | 20240219 | 1126 | 2380158 | 812 | Transformer only | Environmental/External | Lightning | 2 | 1624 | 39.139 | -121.0799 | No | Overcast-Heavy Rain-Fog;32-90 F | Transformer | Failed/Faulted | 24-0030573 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917813 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 2677 | 20240218 | 2231 | 20240219 | 17 | 2380173 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1908 | 38.7007 | -120.9851 | No | Clear-Lightning;32-90 F |  |  | 24-0030576 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917816 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223343749520 | 20240218 | 2303 | 20240219 | 1048 | 2380686 | 705 | Transformer only | Environmental/External | Lightning | 5 | 3525 | 39.0204 | -120.8236 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917941 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 2677 | 20240219 | 48 | 20240219 | 1054 | 2380256 | 606 | Distribution Circuit | Environmental/External | Lightning | 17 | 10302 | 38.7007 | -120.9851 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0030690 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917916 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | TRANSFORMER | 222902937534 | 20240219 | 49 | 20240219 | 1200 | 2380255 | 671 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 671 | 38.6931 | -120.9839 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0030591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917831 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222302746432 | 20240219 | 137 | 20240219 | 1327 | 2380259 | 710 | Transformer only | Environmental/External | Lightning | 2 | 1420 | 38.9392 | -121.1919 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0030685 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917913 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | MTR#1011120348 | 20240219 | 143 | 20240219 | 831 | 2380258 | 408 | Transformer only | Environmental/External | Lightning | 2 | 816 | 38.9124 | -121.1841 | No | Overcast-Fog-Drizzle;32-90 F | Transformer | Malfunctioning | 24-0030658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917889 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222265646267 | 20240219 | 143 | 20240219 | 1235 | 2380260 | 652 | Transformer only | Environmental/External | Lightning | 3 | 1956 | 38.9341 | -121.2047 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917929 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222515051207 | 20240219 | 657 | 20240219 | 1112 | 2380389 | 255 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 255 | 39.0692 | -121.1154 | No | Partly Cloudy-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0030646 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917877 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222611553788 | 20240219 | 733 | 20240219 | 1209 | 2380538 | 276 | Transformer only | Environmental/External | Lightning | 1 | 276 | 39.1399 | -121.0802 | No | Overcast-Fog;32-90 F | Transformer | Burned/flashed | 24-0030677 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917902 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222616053799 | 20240219 | 851 | 20240219 | 906 | 2380540 | 15 | Transformer only | Environmental/External | Lightning | 1 | 15 | 39.1399 | -121.0785 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917904 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223074646760 | 20240219 | 853 | 20240219 | 1256 | 2380542 | 243 | Transformer only | Environmental/External | Lightning | 1 | 243 | 38.9455 | -120.9205 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0030761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917972 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2543 | 20240219 | 951 | 20240219 | 1142 | 2380630 | 111 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 86 | 9546 | 38.7883 | -120.1531 | No | Overcast-Drizzle;32-90 F |  |  | 24-0030790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917992 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 3383 | 20240219 | 1049 | 20240219 | 1317 | 2380862 | 148 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 22 | 3256 | 38.8033 | -120.0984 | No | Overcast-Rain;32-90 F |  |  | 24-0030869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918044 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 71607 | 20240219 | 1058 | 20240219 | 1705 | 2380874 | 367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 367 | 39.1446 | -121.0825 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Burned/flashed | 24-0030856 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918035 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223345049552 | 20240219 | 1110 | 20240219 | 1452 | 2380906 | 222 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1110 | 39.0213 | -120.8232 | No | Overcast-Rain;32-90 F | Transformer (OH) | Broken | 24-0030818 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918007 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN 1 LD SIDE CGC 223524634966 | 20240219 | 1141 | 20240219 | 1722 | 2380981 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2899 | 38.6201 | -120.7684 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030822 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1918010 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223198042725 | 20240219 | 1309 | 20240219 | 1812 | 2381346 | 303 | Transformer only | Environmental/External | Lightning | 2 | 606 | 38.8345 | -120.8793 | No | Overcast-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918088 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6605 | 20240219 | 1351 | 20240219 | 1729 | 2381523 | 218 | Distribution Circuit | Environmental/External | Ice or snow | 42 | 7841 | 39.3245 | -120.3788 | No | Overcast-Snow;32-90 F | Conductor- Overhead | Together | 24-0030962 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918112 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6823 | 20240219 | 1539 | 20240219 | 2019 | 2381801 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 3175 | 39.3138 | -120.34 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0031051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918169 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 1553 | 20240219 | 1631 | 20240219 | 2223 | 2381844 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 4472 | 38.7447 | -120.8192 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken | 24-0031023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918151 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 222999453483 | 20240219 | 1638 | 20240220 | 1119 | 2381887 | 1121 | Transformer only | Environmental/External | Lightning | 1 | 1121 | 39.13 | -120.9435 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918172 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ 1 N/O CGC 222312555629 | 20240219 | 1724 | 20240220 | 1515 | 2381888 | 1311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2622 | 39.192 | -121.1849 | No | Overcast-Fog-Rain-Lightning;32-90 F | Crossarm- Wood | Broken | 24-0031022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1918150 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222852258728 | 20240219 | 1756 | 20240220 | 1155 | 2381903 | 1079 | Transformer only | Environmental/External | Lightning | 3 | 3237 | 39.2748 | -120.9927 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0031036 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918159 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222804247405 | 20240219 | 1801 | 20240220 | 1015 | 2381948 | 974 | Transformer only | Environmental/External | Lightning | 2 | 1948 | 38.9639 | -121.0148 | No | Partly Cloudy-Fog-Drizzle-Lightning;32-90 F | Transformer (OH) | Broken | 24-0031060 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918176 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | TRANSFORMER | 223948260642 | 20240219 | 1815 | 20240220 | 1646 | 2381978 | 1351 | Transformer only | Environmental/External | Lightning | 3 | 4053 | 39.323 | -120.6048 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0031624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918477 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50010 | 20240219 | 2031 | 20240219 | 2047 | 2382061 | 16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1266 | 20256 | 39.2219 | -121.0498 | No | Overcast-Fog-Rain;32-90 F | Recloser | Malfunctioning | 24-0031087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1918197 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 6823 | 20240219 | 2039 | 20240220 | 1304 | 2382088 | 985 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 14553 | 39.3138 | -120.34 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0031118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918225 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50010 | 20240219 | 2120 | 20240219 | 2150 | 2382080 | 30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1266 | 37980 | 39.2219 | -121.0498 | No | Overcast-Fog-Rain;32-90 F | Recloser | Malfunctioning | 24-0031115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1918221 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1105 | 153701105 | SWITCH | 2325 | 20240220 | 1715 | 20240221 | 1131 | 2383293 | 1096 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 19137 | 38.8691 | -121.3401 | No | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken | 24-0031656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1918495 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 33537 | 20240220 | 1731 | 20240220 | 2118 | 2383307 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 4086 | 38.8107 | -121.1791 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0031658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1918496 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 10735 | 20240220 | 1748 | 20240220 | 2000 | 2383321 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 5412 | 38.7023 | -120.7619 | No | Overcast-Fog-Lightning;32-90 F |  |  | 24-0031675 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918510 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 31601 | 20240220 | 1800 | 20240220 | 1806 | 2383096 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 39.3316 | -120.5727 | No | Overcast-Rain;32-90 F | Connector or Splice (UG) | Normal | 24-0031665 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1918502 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20240220 | 2028 | 20240221 | 947 | 2383408 | 799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 42651 | 38.7309 | -120.8421 | No | Overcast-Fog;32-90 F | Connector or Splice (OH) | Burned Open | 24-0031745 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918575 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223527537865 | 20240220 | 2032 | 20240221 | 1204 | 2383409 | 932 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1864 | 38.6998 | -120.7649 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0031690 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918519 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6611 | 20240221 | 629 | 20240222 | 1155 | 2383586 | 1766 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 51214 | 39.3192 | -120.432 | No | Clear;Below 32 F |  |  | 24-0032626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1919176 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20240221 | 636 | 20240221 | 749 | 2383617 | 73 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 135 | 9855 | 39.0914 | -121.0565 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0031849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918614 | 0 | EPSS Ckt | N | 2024 | BC
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222276842392 | 20240221 | 957 | 20240221 | 1046 | 2384054 | 49 | Transformer only | Vegetation | Tree - branch fell on line | 14 | 686 | 38.8279 | -121.2018 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0031976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918795 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20240221 | 1010 | 20240221 | 1102 | 2384074 | 52 | Distribution Circuit | Animal | Bird found | 20 | 1040 | 38.8769 | -121.017 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0031973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918794 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222703053254 | 20240221 | 1412 | 20240221 | 1732 | 2384407 | 200 | Transformer only | Vegetation | Tree - fell into line | 5 | 1000 | 39.1252 | -121.0488 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0032219 | OH | Sus | 31684813 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1918851 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224731360568 | 20240221 | 1433 | 20240223 | 1138 | 2384423 | 2705 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 2705 | 39.3175 | -120.3286 | No | Clear;32-90 F |  |  | 24-0032637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919186 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJ'S SS OF CGC222826544928 | 20240222 | 905 | 20240222 | 1339 | 2385000 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 548 | 38.8959 | -121.0089 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0032450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1919020 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222718854576 | 20240222 | 943 | 20240222 | 1308 | 2385133 | 205 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 205 | 39.1615 | -121.0419 | No | Clear;32-90 F | Service conductor | Broken | 24-0032512 | OH | Sus | 31684886 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919127 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 20240222 | 1129 | 20240222 | 1626 | 2385238 | 297 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1167 | 8748 | 39.3313 | -121.1015 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0032569 | OH | Sus | 31684854 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1919154 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ'S SS OF CGC222282555588 | 20240222 | 1131 | 20240222 | 1222 | 2385265 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 51 | 39.1897 | -121.1967 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0032557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1919145 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 8585 | 20240223 | 831 | 20240223 | 1000 | 2385938 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 4895 | 38.8475 | -121.2149 | No | Fog;32-90 F |  |  | 24-0033120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1919562 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 35823 | 20240223 | 1358 | 20240223 | 1840 | 2386377 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1128 | 38.8389 | -121.3297 | No | Partly Cloudy;32-90 F |  |  | 24-0033394 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1919644 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 7007 | 20240223 | 1500 | 20240223 | 1635 | 2386427 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 285 | 38.8213 | -120.07 | No | Overcast;32-90 F |  |  | 24-0033342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919627 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 17147 | 20240224 | 500 | 20240224 | 557 | 2386628 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 152 | 38.884 | -121.4048 | No | Partly Cloudy;32-90 F |  |  | 24-0033440 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919695 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222633058530 | 20240224 | 745 | 20240224 | 1228 | 2386665 | 283 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 566 | 39.2718 | -121.0707 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033458 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919737 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222269746278 | 20240224 | 1429 | 20240224 | 2200 | 2386913 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 451 | 38.9344 | -121.2033 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033537 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919792 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20240224 | 1541 | 20240224 | 1630 | 2386988 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 778 | 38122 | 38.7523 | -120.6821 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0033519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1919783 | 0 | EPSS Ckt | N | 2024 | A C TIME OC
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223087737565 | 20240224 | 1702 | 20240224 | 2357 | 2387038 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 415 | 38.6937 | -120.919 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919800 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222841656004 | 20240225 | 704 | 20240225 | 929 | 2387288 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 290 | 39.2 | -120.9974 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0033601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1919871 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222841656004 | 20240225 | 1202 | 20240225 | 1319 | 2387405 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 154 | 39.2 | -120.9974 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0033622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1919888 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | S SPANS N/E OF CGC 223241054370 | 20240226 | 915 | 20240226 | 1152 | 2387820 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 628 | 39.1596 | -120.8586 | No | Overcast-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0033737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920029 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | FUSE | 5957 | 20240226 | 1307 | 20240226 | 1440 | 2388197 | 93 | Distribution Circuit | Vegetation | Tree - grew into line | 8 | 744 | 38.7435 | -121.1517 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0033931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920184 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 7497 | 20240227 | 1003 | 20240227 | 1236 | 2388951 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 8721 | 38.8616 | -121.0162 | No | Clear;32-90 F |  |  | 24-0034346 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1920487 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222820043600 | 20240227 | 1348 | 20240228 | 341 | 2389195 | 833 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 14811 | 38.8595 | -121.0105 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0034505 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1920524 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | JUMPER | FB 1 S/O 222148740491 | 20240227 | 1720 | 20240227 | 1842 | 2389377 | 82 | Distribution Circuit | Vegetation | Tree - grew into line | 49 | 4018 | 38.7756 | -121.2471 | No | Clear;32-90 F | Circuit Breaker | Normal | 24-0034588 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920548 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9767 | 20240227 | 1831 | 20240228 | 751 | 2389436 | 800 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 3079 | 39.1887 | -121.0658 | No | Clear;32-90 F |  |  | 24-0034612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1920561 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ 2 SPAN W/OF CGC 222128456217 | 20240228 | 1010 | 20240228 | 1114 | 2389931 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 64 | 39.2072 | -121.2499 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0034813 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920801 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 946229 | 20240228 | 1431 | 20240228 | 1547 | 2390225 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 4636 | 38.9274 | -121.1027 | No | Clear;32-90 F |  |  | 24-0035074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1920871 | 0 | EPSS Ckt | N | 2024 | B & C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223768038410 | 20240228 | 1457 | 20240229 | 50 | 2390245 | 593 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1186 | 38.715 | -120.6805 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0035122 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1920880 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222553546166 | 20240228 | 1614 | 20240228 | 1735 | 2390294 | 81 | Transformer only | Animal | Bird found | 4 | 324 | 38.9308 | -121.1037 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0035136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1920885 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15345 | 20240228 | 2327 | 20240229 | 117 | 2390481 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 660 | 38.9262 | -121.3953 | No | Clear;32-90 F |  |  | 24-0035200 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1920917 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | FUSE | 30193 | 20240229 | 150 | 20240229 | 416 | 2390495 | 146 | Distribution Circuit | Vegetation | Other ground vegetation | 436 | 21815 | 38.8155 | -121.2687 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0035205 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1920919 | 1 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 13729 | 20240229 | 247 | 20240229 | 325 | 2390511 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 1596 | 38.6817 | -120.964 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Normal | 24-0035207 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920921 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | JUMPER | 18887 SS JUMPER | 20240229 | 520 | 20240229 | 907 | 2390538 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 9988 | 38.5556 | -120.9916 | No | Overcast;32-90 F | Jumper | Burned Open | 24-0035213 | OH | Sus | 46200798 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1920930 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 5435 | 20240229 | 929 | 20240229 | 1030 | 2390923 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 3355 | 38.8793 | -121.1264 | No | Overcast;32-90 F |  |  | 24-0035392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1921067 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2140 | 20240229 | 1746 | 20240229 | 1913 | 2391583 | 87 | Distribution Circuit | Vegetation | Tree - branch fell on line | 604 | 22830 | 39.2895 | -120.9854 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0035747 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1921205 | 0 | EPSS Ckt | N | 2024 | A-B
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6613 | 20240301 | 549 | 20240304 | 1646 | 2391770 | 4977 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 308574 | 39.3178 | -120.4494 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921315 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 8029 | 20240301 | 642 | 20240301 | 1025 | 2391919 | 223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 11819 | 39.6173 | -120.5919 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Normal | 24-0035973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921283 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20240301 | 844 | 20240306 | 1532 | 2391866 | 7608 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 213024 | 39.3181 | -120.4547 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036240 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921370 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1102 | 153701102 | FUSE | 7389 | 20240301 | 1005 | 20240301 | 1345 | 2391931 | 220 | Distribution Circuit | Equipment Failure/Involved | Underground | 156 | 30095 | 38.8899 | -121.303 | Yes | Partly Cloudy;32-90 F | Switch (UG) | Burned/flashed | 24-0036018 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921294 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20240301 | 1210 | 20240305 | 1537 | 2392040 | 5967 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 334152 | 39.3203 | -120.4331 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0036202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921353 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222911833380 | 20240301 | 1233 | 20240301 | 1422 | 2392070 | 109 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 109 | 38.5785 | -120.9828 | Yes | Clear;32-90 F |  |  | 24-0036172 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921344 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20240301 | 1303 | 20240301 | 1414 | 2392110 | 71 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 715 | 40756 | 38.773 | -120.2933 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0036125 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921326 | 0 | EPSS Ckt | N | 2024 | SGF RLY
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7935 | 20240301 | 1330 | 20240307 | 1014 | 2398010 | 8444 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 312428 | 39.6302 | -120.5447 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0038402 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1922674 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7927 | 20240301 | 1333 | 20240301 | 1453 | 2392185 | 80 | Distribution Circuit | Animal | Bird found | 7 | 560 | 38.8464 | -121.4237 | Yes | Partly Cloudy-Fog-Rain;32-90 F | Fuse | Burned Open | 24-0036186 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921348 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 992864 | 20240301 | 1406 | 20240304 | 1801 | 2392502 | 4381 | Distribution Circuit | Vegetation | Tree - fell into line | 1027 | 2267552 | 38.8042 | -120.1031 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036261 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921380 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | OCB | 1111/2 | 20240301 | 1418 | 20240301 | 1833 | 2392292 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 886 | 100296 | 38.7313 | -120.7839 | Yes | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0036175 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921345 | 0 | EPSS Ckt | N | 2024 | A GRD INST OC
SIERRA | PLACER | TAMARACK-1101 | 152291101 | SWITCH | 2017 | 20240301 | 1530 | 20240301 | 1706 | 2392448 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 308 | 29568 | 39.3184 | -120.455 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Connector or Splice (OH) | Broken | 24-0036239 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1921369 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | SWITCH | 48632 | 20240301 | 1533 | 20240304 | 1503 | 2392432 | 4256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 325131 | 39.32 | -120.379 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Insulator | Broken | 24-0036224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921368 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | JUMPER | MISS-MAP AT J314 | 20240301 | 1543 | 20240301 | 1630 | 2392543 | 47 | Distribution Circuit | Company Initiated | Improper Construction | 20 | 940 | 38.8931 | -121.3098 | Yes | Overcast;32-90 F | Elbow | Normal | 24-0036018 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921390 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223896539890 | 20240301 | 1637 | 20240301 | 1743 | 2392530 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 132 | 38.7535 | -120.6356 | Yes | Partly Cloudy-Fog-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken | 24-0036340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921410 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | SWITCH | 2348 | 20240301 | 1708 | 20240301 | 1730 | 2392585 | 22 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 1650 | 38.8933 | -121.3061 | Yes | Overcast-Rain;32-90 F | Switch (UG) | Burned/flashed | 24-0036018 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1921398 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 20240301 | 1723 | 20240301 | 1906 | 2392590 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1442 | 38.7941 | -120.8199 | Yes | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0036415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921461 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 1731 | 20240301 | 1727 | 20240303 | 1431 | 2395133 | 2704 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 256880 | 39.5698 | -120.6203 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1921933 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 5469 | 20240301 | 1727 | 20240305 | 1756 | 2397929 | 5789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 40523 | 39.6128 | -120.6006 | Yes | Overcast;Below 32 F | Conductor- Overhead | Together | 24-0038369 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922654 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32995 | 20240301 | 1748 | 20240302 | 1203 | 2392720 | 1095 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 271560 | 39.253 | -121.1151 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921457 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 37238 | 20240301 | 1757 | 20240302 | 1837 | 2392738 | 1480 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 108257 | 39.0474 | -120.7852 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921417 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20240301 | 1822 | 20240302 | 1512 | 2392936 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 672 | 584520 | 39.2129 | -121.0129 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036378 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1921455 | 0 | EPSS Ckt | N | 2024 | a - c - time oc
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | OTHER | WIRE DOWN | 20240301 | 1822 | 20240302 | 1930 | 2392807 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 372673 | 39.2868 | -121.027 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036386 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921431 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1101 | 152161101 | FUSE | 8407 | 20240301 | 1847 | 20240302 | 1047 | 2392857 | 960 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 130504 | 38.8972 | -121.0611 | Yes | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0036444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921490 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8267 | 20240301 | 1848 | 20240302 | 1815 | 2392855 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 15477 | 38.9744 | -121.05 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921481 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1101/2 | 20240301 | 1905 | 20240302 | 1103 | 2392900 | 958 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2184 | 361984 | 39.02 | -120.8294 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921447 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20240301 | 1906 | 20240304 | 1738 | 2392923 | 4232 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 317040 | 39.2562 | -120.7669 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1921454 | 0 | EPSS Ckt | N | 2024 | B+C+GRD
SIERRA | PLACER | DRUM-1101 | 152321101 | FUSE | 9213 | 20240301 | 1906 | 20240304 | 1738 | 2395162 | 4232 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 63480 | 39.2814 | -120.7074 | Yes | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1921938 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DRUM-1101 | 152321101 | FUSE | 31201 | 20240301 | 1906 | 20240304 | 1744 | 2395389 | 4238 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 67808 | 39.2872 | -120.6947 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0036410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1921955 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | OTHER | 8929 | 20240301 | 1908 | 20240302 | 1502 | 2393269 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 34110 | 39.2121 | -121.098 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036428 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1921483 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12717 | 20240301 | 1928 | 20240302 | 1448 | 2392978 | 1160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 19720 | 38.7654 | -120.7158 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Together | 24-0036751 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921782 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 9225 | 20240301 | 1946 | 20240303 | 1417 | 2394157 | 2551 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 45918 | 39.3227 | -120.6364 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Transformer (OH) | Broken- wire on ground | 24-0036632 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921674 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1249 | 20240301 | 2001 | 20240302 | 1115 | 2393315 | 914 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 31076 | 38.8114 | -120.8047 | Yes | Snow;Below 32 F | Conductor- Overhead | Together | 24-0036785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921808 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 20503 | 20240301 | 2039 | 20240302 | 937 | 2393419 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 22562 | 38.7578 | -120.8402 | Yes | Overcast-Fog-Rain;32-90 F | Other | Broken | 24-0036769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921795 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8667 | 20240301 | 2045 | 20240302 | 1400 | 2392929 | 1035 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 55890 | 39.184 | -120.9994 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0036471 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921515 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 8459 | 20240301 | 2049 | 20240302 | 1329 | 2393452 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12000 | 39.0275 | -121.0037 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921623 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223447039548 | 20240301 | 2101 | 20240302 | 823 | 2393582 | 682 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 2046 | 38.7455 | -120.7926 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0036737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921771 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20240301 | 2108 | 20240302 | 1525 | 2393592 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 411 | 297240 | 38.7121 | -120.9501 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036504 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1921549 | 0 | EPSS Ckt | N | 2024 | ABC GRD
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 6973 | 20240301 | 2124 | 20240302 | 1616 | 2393632 | 1132 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 35420 | 39.3385 | -121.0579 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921599 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20240301 | 2139 | 20240302 | 1716 | 2393678 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 243443 | 38.8931 | -120.9977 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921566 | 0 | EPSS Ckt | N | 2024 | A+C
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9313 | 20240301 | 2139 | 20240303 | 1119 | 2393654 | 2260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 11300 | 38.8293 | -121.0463 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 24-0037053 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921992 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5725 | 20240301 | 2142 | 20240302 | 1633 | 2393661 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 24882 | 39.0076 | -121.0399 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921877 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7451 | 20240301 | 2146 | 20240302 | 1425 | 2393677 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 45972 | 39.1832 | -121.0848 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036582 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921621 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33617 | 20240301 | 2147 | 20240302 | 1400 | 2394518 | 973 | Distribution Circuit | Vegetation | Tree - grew into line | 30 | 29190 | 39.2929 | -121.0153 | Yes | Overcast-Snow;Below 32 F | Fuse | Broken | 24-0036771 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1921796 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2100 | 20240301 | 2147 | 20240303 | 1841 | 2393702 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 1914 | 2764131 | 39.2417 | -121.0264 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921574 | 0 | EPSS Ckt | N | 2024 | A - C
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | FUSE | 30553 | 20240301 | 2147 | 20240302 | 1158 | 2393679 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 22126 | 39.2128 | -121.0738 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036600 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921640 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 86696 | 20240301 | 2149 | 20240302 | 1309 | 2393692 | 920 | Distribution Circuit | Vegetation | Tree - fell into line | 770 | 700907 | 39.1827 | -120.8571 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921649 | 0 | EPSS Ckt | N | 2024 | B OC
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6375 | 20240301 | 2149 | 20240303 | 1601 | 2394698 | 2532 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 218340 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken | 24-0036831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921841 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 57223 | 20240301 | 2149 | 20240303 | 1230 | 2394950 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9284 | 39.2092 | -120.8186 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921903 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 6515 | 20240301 | 2149 | 20240302 | 1511 | 2393722 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6252 | 39.0044 | -121.0165 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0036616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921657 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 4023 | 20240301 | 2151 | 20240303 | 1016 | 2393726 | 2185 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 92226 | 39.1593 | -121.0593 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1921766 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9383 | 20240301 | 2152 | 20240302 | 1923 | 2393725 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 63259 | 38.9077 | -120.8458 | Yes | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0036910 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921896 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 36265 | 20240301 | 2200 | 20240302 | 1142 | 2393788 | 822 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 63294 | 39.0955 | -120.9624 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0036817 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921832 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20240301 | 2224 | 20240302 | 959 | 2393868 | 695 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 115370 | 38.7712 | -120.9325 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0036794 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921813 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 7989 | 20240301 | 2236 | 20240302 | 1918 | 2393882 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 45622 | 38.6663 | -120.8941 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036818 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921833 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20240301 | 2243 | 20240303 | 1923 | 2393891 | 2680 | Distribution Circuit | Vegetation | Tree - fell into line | 1037 | 1688686 | 38.9052 | -120.8374 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921605 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7383 | 20240301 | 2249 | 20240302 | 1342 | 2393902 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40185 | 39.2614 | -121.0127 | Yes | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1921660 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 6129 | 20240301 | 2320 | 20240302 | 1703 | 2393967 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 114804 | 38.9854 | -121.0048 | Yes | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036783 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921806 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 32536 | 20240301 | 2331 | 20240302 | 1752 | 2394708 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 313184 | 39.2398 | -120.9935 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921847 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20240301 | 2332 | 20240302 | 107 | 2393072 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 14725 | 39.3251 | -120.6429 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Transformer (OH) | Broken- wire on ground | 24-0036602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1921642 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21935 | 20240301 | 2333 | 20240302 | 956 | 2394057 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 623 | 38.6764 | -120.7519 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0036773 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921798 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21933 | 20240301 | 2337 | 20240302 | 1338 | 2394556 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9251 | 38.6827 | -120.7547 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0036750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921781 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 8361 | 20240302 | 7 | 20240302 | 925 | 2394086 | 558 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 6138 | 38.6763 | -120.7524 | No | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0036731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921765 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 6703 | 20240302 | 126 | 20240302 | 1722 | 2395030 | 956 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 12701 | 39.3202 | -120.6232 | No | Overcast-Fog-Snow-Strong Winds;Below 32 F |  |  | 24-0036946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921918 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20240302 | 134 | 20240302 | 1531 | 2394183 | 837 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 137 | 114669 | 39.3251 | -120.6429 | No | Overcast-Fog-Snow-Strong Winds;Below 32 F |  |  | 24-0036602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1921684 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1507 | 20240302 | 702 | 20240302 | 1606 | 2394460 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 6129 | 38.7412 | -120.7227 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on object | 24-0036730 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921763 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222866956948 | 20240302 | 822 | 20240302 | 1810 | 2394537 | 588 | Transformer only | Environmental/External | Ice or snow | 2 | 1176 | 39.2258 | -120.9892 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 24-0036906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921892 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | SWITCH | 2348 | 20240302 | 934 | 20240302 | 1932 | 2394667 | 598 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 44850 | 38.8933 | -121.3061 | No | Partly Cloudy-Drizzle;32-90 F | Switch (UG) | Broken | 24-0036018 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921826 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222919533380 | 20240302 | 1137 | 20240302 | 1647 | 2394837 | 310 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 310 | 38.5786 | -120.9801 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1921919 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 32613 | 20240302 | 1147 | 20240302 | 1208 | 2394873 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 735 | 39.2262 | -121.0671 | No | Overcast-Fog;32-90 F | Insulator | Broken | 24-0036886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1921880 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | BURNED OJ @ 5220 HIDDEN HOLLOW DR | 20240302 | 1510 | 20240302 | 1625 | 2395354 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 300 | 38.6828 | -120.7561 | No | Overcast-Fog-Drizzle;32-90 F | Jumper | Burned Open | 24-0037005 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921951 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 9221 | 20240302 | 1551 | 20240303 | 1407 | 2395178 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 23155 | 39.3014 | -120.6601 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1922069 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6639 | 20240302 | 1725 | 20240305 | 1656 | 2396750 | 4291 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 85820 | 39.3215 | -120.4351 | No | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037639 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1922328 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | JUMPER | OJ 1 LD SIDE OF FUCO 31313 | 20240302 | 1727 | 20240303 | 1609 | 2395130 | 1362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 28602 | 39.5672 | -120.6291 | No | Overcast-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0036334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1921931 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 8029 | 20240302 | 1727 | 20240304 | 1833 | 2396215 | 2946 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 156138 | 39.6173 | -120.5919 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0037224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1922143 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7969 | 20240302 | 1727 | 20240307 | 1837 | 2397945 | 7270 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 50890 | 39.6879 | -120.6455 | No | Overcast-Snow;Below 32 F |  |  | 24-0036334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1922661 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 32525 | 20240302 | 1727 | 20240307 | 1837 | 2399208 | 7270 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7270 | 39.6278 | -120.6161 | No | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1923219 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | SWITCH | 9201 | 20240302 | 1826 | 20240304 | 1708 | 2396171 | 2802 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 56040 | 39.3039 | -120.6475 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1922133 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 34527 | 20240302 | 1914 | 20240303 | 1157 | 2395544 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 65672 | 39.2657 | -120.9108 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037138 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1922071 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18507 | 20240302 | 2002 | 20240302 | 2145 | 2395576 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1236 | 38.762 | -120.5384 | No | Overcast-Fog-Snow-Strong Winds;Below 32 F |  |  | 24-0037070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922011 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224052739852 | 20240302 | 2011 | 20240302 | 2156 | 2395573 | 105 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 420 | 38.752 | -120.5799 | No | Overcast-Fog-Snow;32-90 F |  |  | 24-0037075 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1922018 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1102 | 153701102 | SWITCH | 2312 | 20240302 | 2026 | 20240302 | 2200 | 2395609 | 94 | Distribution Circuit | Company Initiated | Return Circuit Normal | 156 | 4713 | 38.8937 | -121.3055 | No | Overcast-Fog-Drizzle;32-90 F | Switch (UG) | Normal | 24-0036018 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1922009 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224069639939 | 20240302 | 2124 | 20240303 | 1351 | 2395628 | 987 | Transformer only | Vegetation | Tree - fell into line | 3 | 2961 | 38.7543 | -120.5737 | No | Overcast-Fog-Snow;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0037141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1922073 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224093839940 | 20240302 | 2140 | 20240302 | 2240 | 2395638 | 60 | Transformer only | Environmental/External | Ice or snow | 2 | 120 | 38.7541 | -120.5651 | No | Overcast-Fog-Snow;Below 32 F | Fuse | Burned Open | 24-0037081 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922024 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | JUMPER | WIRE DOWN @ CGC 223874660452 | 20240302 | 2158 | 20240304 | 1436 | 2395642 | 2438 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 82191 | 39.3185 | -120.6295 | No | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | Yes | 1922036 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2708 | 20240302 | 2232 | 20240303 | 1818 | 2395651 | 1186 | Distribution Circuit | 3rd Party | Vehicle | 383 | 193670 | 38.7961 | -121.1633 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0037082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922025 | 0 | EPSS Ckt | N | 2024 | A & B
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7919 | 20240303 | 730 | 20240303 | 936 | 2395783 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 8190 | 38.7507 | -120.632 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 24-0037169 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922095 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224093039903 | 20240303 | 1121 | 20240303 | 1323 | 2396150 | 122 | Transformer only | Environmental/External | Ice or snow | 3 | 366 | 38.7531 | -120.5654 | No | Snow-Overcast;32-90 F | Transformer | Normal | 24-0037207 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922130 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8947 | 20240303 | 1232 | 20240303 | 1441 | 2396084 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3225 | 39.2127 | -121.0123 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 24-0037198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1922125 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222686246597 | 20240303 | 1409 | 20240303 | 1455 | 2396198 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 414 | 38.9423 | -121.0568 | No | Partly Cloudy-Drizzle;32-90 F | Connector or Splice (OH) | Broken | 24-0037228 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922146 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | OTHER | WIRE DOWN @ CGC 221509539313 | 20240303 | 1457 | 20240303 | 1845 | 2396223 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 1536 | 38.7454 | -121.4699 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | Yes | 1922150 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | MTR#1004687956 | 20240303 | 1554 | 20240304 | 1250 | 2396243 | 1256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2512 | 38.9897 | -121.0239 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken | 24-0037253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922166 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 8353 | 20240303 | 1640 | 20240303 | 1719 | 2396264 | 39 | Distribution Circuit | Vegetation | Tree - bark fell into line | 100 | 3900 | 39.2346 | -121.2074 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0037254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922167 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223423639031 | 20240303 | 1742 | 20240303 | 1928 | 2396291 | 106 | Transformer only | Unknown Cause | Patrol - found nothing | 8 | 848 | 38.7321 | -120.8007 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0037261 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1922171 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 139520 | 20240303 | 1923 | 20240304 | 1011 | 2396339 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 155400 | 38.9439 | -120.7215 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0036565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922180 | 0 | EPSS Ckt | N | 2024 | UNKNOWN
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 20240303 | 1934 | 20240304 | 1205 | 2396384 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10901 | 38.8791 | -120.8335 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1922231 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5811 | 20240303 | 1937 | 20240303 | 2201 | 2396334 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2206 | 38.8819 | -120.8303 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0037324 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922230 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6615 | 20240304 | 1003 | 20240305 | 1357 | 2397703 | 1674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 58590 | 39.3223 | -120.4359 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0038177 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922610 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6635 | 20240304 | 1003 | 20240306 | 1249 | 2397808 | 3046 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 55228 | 39.3199 | -120.4336 | No | Clear;Below 32 F | Crossarm- Wood | Broken | 24-0038177 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1922625 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18965 | 20240304 | 1026 | 20240304 | 1040 | 2396693 | 14 | Distribution Circuit | Animal | Squirrel | 1 | 14 | 38.7259 | -120.8343 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0037493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922295 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224814240568 | 20240304 | 1301 | 20240304 | 1727 | 2396787 | 266 | Transformer only | Vegetation | Tree - branch fell on line | 12 | 3192 | 38.7683 | -120.3123 | No | Overcast-Fog;Below 32 F | Service conductor | Normal | 24-0036261 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1922306 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 30145 | 20240304 | 1337 | 20240304 | 1642 | 2396882 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1665 | 39.1623 | -120.8618 | No | Partly Cloudy;32-90 F |  |  | 24-0037734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922354 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222485553415 | 20240305 | 1356 | 20240305 | 1630 | 2397807 | 154 | Transformer only | Vegetation | Tree - fell into line | 1 | 154 | 39.13 | -121.1251 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038246 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922626 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224422660633 | 20240305 | 1429 | 20240306 | 949 | 2397840 | 1160 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2320 | 39.3207 | -120.4378 | No | Overcast;32-90 F | Cutout- fuse holder | Broken | 24-0038297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922638 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 9827 | 20240305 | 1546 | 20240305 | 1707 | 2397893 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2106 | 39.1937 | -121.2485 | No | Clear;32-90 F |  |  | 24-0038384 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922660 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225297741727 | 20240305 | 1554 | 20240305 | 1640 | 2397826 | 46 | Transformer only | Environmental/External | Ice or snow | 2 | 92 | 38.7974 | -120.142 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0038363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922651 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6613 | 20240306 | 156 | 20240306 | 1022 | 2398082 | 506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 31372 | 39.3178 | -120.4494 | No | Clear;Below 32 F | Woodpin | Broken | 24-0038589 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922840 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15249 | 20240306 | 557 | 20240306 | 738 | 2398111 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 909 | 38.9265 | -121.2688 | No | Partly Cloudy;32-90 F |  |  | 24-0038542 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922781 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | JUMPER | OJS 1 SPAN S/W OF SAP ID 100095176 | 20240306 | 751 | 20240306 | 938 | 2398171 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 642 | 39.01 | -121.1105 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0038579 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1922823 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 35129 | 20240306 | 923 | 20240306 | 958 | 2398337 | 35 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 245 | 38.7975 | -121.2293 | No | Partly Cloudy;32-90 F |  |  | 24-0038641 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922915 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222798057725 | 20240306 | 1427 | 20240306 | 1912 | 2398547 | 285 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1140 | 39.2474 | -121.0123 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0038849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922963 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223186548275 | 20240306 | 1519 | 20240306 | 2037 | 2398739 | 318 | Distribution Circuit | Environmental/External | Lightning | 22 | 2442 | 38.9868 | -120.8802 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0038931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922988 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 7383 | 20240306 | 1636 | 20240306 | 1831 | 2398723 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 5175 | 39.2614 | -121.0127 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0038928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1922985 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 35653 | 20240306 | 1732 | 20240306 | 1922 | 2398775 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1467 | 38.7667 | -121.4328 | No | Clear;32-90 F |  |  | 24-0038960 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923007 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223188148296 | 20240306 | 1830 | 20240306 | 2035 | 2398800 | 125 | Transformer only | Environmental/External | Lightning | 2 | 250 | 38.9874 | -120.8796 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0038965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923010 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 17147 | 20240307 | 816 | 20240307 | 1122 | 2399029 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 744 | 38.884 | -121.4048 | No | Fog;32-90 F |  |  | 24-0039160 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923224 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31117 | 20240307 | 850 | 20240307 | 1051 | 2399106 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 847 | 38.8544 | -120.8556 | No | Clear;32-90 F |  |  | 24-0039206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923249 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 4911 | 20240307 | 1030 | 20240307 | 1426 | 2399279 | 236 | Distribution Circuit | Equipment Failure/Involved | Underground | 98 | 9688 | 38.7273 | -121.189 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0039137 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923253 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225595542880 | 20240307 | 1059 | 20240307 | 1356 | 2399313 | 177 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 531 | 38.8271 | -120.0371 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0039425 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923303 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11609 | 20240307 | 1157 | 20240307 | 1454 | 2399361 | 177 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1239 | 38.69 | -120.9638 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0039250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923262 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20240307 | 1234 | 20240307 | 1316 | 2399405 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 6502 | 39.4655 | -120.8443 | No | Clear;32-90 F | Insulator | Broken | 24-0039082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923280 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1104 | 153701104 | JUMPER | WIRE DOWN 2 N/OF CGC 22013048300 | 20240307 | 1827 | 20240308 | 1111 | 2399670 | 1004 | Distribution Circuit | Equipment Failure/Involved | Overhead | 460 | 61973 | 38.9911 | -121.2932 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0039548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1923338 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 21239 | 20240307 | 1911 | 20240307 | 2050 | 2399653 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 297 | 38.7738 | -120.3012 | No | Fog;Below 32 F |  |  | 24-0039574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923367 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 12729 | 20240308 | 19 | 20240308 | 154 | 2399741 | 95 | Distribution Circuit | Animal | Bird found | 18 | 1710 | 38.6882 | -120.8282 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0039597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923386 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 9171 | 20240308 | 607 | 20240308 | 927 | 2399876 | 200 | Distribution Circuit | Animal | Bird found | 3 | 600 | 38.8975 | -121.2351 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0039710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923536 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222383943390 | 20240308 | 1229 | 20240308 | 2222 | 2400219 | 593 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1779 | 38.8551 | -121.1637 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039927 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923601 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | OCB | 1106/2 | 20240308 | 1525 | 20240308 | 1650 | 2400336 | 85 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1709 | 145265 | 38.7444 | -121.161 | No | Clear;32-90 F |  |  | 24-0039945 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923605 | 0 | EPSS Ckt | N | 2024 | GRD
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 17147 | 20240308 | 1851 | 20240308 | 2225 | 2400463 | 214 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 856 | 38.884 | -121.4048 | No | Clear;32-90 F |  |  | 24-0040018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1923634 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20240308 | 1954 | 20240309 | 112 | 2400481 | 318 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 7950 | 38.6747 | -120.7232 | No | Overcast;32-90 F |  |  | 24-0040052 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923668 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223627037150 | 20240309 | 732 | 20240309 | 1356 | 2400599 | 384 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 768 | 38.6798 | -120.7303 | No | Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0040073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1923724 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 3921 | 20240309 | 1114 | 20240309 | 1254 | 2400745 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 7900 | 39.2223 | -121.2041 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0040089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923749 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222572555820 | 20240309 | 1535 | 20240309 | 1657 | 2400904 | 82 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 246 | 39.1959 | -121.0932 | No | Overcast;32-90 F |  |  | 24-0040127 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1923788 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5225 | 20240309 | 1830 | 20240309 | 2047 | 2400959 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 6302 | 38.8112 | -121.137 | No | Partly Cloudy;32-90 F |  |  | 24-0040141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923795 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30839 | 20240311 | 1530 | 20240312 | 124 | 2401846 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2970 | 38.8331 | -120.8179 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0040635 | OH | Sus | 31686264 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1924158 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50008 | 20240311 | 2151 | 20240311 | 2257 | 2402202 | 66 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2752 | 181632 | 39.2226 | -121.0515 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0040701 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1924194 | 0 | EPSS Ckt | N | 2024 | A C
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 36764 | 20240313 | 851 | 20240313 | 1509 | 2403288 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 600 | 183127 | 38.787 | -120.206 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 24-0040917 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924598 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6185 | 20240313 | 1244 | 20240313 | 1650 | 2403566 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 3936 | 39.0561 | -120.9817 | No | Clear;32-90 F |  |  | 24-0041617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1924739 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DRUM-1101 | 152321101 | FUSE | 9223 | 20240313 | 1415 | 20240313 | 1520 | 2403505 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 65 | 39.276 | -120.705 | No | Clear;32-90 F |  |  | 24-0041669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1924749 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9375 | 20240313 | 1423 | 20240313 | 1610 | 2403683 | 107 | Distribution Circuit | Vegetation | Tree - bark fell into line | 93 | 9951 | 38.8463 | -120.7949 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1924747 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 992864 | 20240313 | 1523 | 20240313 | 1614 | 2403735 | 51 | Distribution Circuit | Company Initiated | Return Circuit Normal | 119 | 6069 | 38.8042 | -120.1031 | No | Clear;32-90 F | Other | Normal | 24-0040917 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924746 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7037 | 20240313 | 1548 | 20240313 | 2032 | 2403754 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 29820 | 39.1141 | -121.1498 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0041735 | OH | Sus | 31686274 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924783 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 992864 | 20240313 | 1755 | 20240313 | 1831 | 2403865 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 119 | 4284 | 38.8042 | -120.1031 | No | Partly Cloudy;32-90 F | Other | Broken | 24-0040917 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924770 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 1239 | 20240313 | 1953 | 20240314 | 509 | 2403904 | 556 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8896 | 38.7517 | -121.3296 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0041746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924790 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 10301 | 20240313 | 2145 | 20240314 | 342 | 2403907 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5712 | 38.7229 | -120.8313 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0041742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924787 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20240313 | 2227 | 20240314 | 525 | 2403955 | 418 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 273 | 97454 | 38.6472 | -120.9177 | No | Clear;32-90 F |  |  | 24-0041784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1924817 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2561 | 20240314 | 258 | 20240314 | 1429 | 2404017 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 51825 | 38.8036 | -120.1099 | No | Clear;Below 32 F | Crossarm- Wood | Broken | 24-0041798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924828 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20240314 | 439 | 20240315 | 1800 | 2404096 | 2241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1077 | 272112 | 39.5596 | -120.8241 | No | Clear-Strong Winds;Below 32 F | Insulator | Broken | 24-0041804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1924834 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20240314 | 631 | 20240314 | 1130 | 2404150 | 283 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1040 | 140786 | 38.7607 | -120.505 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1924853 | 0 | EPSS Ckt | N | 2024 | C+GRD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20240314 | 810 | 20240314 | 1433 | 2404312 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 3052 | 386692 | 38.7716 | -120.8148 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0041878 | OH | Sus | 46211570 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1924901 | 0 | EPSS Ckt | N | 2024 | A B C GRD & TIME OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9369 | 20240314 | 852 | 20240314 | 1216 | 2404434 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 3264 | 38.8737 | -120.9994 | No | Clear;32-90 F |  |  | 24-0042124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925122 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 20240314 | 953 | 20240314 | 1123 | 2404629 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 262 | 23580 | 39.3676 | -121.0458 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925033 | 0 | EPSS Ckt | N | 2024 | A-B TIME OC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | WIRE DOWN 1 SPAN LD SD 20909 | 20240314 | 1000 | 20240314 | 1850 | 2404650 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 719 | 44057 | 38.6008 | -120.6392 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042104 | OH | Sus | 46211740 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1925110 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223230444464 | 20240314 | 1246 | 20240314 | 2025 | 2405114 | 459 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 459 | 38.8816 | -120.865 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0042360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925210 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | SWITCH | 92012 | 20240314 | 1300 | 20240314 | 1319 | 2405161 | 19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1328 | 25232 | 38.8586 | -120.8332 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1925157 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | SWITCH | 3880 | 20240314 | 1530 | 20240314 | 1549 | 2405339 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 235 | 4465 | 38.6722 | -121.0891 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0032231 | UG | Sus | 35316555 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1925226 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222722347699 | 20240314 | 1733 | 20240314 | 1912 | 2405443 | 99 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 198 | 38.9724 | -121.0436 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0042408 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1925232 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | FLYING BELLS EAST OF 32283 | 20240314 | 2142 | 20240315 | 230 | 2405546 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1440 | 39.2289 | -121.1035 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0042372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1925263 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18953 | 20240315 | 544 | 20240315 | 1259 | 2405685 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5655 | 38.7136 | -120.5851 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042543 | OH | Sus | 46211793 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925332 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | FUSE | 7089 | 20240315 | 623 | 20240315 | 847 | 2405700 | 144 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 9648 | 38.7626 | -120.5817 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042606 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925395 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20240315 | 625 | 20240315 | 1414 | 2405702 | 469 | Distribution Circuit | Vegetation | Tree - grew into line | 73 | 34237 | 38.7721 | -120.5821 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0042567 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1925348 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 916723 | 20240315 | 730 | 20240315 | 800 | 2405716 | 30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 90 | 38.9454 | -121.0902 | No | Clear;32-90 F |  |  | 24-0042574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925352 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 37335 | 20240315 | 857 | 20240315 | 1655 | 2405967 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3824 | 39.1743 | -120.8299 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042762 | OH | Sus | 31686654 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1925550 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 8463 | 20240315 | 1143 | 20240315 | 1714 | 2406387 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 16550 | 39.0463 | -120.9816 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0042879 | OH | Sus | 46212431 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1925600 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222553056776 | 20240315 | 1213 | 20240315 | 1430 | 2406452 | 137 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 137 | 39.2226 | -121.0996 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0042768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925553 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 1571 | 20240315 | 1333 | 20240316 | 1654 | 2406583 | 1641 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 50970 | 38.7745 | -120.2979 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042967 | OH | Sus | 35537932 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1925631 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20240315 | 1354 | 20240315 | 1521 | 2406632 | 87 | Distribution Circuit | Environmental/External | Water | 596 | 51852 | 39.0443 | -120.9859 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0042861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1925597 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223943037719 | 20240315 | 1401 | 20240316 | 1759 | 2406640 | 1678 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2920 | 38.6947 | -120.6196 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043061 | OH | Sus | 35537933 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925699 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20521 | 20240315 | 1425 | 20240315 | 1806 | 2406690 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1326 | 38.6497 | -120.676 | No | Clear;32-90 F |  |  | 24-0043004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925648 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222905548768 | 20240315 | 1606 | 20240316 | 934 | 2406820 | 1048 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1048 | 39.0019 | -120.9786 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043021 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925659 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222645253840 | 20240316 | 1209 | 20240316 | 1613 | 2407273 | 244 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 732 | 39.1412 | -121.0683 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925816 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 31173 | 20240316 | 1535 | 20240316 | 2315 | 2407362 | 460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4025 | 39.1905 | -120.809 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043164 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925827 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31113 | 20240316 | 1931 | 20240316 | 2110 | 2407513 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 693 | 38.8566 | -120.8615 | No | Clear;32-90 F |  |  | 24-0043185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925847 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 9145 | 20240316 | 2237 | 20240317 | 30 | 2407545 | 113 | Distribution Circuit | Animal | Bird found | 13 | 1469 | 38.912 | -121.2075 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925876 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 5303 | 20240317 | 112 | 20240317 | 1615 | 2407587 | 903 | Distribution Circuit | 3rd Party | Vehicle | 31 | 27993 | 38.9009 | -121.1287 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0043214 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1925881 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5777 | 20240317 | 716 | 20240317 | 824 | 2407630 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 136 | 39.0269 | -121.0979 | No | Clear;32-90 F |  |  | 24-0043229 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925899 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 30719 | 20240317 | 1113 | 20240317 | 1258 | 2407724 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2310 | 39.3701 | -121.1017 | No | Clear;32-90 F |  |  | 24-0043253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925939 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7595 | 20240317 | 1825 | 20240317 | 1941 | 2407858 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 228 | 38.8243 | -121.45 | No | Clear;32-90 F |  |  | 24-0043282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925958 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 37223 | 20240318 | 813 | 20240318 | 1157 | 2408022 | 224 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1568 | 38.8477 | -121.1004 | No | Clear;32-90 F |  |  | 24-0043539 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926269 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 5191 | 20240318 | 949 | 20240318 | 1605 | 2408180 | 376 | Distribution Circuit | Equipment Failure/Involved | Underground | 45 | 9836 | 38.8809 | -121.1141 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0043470 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1926227 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 6457 | 20240318 | 1016 | 20240318 | 1103 | 2408255 | 47 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1316 | 39.243 | -121.0378 | No | Clear;32-90 F |  |  | 24-0043503 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926247 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222551552360 | 20240318 | 1610 | 20240319 | 112 | 2408644 | 542 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1084 | 39.1003 | -121.1019 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0043732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926348 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8937 | 20240318 | 1628 | 20240318 | 1809 | 2408669 | 101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1010 | 39.218 | -120.9734 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043752 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926357 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRIP-SAVER | 2679 | 20240318 | 1901 | 20240318 | 2011 | 2408772 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 5530 | 38.7074 | -120.9708 | No | Clear;32-90 F |  |  | 24-0043780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926371 | 0 | EPSS Ckt | N | 2024 | AB
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | TRANSFORMER | 222811338415 | 20240318 | 1942 | 20240319 | 937 | 2408836 | 835 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2505 | 38.7174 | -121.0145 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926385 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31133 | 20240318 | 2047 | 20240318 | 2310 | 2408854 | 143 | Distribution Circuit | Animal | Bird found | 2 | 286 | 38.8304 | -120.8781 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043838 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926417 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20240319 | 749 | 20240319 | 938 | 2408980 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4469 | 38.6888 | -120.9245 | No | Clear;32-90 F |  |  | 24-0043957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926573 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222939650304 | 20240319 | 1059 | 20240319 | 1434 | 2409313 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 645 | 39.0429 | -120.9662 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926656 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | SWITCH | 48632 | 20240319 | 1720 | 20240320 | 1223 | 2409479 | 1143 | Distribution Circuit | 3rd Party | Vehicle | 243 | 4214 | 39.32 | -120.379 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0043556 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1926692 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15345 | 20240320 | 515 | 20240320 | 636 | 2409807 | 81 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 324 | 38.9262 | -121.3953 | No | Clear;32-90 F |  |  | 24-0044423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926751 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 3457 | 20240320 | 711 | 20240320 | 821 | 2409882 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 4620 | 38.9166 | -121.0984 | No | Clear;32-90 F |  |  | 24-0044456 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926797 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20240320 | 715 | 20240320 | 855 | 2409886 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2000 | 38.8769 | -121.017 | No | Clear;32-90 F |  |  | 24-0044472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926839 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 50324 | 20240320 | 1112 | 20240320 | 1910 | 2410278 | 478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1953 | 203572 | 38.6953 | -120.818 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0044578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1926938 | 0 | EPSS Ckt | N | 2024 | C GRD & TIME OC
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 38385 | 20240320 | 1714 | 20240320 | 2220 | 2410542 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2448 | 38.8144 | -121.2017 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0044873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927030 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222758437798 | 20240320 | 1809 | 20240320 | 2239 | 2410567 | 270 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 270 | 38.6994 | -121.0345 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0044967 | UG | Sus | 46214170 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927094 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | TRANSFORMER | 222218745140 | 20240321 | 1511 | 20240322 | 20 | 2411328 | 549 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 708 | 38.9033 | -121.2212 | No | Partly Cloudy;32-90 F |  |  | 24-0045285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927233 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 51349 | 20240322 | 809 | 20240322 | 1133 | 2411578 | 204 | Distribution Circuit | Animal | Squirrel | 7 | 384 | 38.9403 | -121.1077 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Normal | 24-0045566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927477 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | FUSE | 9727 | 20240322 | 900 | 20240322 | 1029 | 2411719 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 4717 | 38.998 | -121.0956 | No | Partly Cloudy;32-90 F |  |  | 24-0045545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927470 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | SWITCH | 645945 | 20240322 | 1026 | 20240322 | 1149 | 2411877 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 3154 | 38.609 | -120.8441 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0045449 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927472 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 4303 | 20240322 | 1051 | 20240322 | 1350 | 2411894 | 179 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 179 | 39.6193 | -120.5898 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0045717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927532 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 5355 | 20240322 | 1218 | 20240322 | 1415 | 2411938 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 117 | 38.957 | -121.1192 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0045607 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927487 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1102 | 152591102 | FUSE | 6231 | 20240322 | 1256 | 20240322 | 1843 | 2411863 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 347 | 39.3036 | -120.3384 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Broken | 24-0045687 | OH | Sus | 46215421 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927542 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20665 | 20240322 | 1422 | 20240322 | 1556 | 2412129 | 94 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 376 | 38.6808 | -120.6638 | No | Partly Cloudy;32-90 F |  |  | 24-0045780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927549 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ 2SPANS SS OF CGC 222886060235 | 20240322 | 1612 | 20240322 | 1915 | 2412206 | 183 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 366 | 39.3154 | -120.9807 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0045770 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927545 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10319 | 20240322 | 2105 | 20240322 | 2338 | 2412411 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 76 | 11628 | 38.5661 | -120.7158 | No | Clear-Lightning;32-90 F |  |  | 24-0045874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927611 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223751538205 | 20240322 | 2112 | 20240323 | 1100 | 2412490 | 828 | Transformer only | Environmental/External | Lightning | 1 | 828 | 38.7084 | -120.6891 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045921 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927657 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21335 | 20240322 | 2118 | 20240323 | 1440 | 2412426 | 1042 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5496 | 38.6134 | -120.7032 | No | Overcast-Fog-Rain-Lightning;32-90 F | Insulator | Burned/flashed | 24-0045965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927713 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 20240322 | 2126 | 20240323 | 46 | 2412427 | 200 | Distribution Circuit | Environmental/External | Lightning | 78 | 15600 | 38.7941 | -120.7143 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927618 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18415 | 20240322 | 2156 | 20240323 | 524 | 2412436 | 448 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 6272 | 38.7719 | -120.5759 | No | Clear-Lightning;32-90 F |  |  | 24-0045912 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927648 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20793 | 20240322 | 2208 | 20240323 | 905 | 2412449 | 657 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 10512 | 38.6546 | -120.644 | No | Overcast-Fog-Rain-Lightning;32-90 F | Fuse | Failed/Faulted | 24-0045947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927698 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 1571 | 20240322 | 2209 | 20240323 | 1013 | 2412452 | 724 | Distribution Circuit | Environmental/External | Lightning | 68 | 12924 | 38.7745 | -120.2979 | No | Clear-Lightning;Below 32 F | Pole-Wood | Burned/flashed | 24-0045897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927633 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2173 | 20240323 | 634 | 20240323 | 831 | 2412612 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 6669 | 38.6947 | -120.7187 | No | Overcast-Fog;32-90 F |  |  | 24-0045936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927674 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223675033110 | 20240323 | 651 | 20240323 | 1239 | 2412614 | 348 | Transformer only | Environmental/External | Lightning | 1 | 348 | 38.5684 | -120.7158 | No | Partly Cloudy;32-90 F | Transformer (OH) | Burned/flashed | 24-0046014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927740 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 865334 | 20240323 | 724 | 20240323 | 1043 | 2412637 | 199 | Distribution Circuit | Animal | Other | 2809 | 552243 | 38.6569 | -120.9929 | No | Partly Cloudy;32-90 F | Capacitor | Burned/flashed | 24-0045925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1927661 | 0 | EPSS Ckt | N | 2024 | A B C GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223678533017 | 20240323 | 1012 | 20240323 | 1536 | 2412744 | 324 | Transformer only | Environmental/External | Lightning | 1 | 324 | 38.5659 | -120.7148 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0046033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927755 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 173478 | 20240323 | 1030 | 20240323 | 1455 | 2412725 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3710 | 39.0043 | -121.0288 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0045972 | OH | Sus | 31687674 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927719 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7747 | 20240323 | 1040 | 20240323 | 1834 | 2412683 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 20382 | 39.2406 | -121.1926 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0045942 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927688 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20240323 | 1200 | 20240323 | 1740 | 2412835 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 715 | 68771 | 38.773 | -120.2933 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0046007 | OH | Sus | 46215640 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927734 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18415 | 20240323 | 1408 | 20240323 | 1915 | 2412911 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4298 | 38.7719 | -120.5759 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0046092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927799 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 5257 | 20240323 | 1833 | 20240323 | 2028 | 2413054 | 115 | Distribution Circuit | Environmental/External | Lightning | 52 | 5980 | 39.2088 | -121.2438 | No | Overcast-Lightning;32-90 F | Transformer (OH) | Broken | 24-0046094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927801 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 40093 | 20240323 | 1957 | 20240324 | 106 | 2413127 | 309 | Distribution Circuit | 3rd Party | Vehicle | 11 | 3399 | 38.7817 | -121.2424 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0046068 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927812 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | FUSE | 4285 | 20240325 | 615 | 20240325 | 1257 | 2413721 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2010 | 39.317 | -120.5482 | No | Partly Cloudy-Fog;Below 32 F | Pothead(Riser Termination) | Failed/Faulted | 24-0046296 | OH | Sus | 31687787 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927988 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1102 | 152591102 | FUSE | 6819 | 20240325 | 2148 | 20240326 | 1143 | 2414508 | 835 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 9946 | 39.3039 | -120.3364 | No | Partly Cloudy-Fog;Below 32 F | Connector or Splice (OH) | Arcing | 24-0046707 | OH | Sus | 31688006 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1928241 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 98319 | 20240326 | 644 | 20240326 | 913 | 2414612 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 11131 | 38.9311 | -121.0956 | No | Overcast;32-90 F |  |  | 24-0046768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928287 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223077855897 | 20240326 | 1003 | 20240326 | 1518 | 2415515 | 315 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 315 | 39.1965 | -120.9148 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0046930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928494 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221672544771 | 20240326 | 1040 | 20240326 | 1133 | 2415548 | 53 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 53 | 38.8944 | -121.4134 | No | Partly Cloudy;32-90 F |  |  | 24-0046909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1928486 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222851650807 | 20240326 | 1249 | 20240326 | 1859 | 2415661 | 370 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1480 | 39.0575 | -120.997 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0047026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928530 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S @ FLYING BELLS 1/N/OF 21065 | 20240326 | 1325 | 20240326 | 1509 | 2415725 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 227 | 10674 | 38.7713 | -120.7704 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0046901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1928519 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39055 | 20240326 | 1347 | 20240326 | 1518 | 2415750 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 455 | 39.0419 | -121.0691 | No | Clear;32-90 F |  |  | 24-0047080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928538 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 5229 | 20240326 | 1350 | 20240326 | 1456 | 2415754 | 66 | Distribution Circuit | Animal | Squirrel | 40 | 2640 | 38.913 | -121.2561 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0047020 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928527 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 3775 | 20240326 | 1649 | 20240326 | 2013 | 2415889 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 5304 | 38.8999 | -120.8951 | No | Clear;32-90 F |  |  | 24-0047137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928555 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 95773 | 20240326 | 1733 | 20240326 | 2003 | 2415914 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 400 | 38.897 | -120.8932 | No | Clear;32-90 F |  |  | 24-0047154 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928567 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 8151 | 20240326 | 1906 | 20240326 | 1947 | 2415960 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 41 | 39.2292 | -121.0448 | No | Clear;32-90 F |  |  | 24-0047157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928570 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 2597 | 20240326 | 2019 | 20240326 | 2134 | 2416033 | 75 | Distribution Circuit | Equipment Failure/Involved | Underground | 69 | 5175 | 38.8252 | -121.2582 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0047107 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1928578 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6383 | 20240327 | 637 | 20240327 | 834 | 2416179 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 155 | 18135 | 39.0911 | -120.9507 | No | Overcast;32-90 F |  |  | 24-0047293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928695 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | JUMPER | OJ 1 P/SS OF CGC 223435868738 | 20240327 | 1228 | 20240328 | 1435 | 2416560 | 1567 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1771 | 39.5477 | -120.783 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0047603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1928871 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7365 | 20240327 | 1406 | 20240327 | 1538 | 2416636 | 92 | Distribution Circuit | 3rd Party | Metallic Balloon | 36 | 3312 | 39.2582 | -121.1716 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0047609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928873 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | SWITCH | 2141 | 20240327 | 1622 | 20240327 | 1854 | 2416744 | 152 | Distribution Circuit | Equipment Failure/Involved | Overhead | 351 | 53352 | 39.2216 | -121.079 | No | Overcast-Rain;32-90 F | Crossarm- Wood | Broken | 24-0047650 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1928882 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 19111 | 20240327 | 1705 | 20240328 | 1929 | 2416761 | 1584 | Distribution Circuit | Equipment Failure/Involved | Underground | 140 | 64471 | 38.7195 | -121.0865 | No | Overcast;32-90 F | Conductor- Underground | Deteriorated | 24-0047683 | UG | Sus | 46217076 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928895 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9317 | 20240327 | 1926 | 20240327 | 2052 | 2416827 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 139 | 11954 | 38.9045 | -120.9967 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0047694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928900 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 9817 | 20240327 | 2257 | 20240328 | 434 | 2416907 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8762 | 39.223 | -121.091 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 24-0047737 | OH | Sus | 46217075 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1928941 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1581 | 20240328 | 644 | 20240328 | 822 | 2417038 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1632 | 38.5858 | -120.9347 | No | Overcast-Fog;32-90 F |  |  | 24-0047797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1928991 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 6611 | 20240328 | 934 | 20240328 | 1415 | 2417256 | 281 | Distribution Circuit | Animal | Other | 1 | 281 | 38.7152 | -120.842 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0047942 | OH | Sus | 46217323 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929152 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222483050053 | 20240328 | 1147 | 20240328 | 1324 | 2417401 | 97 | Transformer only | Animal | Squirrel | 1 | 97 | 39.0356 | -121.1262 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929182 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 50550 | 20240328 | 1319 | 20240328 | 2324 | 2417480 | 605 | Distribution Circuit | 3rd Party | Vehicle | 268 | 61946 | 38.8511 | -121.1794 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0048014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929181 | 0 | EPSS Ckt | N | 2024 | BC GRD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7935 | 20240328 | 1558 | 20240330 | 1642 | 2417475 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 108188 | 39.6302 | -120.5447 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0048163 | OH | Sus | 46217702 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929207 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | TRANSFORMER | 223145838720 | 20240328 | 1705 | 20240328 | 2310 | 2417509 | 365 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1460 | 38.7243 | -120.8981 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0048156 | OH | Sus | 46217477 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929206 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SECTIONALIZER | 2626 | 20240328 | 1706 | 20240330 | 1610 | 2417597 | 2824 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 175088 | 39.6182 | -120.5917 | No | Overcast;32-90 F |  |  | 24-0048168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929210 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | RECLOSER | 556218 | 20240328 | 1821 | 20240329 | 348 | 2417631 | 567 | Distribution Circuit | 3rd Party | Vehicle | 649 | 180195 | 38.6342 | -120.9454 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0048166 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929208 | 0 | EPSS Ckt | N | 2024 | TIME OC B GRD
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | SWITCH | 2127 | 20240328 | 2112 | 20240329 | 236 | 2417704 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5184 | 39.2234 | -121.0482 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0048047 | OH | Sus | 35539719 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929231 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 940676 | 20240329 | 641 | 20240329 | 917 | 2417790 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 232 | 28678 | 38.7476 | -120.8598 | No | Partly Cloudy;32-90 F |  |  | 24-0048226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1929288 | 0 | EPSS Ckt | N | 2024 | A & C
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30353 | 20240329 | 643 | 20240329 | 823 | 2417787 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1400 | 39.1214 | -121.0293 | No | Partly Cloudy;32-90 F |  |  | 24-0048254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929307 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 82569 | 20240329 | 717 | 20240329 | 901 | 2417783 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 748 | 38.9742 | -121.0662 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0048240 | OH | Sus | 46217708 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929295 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S 3 SPANS SS OF 223138542610 | 20240329 | 1033 | 20240329 | 1138 | 2417996 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 65 | 38.8324 | -120.8959 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0048320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929381 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | RECLOSER | 1050 | 20240329 | 1125 | 20240329 | 1209 | 2418044 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 1144 | 38.7916 | -121.2372 | No | Overcast;32-90 F |  |  | 24-0048362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1929397 | 0 | EPSS Ckt | N | 2024 | ABC GRD
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 5117 | 20240329 | 1127 | 20240329 | 1312 | 2418047 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 2972 | 38.8054 | -121.2425 | No | Partly Cloudy;32-90 F |  |  | 24-0048426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929416 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | OTHER | SO-ND534414 | 20240329 | 1145 | 20240329 | 1228 | 2418096 | 43 | Distribution Circuit | Company Initiated | Return Circuit Normal | 140 | 1702 | 38.7156 | -121.0891 | No | Overcast;32-90 F | Conductor- Underground | Normal | 24-0047683 | UG | Sus | 46217076 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929425 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20240329 | 1311 | 20240330 | 212 | 2418148 | 781 | Distribution Circuit | 3rd Party | Vehicle | 449 | 96103 | 39.0473 | -121.0486 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken | 24-0048439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929419 | 0 | EPSS Ckt | N | 2024 | B & GRD
SIERRA | PLACER | PENRYN-1106 | 152561106 | SWITCH | 751 | 20240329 | 1412 | 20240329 | 1421 | 2418227 | 9 | Distribution Circuit | 3rd Party | Vehicle | 171 | 1539 | 38.8395 | -121.2065 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0048014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929436 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3987 | 20240330 | 907 | 20240330 | 953 | 2418916 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 230 | 39.2342 | -121.1097 | No | Overcast;32-90 F |  |  | 24-0048704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929585 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222853162904 | 20240331 | 1049 | 20240331 | 1545 | 2419496 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 592 | 39.3897 | -120.9918 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0048919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929729 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6199 | 20240401 | 644 | 20240401 | 909 | 2419827 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 116 | 16820 | 39.0825 | -120.9565 | No | Clear;32-90 F |  |  | 24-0049033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1929858 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12567 | 20240401 | 1313 | 20240401 | 1450 | 2420286 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 97 | 38.6403 | -120.6541 | No | Clear;32-90 F |  |  | 24-0049304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930007 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222680156554 | 20240401 | 1647 | 20240401 | 1815 | 2420418 | 88 | Transformer only | Vegetation | Tree - fell into line | 15 | 1320 | 39.2157 | -121.0547 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930016 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20240402 | 705 | 20240402 | 1107 | 2420659 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 411 | 44888 | 38.7121 | -120.9501 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0049478 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Multi-Fault | 0 | No | Yes | No | 1930108 | 0 | EPSS Ckt | N | 2024 | ABC GRD TIME
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18965 | 20240402 | 847 | 20240402 | 910 | 2420880 | 23 | Distribution Circuit | Animal | Squirrel | 1 | 23 | 38.7259 | -120.8343 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0049566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930246 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21111 | 20240402 | 929 | 20240402 | 1120 | 2420886 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 666 | 38.6937 | -120.7115 | No | Clear;32-90 F |  |  | 24-0049645 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930291 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20240402 | 1040 | 20240402 | 1416 | 2420872 | 216 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1512 | 39.5206 | -120.9976 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0049563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930238 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | TRANSFORMER | 222508544099 | 20240402 | 1556 | 20240402 | 2355 | 2421190 | 479 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 958 | 38.8748 | -121.1198 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0049921 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1930352 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | FUSE | 4425 | 20240402 | 2007 | 20240402 | 2326 | 2421310 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 17313 | 38.7145 | -121.058 | No | Clear;32-90 F |  |  | 24-0049955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1930380 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | JUMPER | OJ'S 1 POLE EAST OF CGC 222958437057 | 20240403 | 833 | 20240403 | 1409 | 2421464 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1680 | 38.6794 | -120.9647 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0050002 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930424 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223019755236 | 20240403 | 835 | 20240403 | 957 | 2421581 | 82 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 82 | 39.1783 | -120.9356 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930495 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN | 20240403 | 1145 | 20240403 | 1645 | 2421798 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1800 | 38.6252 | -120.7568 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0050247 | OH | Sus | 46219830 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1930629 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222268055983 | 20240403 | 1200 | 20240403 | 1334 | 2421820 | 94 | Transformer only | Company Initiated | Construction Activity/equip- company | 4 | 376 | 39.2013 | -121.2003 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0050171 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1930611 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | SWITCH | 50493 | 20240403 | 1920 | 20240404 | 350 | 2422090 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1020 | 38.8061 | -121.3072 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0050375 | OH | Sus | 35541533 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930687 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 34421 | 20240404 | 17 | 20240404 | 343 | 2422166 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 84 | 17304 | 39.0048 | -121.1482 | No | Overcast;32-90 F |  |  | 24-0050483 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930737 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8249 | 20240404 | 656 | 20240404 | 846 | 2422215 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 8800 | 39.0802 | -121.1325 | No | Overcast;32-90 F |  |  | 24-0050556 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930785 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | TRANSFORMER | 222566748570 | 20240404 | 918 | 20240404 | 1101 | 2422338 | 103 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 103 | 38.9967 | -121.0981 | No | Overcast-Rain;32-90 F | Fuse | Broken | 24-0050680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1930844 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223123536853 | 20240404 | 928 | 20240404 | 1012 | 2422341 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 86 | 38.6736 | -120.9076 | No | Overcast-Drizzle;32-90 F | Insulator | Broken | 24-0050584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930809 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | SWITCH | 1639 | 20240404 | 1534 | 20240405 | 101 | 2422894 | 567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 35076 | 39.2265 | -121.1903 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Deteriorated | 24-0050767 | OH | Sus | 35541790 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930903 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 34869 | 20240404 | 1608 | 20240404 | 2103 | 2422978 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 9913 | 38.7977 | -121.2497 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1930927 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240405 | 421 | 20240405 | 843 | 2423383 | 262 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2683 | 297569 | 38.6943 | -120.6784 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931045 | 0 | EPSS Ckt | N | 2024 | A C TIME OC
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 900864 | 20240405 | 610 | 20240405 | 909 | 2423547 | 179 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 7876 | 38.9113 | -120.8245 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 24-0051133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931056 | 0 | EPSS Ckt | N | 2024 | BC
SIERRA | PLACER | DEL MAR-2109 | 152582109 | FUSE | 825891 | 20240405 | 949 | 20240405 | 1014 | 2423911 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 300 | 38.8318 | -121.2192 | No | Overcast-Fog;32-90 F | Insulator | Broken | 24-0051332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1931231 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 2489 | 20240405 | 1015 | 20240405 | 1250 | 2423958 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1085 | 38.7476 | -120.6104 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0051431 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931268 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | RECLOSER | 980728 | 20240405 | 1346 | 20240405 | 1628 | 2424204 | 162 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 327 | 43178 | 38.832 | -121.186 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0051475 | UG | Sus | 46221231 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1931290 | 0 | EPSS Ckt | N | 2024 | C- GRD- TIME OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31339 | 20240405 | 1509 | 20240405 | 1608 | 2424336 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 177 | 38.895 | -120.9936 | No | Partly Cloudy;32-90 F |  |  | 24-0051538 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931328 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | INTERRUPTER | 51686 | 20240405 | 1803 | 20240406 | 807 | 2424792 | 844 | Distribution Circuit | Equipment Failure/Involved | Underground | 1760 | 278404 | 38.805 | -121.2938 | No | Partly Cloudy;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0051613 | UG | Sus | 46221401 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931377 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222891058611 | 20240406 | 1106 | 20240406 | 1746 | 2425235 | 400 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1600 | 39.2714 | -120.9796 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0051763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1931534 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20255 | 20240406 | 1738 | 20240406 | 2003 | 2425418 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 33350 | 38.6208 | -120.8489 | No | Overcast;32-90 F |  |  | 24-0051824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931568 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32161 | 20240407 | 832 | 20240407 | 903 | 2425622 | 31 | Distribution Circuit | Animal | Bird found | 23 | 713 | 38.7897 | -121.2516 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0051872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1931616 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | SWITCH | 6665 | 20240407 | 1156 | 20240407 | 2012 | 2425708 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 38154 | 39.3223 | -120.381 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0051888 | OH | Sus | 46221763 | NORTH VALLEY AND SIERRA | APR | Open Circuit | 0 | No | No | No | 1931643 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | FUSE | 40951 | 20240408 | 455 | 20240408 | 1107 | 2425901 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 7440 | 39.302 | -120.3892 | No | Clear;Below 32 F | Cutout- fuse holder | Broken | 24-0051972 | OH | Sus | 31690005 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1931729 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 35251 | 20240408 | 612 | 20240408 | 1127 | 2425911 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5985 | 38.8314 | -121.1862 | No | Clear;32-90 F | Insulator | Broken | 24-0052031 | OH | Sus | 31689949 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931843 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | 4 POLE SS OF CGC 222832456183 | 20240408 | 1719 | 20240408 | 2050 | 2426520 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 211 | 39.2045 | -121.0017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1931924 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 40507 | 20240409 | 710 | 20240409 | 800 | 2426713 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 450 | 38.8738 | -121.1401 | No | Clear;32-90 F |  |  | 24-0052460 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1932072 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11707 | 20240409 | 917 | 20240409 | 1109 | 2426884 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2352 | 38.6924 | -120.9238 | No | Clear;32-90 F |  |  | 24-0052573 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1932218 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7671 | 20240409 | 1000 | 20240409 | 1138 | 2426957 | 98 | Distribution Circuit | Animal | Bird found | 44 | 4312 | 38.8956 | -121.4145 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0052588 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1932226 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 2567 | 20240409 | 1659 | 20240410 | 134 | 2427350 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2642 | 38.8242 | -121.4698 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0052826 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1932282 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223187054669 | 20240409 | 1821 | 20240409 | 1908 | 2427384 | 47 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 47 | 39.1634 | -120.8768 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 24-0052832 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1932287 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 145584 | 20240410 | 1055 | 20240410 | 1147 | 2427808 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 96 | 4992 | 39.1016 | -120.954 | No | Clear;32-90 F |  |  | 24-0053069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1932519 | 0 | EPSS Ckt | N | 2024 | TIME OC C GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 75877 | 20240410 | 1137 | 20240410 | 1155 | 2427856 | 18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 72 | 38.859 | -121.4633 | No | Clear;32-90 F |  |  | 24-0053066 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1932516 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 42584 | 20240410 | 1608 | 20240410 | 1730 | 2428033 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 238 | 19516 | 39.2295 | -121.2048 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0053147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1932552 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | LINCOLN-1101 | 153701101 | TRANSFORMER | 222057645760 | 20240411 | 1008 | 20240411 | 1525 | 2428485 | 317 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 317 | 38.9207 | -121.2778 | No | Clear;32-90 F | Transformer | Broken | 24-0053518 | OH | Sus | 46227492 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1932799 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | SWITCH | 481 | 20240411 | 1100 | 20240411 | 1423 | 2428532 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 20503 | 39.2168 | -121.2011 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0053361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1932793 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 9261 | 20240412 | 1020 | 20240412 | 1203 | 2429339 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2266 | 39.2862 | -121.0551 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0053963 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1933074 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8639 | 20240412 | 1205 | 20240412 | 1303 | 2429487 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 638 | 39.145 | -120.9763 | No | Partly Cloudy;32-90 F |  |  | 24-0054110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1933131 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222293043719 | 20240412 | 1740 | 20240412 | 1829 | 2429908 | 49 | Transformer only | Animal | Squirrel | 2 | 98 | 38.8645 | -121.1962 | No | Overcast;32-90 F | Bushing | Normal | 24-0054265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1933194 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 938135 | 20240412 | 2218 | 20240413 | 943 | 2430004 | 685 | Distribution Circuit | 3rd Party | Vehicle | 32 | 21920 | 38.9 | -121.2193 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0054304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1933231 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223033037022 | 20240413 | 442 | 20240413 | 630 | 2430100 | 108 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 108 | 38.6784 | -120.9385 | No | Overcast;32-90 F | Connector or Splice (OH) | Burned Open | 24-0054331 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1933260 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 3125 | 20240413 | 1331 | 20240413 | 1454 | 2430467 | 83 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1494 | 38.8521 | -121.1708 | No | Partly Cloudy;32-90 F |  |  | 24-0054488 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1933363 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20240413 | 2002 | 20240413 | 2120 | 2430930 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1560 | 38.8769 | -121.017 | No | Overcast;32-90 F |  |  | 24-0054577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1933442 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 4081 | 20240414 | 1016 | 20240414 | 1042 | 2431215 | 26 | Distribution Circuit | Animal | Squirrel | 61 | 1586 | 38.9565 | -121.1047 | No | Overcast;32-90 F | Pothead(Riser Termination) | Normal | 24-0054669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1933540 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20289 | 20240415 | 938 | 20240415 | 1148 | 2431775 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1143 | 38.7615 | -120.9882 | No | Clear;32-90 F |  |  | 24-0054960 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1933813 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 30063 | 20240415 | 1437 | 20240415 | 1542 | 2432071 | 65 | Distribution Circuit | Animal | Squirrel | 2 | 130 | 38.8544 | -121.1368 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0055115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1933859 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | JUMPER | SS JUMPERS TO 6197 | 20240415 | 2108 | 20240416 | 203 | 2432249 | 295 | Distribution Circuit | 3rd Party | Vehicle | 1 | 295 | 38.7244 | -121.2258 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0055183 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1933889 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 50172 | 20240416 | 1233 | 20240417 | 49 | 2432732 | 736 | Distribution Circuit | 3rd Party | Vehicle | 345 | 40609 | 38.9458 | -121.1226 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 24-0055436 | OH | Sus | 35545829 | NORTH VALLEY AND SIERRA | APR | Multi-Fault | 0 | No | Yes | No | 1934152 | 0 | EPSS Ckt | N | 2024 | A-B-C- GRD- TIME OC
SIERRA | PLACER | WISE-1101 | 152271101 | TRANSFORMER | 222567044490 | 20240416 | 1545 | 20240416 | 1710 | 2432882 | 85 | Transformer only | Animal | Squirrel | 3 | 255 | 38.8849 | -121.0991 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0055602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934212 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222353546103 | 20240416 | 1601 | 20240417 | 805 | 2432891 | 964 | Transformer only | 3rd Party | Dig in- 3rd party | 1 | 964 | 38.9295 | -121.1738 | No | Partly Cloudy;32-90 F | Transformer | Broken | 24-0055568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1934196 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 7989 | 20240417 | 612 | 20240417 | 837 | 2433120 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 7830 | 38.6663 | -120.8941 | No | Clear;32-90 F |  |  | 24-0055786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934377 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 33541 | 20240417 | 822 | 20240417 | 947 | 2433203 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2720 | 38.8106 | -121.18 | No | Partly Cloudy;32-90 F |  |  | 24-0055824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1934470 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 34869 | 20240417 | 908 | 20240417 | 1342 | 2433291 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 7058 | 38.7977 | -121.2497 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0055843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934490 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223218042800 | 20240417 | 1156 | 20240417 | 1258 | 2433494 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 186 | 38.8366 | -120.8717 | No | Partly Cloudy;32-90 F | Secondary | Burned/flashed | 24-0055907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1934511 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | OLETA-1101 | 163541101 | FUSE | 12055 | 20240417 | 1406 | 20240417 | 1604 | 2433598 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 3304 | 38.5385 | -120.965 | No | Partly Cloudy;32-90 F |  |  | 24-0056072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1934565 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | FUSE | 19443 | 20240417 | 1533 | 20240418 | 39 | 2433655 | 546 | Distribution Circuit | Equipment Failure/Involved | Underground | 156 | 29724 | 38.6805 | -121.0445 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0056100 | UG | Sus | 35546130 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934572 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 22345 | 20240418 | 1131 | 20240418 | 1438 | 2434129 | 187 | Distribution Circuit | 3rd Party | Vehicle | 33 | 6171 | 38.6638 | -120.8945 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0056419 | OH | Sus | 46230679 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1934764 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | TSB 1 S/O 20847 | 20240418 | 2006 | 20240419 | 122 | 2434413 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5056 | 38.7559 | -120.6785 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0056638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1934808 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | JUMPER | OJ SS OF CGC 222319845813 | 20240418 | 2113 | 20240419 | 230 | 2434433 | 317 | Distribution Circuit | 3rd Party | Vehicle | 1 | 317 | 38.9225 | -121.1858 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0056654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1934816 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 6563 | 20240419 | 607 | 20240419 | 758 | 2434569 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 6105 | 39.0004 | -121.1276 | No | Clear;32-90 F |  |  | 24-0056713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1934866 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 452800 | 20240419 | 706 | 20240419 | 724 | 2434602 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3266 | 58788 | 39.2411 | -121.0323 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0056693 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934856 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225151841340 | 20240419 | 741 | 20240419 | 1412 | 2434846 | 391 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 5083 | 38.7877 | -120.1934 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0056822 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1934998 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 452800 | 20240419 | 1021 | 20240419 | 1059 | 2434856 | 32 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3081 | 117078 | 39.2411 | -121.0323 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0056825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1934999 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | SWITCH | 1024 | 20240419 | 1350 | 20240419 | 1416 | 2435093 | 26 | Distribution Circuit | Equipment Failure/Involved | Underground | 73 | 1898 | 38.8036 | -121.2612 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0056936 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935042 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 9919 | 20240419 | 1542 | 20240419 | 1850 | 2435159 | 188 | Distribution Circuit | Animal | Bird found | 36 | 6771 | 38.9632 | -121.1358 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0057069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1935069 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8171 | 20240419 | 1656 | 20240419 | 1828 | 2435209 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2852 | 39.1114 | -121.144 | No | Clear;32-90 F |  |  | 24-0057070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935070 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20240419 | 2002 | 20240419 | 2146 | 2435274 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 5928 | 38.9142 | -120.9386 | No | Clear;32-90 F |  |  | 24-0057082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935084 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222232055960 | 20240420 | 1312 | 20240420 | 1855 | 2435553 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 39.2005 | -121.2136 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057187 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1935223 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ AT CORNER POLE TWD CGC 222641052666 | 20240420 | 1420 | 20240420 | 1600 | 2435565 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 100 | 39.1095 | -121.0693 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0057184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935221 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 4011 | 20240421 | 751 | 20240421 | 1047 | 2435814 | 176 | Distribution Circuit | Animal | Squirrel | 1 | 176 | 38.9629 | -121.0404 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0057294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1935307 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 2045 | 20240421 | 1019 | 20240421 | 1304 | 2435828 | 165 | Distribution Circuit | Animal | Squirrel | 75 | 12375 | 38.6682 | -120.9388 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0057317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1935324 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 3729 | 20240421 | 1146 | 20240421 | 1245 | 2435854 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 3422 | 39.1397 | -121.0574 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0057293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935316 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | OTHER | HOT WIRE DOWN 16882 YOU BET RD | 20240421 | 1206 | 20240421 | 1609 | 2435860 | 243 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 172 | 13380 | 39.1905 | -120.9368 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0057314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | Yes | 1935322 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 6447 | 20240421 | 1333 | 20240421 | 1438 | 2435891 | 65 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 1885 | 39.1143 | -121.0741 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0057321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935328 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OCB | 1104/2 | 20240422 | 226 | 20240422 | 245 | 2436096 | 19 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2656 | 42505 | 39.2314 | -121.0346 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0057360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935364 | 0 | EPSS Ckt | N | 2024 | none
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 32145 | 20240422 | 744 | 20240422 | 914 | 2436183 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 360 | 39.0479 | -121.0473 | No | Clear;32-90 F |  |  | 24-0057435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935443 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 6481 | 20240422 | 938 | 20240422 | 1149 | 2436404 | 131 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 2272 | 38.9632 | -121.1341 | No | Clear;32-90 F |  |  | 24-0057544 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1935538 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9987 | 20240422 | 1148 | 20240422 | 1329 | 2436611 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2424 | 38.919 | -120.9164 | No | Clear;32-90 F |  |  | 24-0057634 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935569 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 35713 | 20240422 | 2028 | 20240422 | 2156 | 2436975 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 352 | 38.975 | -121.1367 | No | Clear;32-90 F |  |  | 24-0057780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935637 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 35598 | 20240423 | 1005 | 20240423 | 1549 | 2437370 | 344 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 1032 | 38.7639 | -120.9263 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0057009 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935808 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 36764 | 20240423 | 1021 | 20240423 | 1440 | 2437387 | 259 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 11914 | 38.787 | -120.206 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0057950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935812 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJ 1 E/OF MTR# 1005205910 | 20240423 | 1032 | 20240423 | 1355 | 2437284 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 406 | 38.7324 | -120.6613 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0057900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935766 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ 1 SS OF CGC# 223765934280 | 20240424 | 844 | 20240424 | 1149 | 2437901 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 185 | 38.6004 | -120.6839 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0058358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935986 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 20973 | 20240424 | 1019 | 20240424 | 1110 | 2438103 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 918 | 38.7276 | -120.5699 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0058458 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1936128 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20240424 | 1847 | 20240425 | 132 | 2438417 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 938 | 23775 | 38.7391 | -120.6681 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0058687 | OH | Sus | 31692140 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1936196 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 20240424 | 2301 | 20240425 | 220 | 2438551 | 181 | Distribution Circuit | Animal | Other | 3692 | 165097 | 38.9144 | -121.0197 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0058715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Multi-Fault | 0 | No | No | No | 1936223 | 0 | EPSS Ckt | N | 2024 | A-C- GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7671 | 20240425 | 744 | 20240425 | 855 | 2438624 | 71 | Distribution Circuit | Animal | Bird found | 44 | 3124 | 38.8956 | -121.4145 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0058788 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1936301 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 100000032501 | 20240426 | 1820 | 20240427 | 125 | 2440150 | 425 | Transformer only | Environmental/External | Lightning | 2 | 850 | 38.9886 | -121.0187 | No | Partly Cloudy-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936834 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222804232757 | 20240426 | 1833 | 20240426 | 2100 | 2440156 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 294 | 38.562 | -121.0206 | No | Clear-Lightning;32-90 F | Fuse | Failed/Faulted | 24-0059535 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936843 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5087 | 20240426 | 1840 | 20240426 | 2144 | 2440134 | 184 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1104 | 38.8004 | -121.1641 | No | Partly Cloudy;32-90 F | Woodpin | Broken | 24-0059507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1936821 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222790448300 | 20240426 | 1953 | 20240427 | 105 | 2440216 | 312 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 624 | 38.9886 | -121.0194 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059527 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936838 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | TRANSFORMER | 222804232757 | 20240427 | 621 | 20240427 | 1245 | 2440374 | 384 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 768 | 38.562 | -121.0206 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0059590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936914 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 9435 | 20240427 | 640 | 20240427 | 816 | 2440380 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1536 | 38.8933 | -121.2203 | No | Clear;32-90 F |  |  | 24-0059591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1936916 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRANSFORMER | 222832449486 | 20240427 | 1015 | 20240427 | 1518 | 2440494 | 303 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 303 | 39.021 | -121.004 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0059621 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936966 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 55945 | 20240427 | 1217 | 20240427 | 1328 | 2440565 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 71 | 38.5839 | -120.7367 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0059624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1936967 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 34869 | 20240427 | 1355 | 20240427 | 1433 | 2440624 | 38 | Distribution Circuit | 3rd Party | Metallic Balloon | 77 | 2926 | 38.7977 | -121.2497 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0059657 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1936984 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 21093 | 20240428 | 1245 | 20240428 | 1455 | 2441070 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2730 | 38.73 | -120.7919 | No | Clear;32-90 F | Insulator | Broken | 24-0059774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1937098 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18773 | 20240429 | 551 | 20240429 | 818 | 2441402 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 136 | 19992 | 38.6472 | -120.9436 | No | Clear;32-90 F |  |  | 24-0059875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1937201 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | TRANSFORMER | T0608 | 20240430 | 155 | 20240430 | 707 | 2442132 | 312 | Transformer only | Equipment Failure/Involved | Underground | 15 | 4680 | 38.6761 | -120.9906 | No | Clear;32-90 F | Secondary | Broken | 24-0060251 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1937488 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | TRANSFORMER | 223995761006 | 20240430 | 733 | 20240430 | 2045 | 2442234 | 792 | Transformer only | Environmental/External | Lightning | 1 | 792 | 39.3333 | -120.5878 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1937696 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18793 | 20240430 | 1031 | 20240430 | 1317 | s1937745 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1660 | 38.6472 | -120.6835 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0060511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1937745 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222635753082 | 20240430 | 1038 | 20240430 | 1440 | 2442592 | 242 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 726 | 39.1201 | -121.0715 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060431 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1937709 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20240430 | 1102 | 20240501 | 222 | 2442618 | 920 | Distribution Circuit | 3rd Party | Vehicle | 375 | 28029 | 38.8101 | -121.1629 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0060406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1937703 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221792147909 | 20240430 | 1142 | 20240501 | 41 | 2442659 | 779 | Transformer only | Animal | Other | 3 | 2337 | 38.9803 | -121.3704 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0060477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1937727 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15473 | 20240430 | 2024 | 20240430 | 2254 | 2443010 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1800 | 38.9617 | -121.3599 | No | Clear;32-90 F |  |  | 24-0060674 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1937812 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32941 | 20240501 | 713 | 20240501 | 816 | 2443085 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 315 | 39.2552 | -121.21 | No | Clear;32-90 F |  |  | 24-0060746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1937865 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222904539400 | 20240501 | 1922 | 20240501 | 1933 | 2443731 | 11 | Transformer only | Animal | Squirrel | 2 | 22 | 38.7439 | -120.9831 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0061092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938112 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223802636713 | 20240501 | 2200 | 20240502 | 324 | 2443823 | 324 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1296 | 38.6703 | -120.6692 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938137 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5085 | 20240502 | 600 | 20240502 | 758 | 2443860 | 118 | Distribution Circuit | Animal | Bird found | 72 | 8496 | 38.7933 | -121.1712 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0061158 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938164 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10559 | 20240502 | 610 | 20240502 | 746 | 2443864 | 96 | Distribution Circuit | Animal | Bird found | 89 | 8544 | 38.7897 | -120.9324 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061165 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1938170 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 2045 | 20240502 | 1122 | 20240502 | 1247 | 2444239 | 85 | Distribution Circuit | Animal | Squirrel | 75 | 6375 | 38.6682 | -120.9388 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0061301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938363 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 30063 | 20240502 | 1325 | 20240502 | 1407 | 2444286 | 42 | Distribution Circuit | Animal | Squirrel | 2 | 84 | 38.8544 | -121.1368 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0061370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938396 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY SUB | 15210 | OCB | 52G | 20240502 | 1700 | 20240502 | 1706 | 2444508 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 852 | 39.3638 | -120.7923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0010940 | OH | Sus | 31624660 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1938421 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 586723 | 20240503 | 717 | 20240503 | 820 | 2444708 | 63 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 756 | 38.9143 | -121.2099 | No | Clear;32-90 F |  |  | 24-0061596 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1938541 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223045436629 | 20240503 | 951 | 20240503 | 1129 | 2444933 | 98 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 196 | 38.6687 | -120.9348 | No | Clear;32-90 F |  |  | 24-0061721 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1938685 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 3349 | 20240503 | 1252 | 20240503 | 1539 | 2445098 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1503 | 38.7751 | -120.4256 | No | Clear;32-90 F |  |  | 24-0061810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1938712 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222638557405 | 20240503 | 1656 | 20240503 | 2300 | 2445238 | 364 | Transformer only | 3rd Party | Dig in- 3rd party | 2 | 728 | 39.239 | -121.0695 | No | Clear;32-90 F | Secondary | Broken | 24-0061883 | OH | Sus | 31693040 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938735 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 18437 | 20240504 | 1621 | 20240505 | 13 | 2445961 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 12744 | 38.7597 | -120.5588 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0062170 | OH | Sus | 46238450 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1938949 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 2489 | 20240504 | 1648 | 20240505 | 438 | 2445978 | 710 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4970 | 38.7476 | -120.6104 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 24-0062216 | OH | Sus | 46238547 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1938993 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31097 | 20240504 | 1719 | 20240504 | 2308 | 2446032 | 349 | Distribution Circuit | 3rd Party | Vehicle | 10 | 3490 | 38.9332 | -120.753 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0062172 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1938951 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2218 | 20240504 | 1739 | 20240504 | 2334 | 2446046 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 27274 | 38.9803 | -121.4147 | No | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0062176 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1938955 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 5335 | 20240504 | 1810 | 20240504 | 2232 | 2446101 | 262 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 18000 | 38.9124 | -121.1982 | No | Overcast-Lightning;32-90 F |  |  | 24-0062266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939039 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 222593550450 | 20240504 | 1832 | 20240505 | 35 | 2446121 | 363 | Transformer only | Environmental/External | Lightning | 1 | 363 | 39.0478 | -121.0871 | No | Overcast-Fog-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939000 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5047 | 20240504 | 1836 | 20240505 | 16 | 2446117 | 340 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 9520 | 38.8257 | -121.158 | No | Overcast-Fog-Lightning;32-90 F |  |  | 24-0062276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1939049 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 37391 | 20240504 | 1849 | 20240504 | 2250 | 2446128 | 241 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 24594 | 38.8824 | -121.0765 | No | Overcast-Fog-Lightning;32-90 F |  |  | 24-0062270 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939043 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5895 | 20240504 | 1908 | 20240505 | 329 | 2446259 | 501 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1503 | 38.8982 | -120.956 | No | Overcast-Fog;32-90 F |  |  | 24-0062298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1939063 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222571250615 | 20240504 | 1916 | 20240505 | 446 | 2446153 | 570 | Distribution Circuit | Environmental/External | Lightning | 2 | 646 | 39.0528 | -121.0959 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939018 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222997545752 | 20240504 | 1923 | 20240505 | 1144 | 2446155 | 981 | Transformer only | Environmental/External | Lightning | 3 | 2943 | 38.9178 | -120.9479 | No | Partly Cloudy-Fog;32-90 F | Transformer | Failed/Faulted | 24-0062295 | OH | Sus | 35550824 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939061 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240504 | 2011 | 20240505 | 1112 | 2446177 | 901 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 18237 | 38.8694 | -121.0803 | No | Overcast-Drizzle-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062229 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939005 | 0 | EPSS Ckt | N | 2024 | A GRD
SIERRA | PLACER | LINCOLN-1102 | 153701102 | FUSE | 37513 | 20240505 | 150 | 20240505 | 2315 | 2446250 | 1285 | Distribution Circuit | Equipment Failure/Involved | Underground | 1271 | 56436 | 38.8879 | -121.3073 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 24-0062324 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939090 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222403242466 | 20240505 | 1123 | 20240505 | 1811 | 2446440 | 408 | Transformer only | Environmental/External | Lightning | 1 | 408 | 38.8297 | -121.1572 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 24-0062390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939149 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 7017 | 20240505 | 1502 | 20240505 | 1521 | 2446488 | 19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 95 | 39.1642 | -121.0627 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0062388 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1939147 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 8551 | 20240506 | 900 | 20240506 | 1053 | 2446834 | 113 | Distribution Circuit | Animal | Squirrel | 87 | 9831 | 38.7465 | -121.1707 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0062536 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1939343 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222998545739 | 20240506 | 1021 | 20240506 | 1525 | 2447053 | 304 | Transformer only | Environmental/External | Lightning | 1 | 304 | 38.9175 | -120.9476 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0062594 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939378 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7585 | 20240506 | 1301 | 20240506 | 1432 | 2447229 | 91 | Distribution Circuit | 3rd Party | Metallic Balloon | 17 | 1547 | 38.7722 | -121.4512 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0062712 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1939416 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20240506 | 1306 | 20240506 | 1901 | 2447240 | 355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 778 | 117683 | 38.7523 | -120.6821 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0062647 | OH | Sus | 31693368 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | Yes | No | 1939404 | 0 | EPSS Ckt | N | 2024 | A-C-GRD TIME OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222954045150 | 20240506 | 1347 | 20240506 | 1446 | 2447264 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 38.9012 | -120.9631 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0062714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939417 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7145 | 20240507 | 1043 | 20240507 | 1339 | 2447869 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 22176 | 39.2317 | -121.0746 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0062995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1939649 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 808 | 20240507 | 1228 | 20240507 | 1605 | 2447969 | 217 | Distribution Circuit | Company Initiated | Improper Construction | 5 | 1085 | 39.4883 | -120.857 | No | Clear;32-90 F | Insulator | Normal | 24-0062945 | OH | Sus | 46239328 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1939680 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | CATLETT-1102 | 153761102 | TRANSFORMER | 221556740358 | 20240507 | 1432 | 20240508 | 521 | 2448057 | 889 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 11053 | 38.7734 | -121.4551 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063246 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939738 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 37669 | 20240507 | 2051 | 20240508 | 1200 | 2448274 | 909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 909 | 38.897 | -121.3161 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0063362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939839 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1103 | 153651103 | TRANSFORMER | T4694 | 20240508 | 930 | 20240508 | 1130 | 2448890 | 120 | Transformer only | Company Initiated | Construction Activity/equip- company | 2 | 240 | 38.6568 | -120.9688 | No | Clear;32-90 F | Service conductor | Broken | 24-0063665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940058 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 38363 | 20240508 | 1013 | 20240508 | 1112 | 2448672 | 59 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 5900 | 38.7844 | -121.2546 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063580 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940039 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223422538219 | 20240508 | 1019 | 20240508 | 1340 | 2448675 | 201 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 201 | 38.7096 | -120.8019 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0063602 | OH | Sus | 31693484 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940046 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | OTHER | 1 OF 3 HOT WIRES DOWN WIRE SS OF LR 2306 | 20240508 | 1022 | 20240508 | 1423 | 2448724 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3288 | 282111 | 38.9264 | -121.2933 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063533 | OH | Sus | 31693485 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | Yes | 1940021 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222292942293 | 20240508 | 1044 | 20240508 | 1105 | 2448787 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 42 | 38.8249 | -121.1961 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0063604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940047 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 55666 | 20240508 | 1159 | 20240508 | 1427 | 2448863 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 14722 | 38.7296 | -121.0893 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063676 | OH | Sus | 46240069 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1940066 | 0 | EPSS Ckt | N | 2024 | C PHASE & GRD
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7553 | 20240508 | 1543 | 20240508 | 2007 | 2449097 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 792 | 38.7728 | -121.4233 | No | Clear-Strong Winds;32-90 F |  |  | 24-0063920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940145 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7263 | 20240508 | 1738 | 20240509 | 343 | 2449180 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 9328 | 39.2147 | -121.0803 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063903 | OH | Sus | 31693470 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1940138 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | TRANSFORMER | 221992744497 | 20240508 | 1813 | 20240508 | 1847 | 2449208 | 34 | Transformer only | Vegetation | Tree - grew into line | 4 | 136 | 38.8862 | -121.3009 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063916 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940142 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32915 | 20240508 | 2321 | 20240509 | 57 | 2449300 | 96 | Distribution Circuit | Animal | Bird found | 20 | 1920 | 38.8769 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063967 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940190 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5929 | 20240509 | 107 | 20240509 | 254 | 2449333 | 107 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 2996 | 39.0223 | -120.8097 | No | Clear;32-90 F |  |  | 24-0063972 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940194 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 34277 | 20240509 | 218 | 20240509 | 1453 | 2449340 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 1431 | 24965 | 38.9347 | -121.1038 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0063976 | OH | Sus | 46240132 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1940198 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 808 | 20240509 | 307 | 20240509 | 607 | 2449350 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 146976 | 39.4883 | -120.857 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Three Phase Fault | 0 | No | No | No | 1940196 | 0 | EPSS Ckt | N | 2024 | A+B+C+TIME OC
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1435 | 20240509 | 1145 | 20240509 | 1357 | 2449844 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2640 | 38.7507 | -120.7582 | No | Clear;32-90 F |  |  | 24-0064285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940429 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 2371 | 20240510 | 726 | 20240510 | 940 | 2450326 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2412 | 38.9384 | -121.3162 | No | Clear;32-90 F |  |  | 24-0064603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940667 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222580956818 | 20240510 | 730 | 20240510 | 1225 | 2450331 | 295 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 885 | 39.2232 | -121.0899 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064564 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940582 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | JUMPER | OJ'S SS OF CGC 225290341772 | 20240510 | 913 | 20240510 | 1715 | 2450446 | 482 | Distribution Circuit | Vegetation | Tree - grew into line | 56 | 26992 | 38.7988 | -120.1447 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0064586 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940614 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 221961346512 | 20240510 | 1107 | 20240510 | 1746 | 2450813 | 399 | Transformer only | Animal | Squirrel | 5 | 1995 | 38.9418 | -121.3116 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0064764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940738 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 37043 | 20240510 | 1355 | 20240510 | 1508 | 2450959 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 365 | 38.8492 | -121.0809 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0064758 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940737 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 3451 | 20240510 | 1729 | 20240510 | 2000 | 2451130 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1057 | 39.211 | -120.8206 | No | Clear;32-90 F |  |  | 24-0064879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940786 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222276042247 | 20240510 | 2132 | 20240510 | 2253 | 2451218 | 81 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 648 | 38.8239 | -121.2022 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0064908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940821 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 2375 | 20240511 | 925 | 20240511 | 1025 | 2451386 | 60 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 120 | 38.9667 | -121.2932 | No | Clear;32-90 F |  |  | 24-0064966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940886 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20240511 | 1059 | 20240511 | 1725 | 2451445 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 604 | 221899 | 39.5596 | -120.8241 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0064958 | OH | Sus | 2033539 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1940891 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 225405042140 | 20240511 | 1131 | 20240511 | 1309 | 2451458 | 98 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 392 | 38.8079 | -120.1043 | No | Clear;32-90 F | Secondary | Together | 24-0065014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940907 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 6842 | 20240511 | 1417 | 20240511 | 1854 | 2451577 | 277 | Distribution Circuit | Equipment Failure/Involved | Underground | 2787 | 735441 | 38.6419 | -121.0734 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0065054 | UG | Sus | 46246063 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1940924 | 0 | EPSS Ckt | N | 2024 | A B GRD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9523 | 20240511 | 1946 | 20240511 | 2205 | 2451713 | 139 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 278 | 38.8788 | -121.4144 | No | Clear;32-90 F |  |  | 24-0065091 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940960 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 1873 | 20240511 | 2354 | 20240512 | 1923 | 2451796 | 1169 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 488 | 58181 | 38.7234 | -121.2091 | No | Clear;32-90 F |  |  | 24-0065128 | OH | Sus | 46246182 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940996 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 39023 | 20240512 | 702 | 20240512 | 915 | 2451949 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 266 | 38.8258 | -121.1823 | No | Clear;32-90 F |  |  | 24-0065147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941016 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222960757332 | 20240512 | 926 | 20240512 | 1658 | 2451999 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 1880 | 39.2367 | -120.9559 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0065168 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941032 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222577951032 | 20240512 | 1716 | 20240512 | 2348 | 2452120 | 392 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 784 | 39.0643 | -121.0905 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0065205 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941056 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223258633946 | 20240512 | 1831 | 20240512 | 2117 | 2452119 | 166 | Transformer only | Vegetation | Tree - fell into line | 1 | 166 | 38.5936 | -120.861 | No | Clear;32-90 F | Service conductor | Broken | 24-0065204 | OH | Sus | 31693944 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941055 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY SUB | 15203 | OCB | 82 | 20240512 | 1851 | 20240513 | 341 | 2452160 | 530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1478 | 110351 | 39.2093 | -121.0616 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0065207 | OH | Sus | 31693931 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941058 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 3339 | 20240512 | 1851 | 20240512 | 2112 | 2452215 | 141 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 141 | 39.2087 | -121.0763 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0065215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941066 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 31361 | 20240512 | 1851 | 20240512 | 2215 | 2452207 | 204 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3402 | 39.2025 | -121.0781 | No | Clear;32-90 F |  |  | 24-0065238 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941092 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 4729 | 20240513 | 210 | 20240513 | 451 | 2452276 | 161 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 6279 | 39.0824 | -121.1414 | No | Clear;32-90 F |  |  | 24-0065250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941104 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221788947881 | 20240513 | 829 | 20240513 | 1246 | 2452355 | 257 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2570 | 38.9795 | -121.3715 | No | Clear;32-90 F | Service conductor | Broken | 24-0065310 | OH | Sus | 46246246 | NORTH VALLEY AND SIERRA | MAY | Open Circuit | 0 | No | No | No | 1941182 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 30485 | 20240513 | 839 | 20240513 | 1008 | 2452427 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2403 | 39.0391 | -120.9399 | No | Clear;32-90 F |  |  | 24-0065350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941261 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12617 | 20240513 | 1009 | 20240513 | 1239 | 2452561 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 2700 | 38.8068 | -120.7467 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0065352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941262 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJ AT CGC 223082045872 | 20240513 | 1434 | 20240513 | 1611 | 2452714 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 776 | 38.9225 | -120.9175 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0065415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941313 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | T8024 | 20240513 | 1844 | 20240513 | 1851 | 2453040 | 7 | Transformer only | 3rd Party | Other | 103 | 721 | 38.6967 | -121.0003 | No | Clear;32-90 F | Other | Normal | 24-0065601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1941393 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | SWITCH | 1330 | 20240513 | 2206 | 20240513 | 2225 | 2453135 | 19 | Distribution Circuit | Company Initiated | Return Circuit Normal | 114 | 2070 | 38.7214 | -121.2092 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0065128 | UG | Sus | 46246182 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941414 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 3951 | 20240514 | 950 | 20240514 | 1620 | 2453424 | 390 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 390 | 39.2067 | -121.0684 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0065753 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941589 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223553033180 | 20240514 | 2136 | 20240515 | 530 | 2453945 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3654 | 38.5706 | -120.7579 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0066071 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941709 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 4813 | 20240514 | 2241 | 20240514 | 2356 | 2453968 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 3600 | 39.0366 | -121.0763 | No | Clear;32-90 F |  |  | 24-0066072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941711 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 2232 | 20240515 | 427 | 20240515 | 644 | 2454005 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 355 | 32627 | 39.1444 | -120.908 | No | Clear;32-90 F |  |  | 24-0066075 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1941719 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9717 | 20240515 | 714 | 20240515 | 857 | 2454037 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1133 | 39.1977 | -121.0522 | No | Clear;32-90 F |  |  | 24-0066197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941837 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ TWD 9895 | 20240515 | 833 | 20240515 | 1320 | 2454130 | 287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 55678 | 39.1124 | -121.0836 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0066156 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941783 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | TRANSFORMER | 222568943635 | 20240515 | 1556 | 20240515 | 2020 | 2454682 | 264 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 264 | 38.8614 | -121.0986 | No | Clear;32-90 F |  |  | 24-0066581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1941989 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22059 | 20240516 | 859 | 20240516 | 1352 | 2460542 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 293 | 38.7531 | -120.6861 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0066726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942059 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31025 | 20240516 | 1229 | 20240516 | 1356 | 2460684 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 870 | 38.9005 | -120.9155 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942088 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222644456240 | 20240516 | 1253 | 20240516 | 1730 | 2460722 | 277 | Transformer only | 3rd Party | Vehicle | 1 | 277 | 39.2071 | -121.0679 | No | Clear;32-90 F | Secondary | Broken | 24-0066978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942153 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | OTHER | 804 | 20240516 | 1357 | 20240516 | 1433 | 2460754 | 36 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 21708 | 39.5596 | -120.8241 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0066883 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Open Circuit | 0 | No | Yes | No | 1942108 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | JUMPER | OJ SS OF 32489 | 20240516 | 1357 | 20240517 | 215 | 2460789 | 738 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 738 | 39.5679 | -120.6662 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0066907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1942123 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | FUSE | 8539 | 20240517 | 802 | 20240517 | 1836 | 2461317 | 634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 30624 | 38.7785 | -121.2432 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0067138 | OH | Sus | 31694298 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942322 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | AUBURN-1102 | 152161102 | RECLOSER | 1102/2 | 20240517 | 808 | 20240517 | 1252 | 2461340 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1386 | 91704 | 38.9036 | -121.0699 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0067122 | OH | Sus | 31694296 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942288 | 0 | EPSS Ckt | N | 2024 | GRD & SGF
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ 2 W/OF CGC 223548036305 | 20240517 | 826 | 20240517 | 1318 | 2461373 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 584 | 38.6569 | -120.7605 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0067124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942291 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222285542166 | 20240517 | 1018 | 20240517 | 2145 | 2461577 | 687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 13279 | 38.8215 | -121.1987 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0067359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942439 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7969 | 20240517 | 1707 | 20240518 | 1636 | 2461846 | 1409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 9863 | 39.6879 | -120.6455 | No | Clear;32-90 F | Insulator | Broken | 24-0067421 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942466 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | OTHER | WIRE DOWN @ 9230 CYPRESS ST | 20240517 | 2326 | 20240518 | 955 | 2461992 | 629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 137 | 9547 | 38.8741 | -121.1333 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0067444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | Yes | 1942490 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20819 | 20240518 | 745 | 20240518 | 1002 | 2462062 | 137 | Distribution Circuit | Animal | Bird found | 18 | 2466 | 38.6174 | -120.7157 | No | Clear;32-90 F | Bushing | Normal | 24-0067484 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942556 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 35239 | 20240518 | 747 | 20240518 | 906 | 2462063 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 130 | 10270 | 38.8866 | -121.3009 | No | Clear;32-90 F |  |  | 24-0067471 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942536 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222964655540 | 20240518 | 2144 | 20240519 | 1500 | 2462421 | 1036 | Transformer only | Animal | Squirrel | 1 | 1036 | 39.187 | -120.9551 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0067586 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942613 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1249 | 20240519 | 1040 | 20240519 | 1513 | 2462553 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5026 | 38.8114 | -120.8047 | No | Clear;32-90 F |  |  | 24-0067629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942664 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 22877 | 20240519 | 1450 | 20240519 | 1456 | 2462654 | 6 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 6 | 38.6893 | -120.7648 | No | Clear;32-90 F | Metering Equipment | Burned/flashed | 24-0067642 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942677 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 10955 | 20240520 | 935 | 20240520 | 1318 | 2463035 | 223 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 223 | 38.6649 | -120.931 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0067779 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942815 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15349 | 20240520 | 1140 | 20240520 | 1459 | 2463272 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 398 | 38.9263 | -121.3865 | No | Clear;32-90 F |  |  | 24-0067998 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942946 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 31061 | 20240520 | 1142 | 20240520 | 1640 | 2463275 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1192 | 39.0329 | -120.9745 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0067889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942909 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223033956461 | 20240520 | 1238 | 20240520 | 1319 | 2463317 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 39.2101 | -120.9291 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0067920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942925 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15343 | 20240520 | 1411 | 20240520 | 1451 | 2463417 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 40 | 38.9264 | -121.3912 | No | Clear;32-90 F |  |  | 24-0067993 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942944 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 36443 | 20240520 | 1759 | 20240520 | 1851 | 2463622 | 52 | Distribution Circuit | Animal | Bird found | 9 | 468 | 38.7394 | -121.1886 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0068077 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942977 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 89455 | 20240520 | 2043 | 20240520 | 2333 | 2463680 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3400 | 38.8195 | -121.1398 | No | Clear;32-90 F |  |  | 24-0068093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942990 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 8541 | 20240521 | 352 | 20240521 | 451 | 2463898 | 49 | Distribution Circuit | Animal | Squirrel | 76 | 3724 | 39.2081 | -121.0656 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0068124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943022 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222660357075 | 20240521 | 944 | 20240521 | 1154 | 2464218 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 780 | 39.23 | -121.0618 | No | Clear;32-90 F | Service conductor | Broken | 24-0068327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1943213 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15343 | 20240521 | 1116 | 20240521 | 1123 | 2464287 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 7 | 38.9264 | -121.3912 | No | Clear;32-90 F |  |  | 24-0068290 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943200 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | RECLOSER | 63100 | 20240521 | 1119 | 20240521 | 1622 | 2464297 | 303 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 190 | 37334 | 39.2282 | -121.1005 | No | Clear;32-90 F | Insulator | Broken | 24-0068298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1943204 | 0 | EPSS Ckt | N | 2024 | A-B
SIERRA | PLACER | DEL MAR-2105 | 152582105 | RECLOSER | 1050 | 20240521 | 1432 | 20240521 | 1541 | 2464455 | 69 | Distribution Circuit | Company Initiated | Coordination failure | 26 | 1794 | 38.7916 | -121.2372 | No | Clear;32-90 F | Recloser | Normal | 24-0068451 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1943250 | 0 | EPSS Ckt | N | 2024 | A-B-C- & GRD
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 5117 | 20240521 | 1434 | 20240521 | 1525 | 2464453 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 1444 | 38.8054 | -121.2425 | No | Clear;32-90 F |  |  | 24-0068469 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943252 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18249 | 20240522 | 3 | 20240522 | 149 | 2464735 | 106 | Distribution Circuit | Animal | Squirrel | 6 | 636 | 38.7041 | -120.8499 | No | Clear;32-90 F | Fuse | Normal | 24-0068559 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943307 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15345 | 20240522 | 216 | 20240522 | 320 | 2464739 | 64 | Distribution Circuit | Animal | Bird found | 4 | 256 | 38.9262 | -121.3953 | No | Clear;32-90 F | Lightning Arrestor | Normal | 24-0068562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943310 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | JUMPER | OJS 1 SPANS SS OF CGC 223271235397 | 20240522 | 827 | 20240522 | 1113 | 2464840 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 332 | 38.634 | -120.8554 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0068618 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1943360 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223313055681 | 20240522 | 923 | 20240522 | 1307 | 2464976 | 224 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1120 | 39.1896 | -120.8316 | No | Clear;32-90 F |  |  | 24-0061791 | OH | Sus | 35468820 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1943460 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 6771 | 20240522 | 1728 | 20240523 | 311 | 2465353 | 583 | Distribution Circuit | 3rd Party | Vehicle | 35 | 20405 | 39.2623 | -120.9043 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0068958 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1943558 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221643543501 | 20240522 | 1832 | 20240523 | 243 | 2465260 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 491 | 38.8595 | -121.4237 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0068971 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943563 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 19111 | 20240523 | 423 | 20240523 | 1915 | 2465530 | 613 | Distribution Circuit | Equipment Failure/Involved | Underground | 140 | 49559 | 38.7195 | -121.0865 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0069088 | UG | Sus | 46250610 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943667 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 7963 | 20240523 | 1015 | 20240523 | 1249 | 2465883 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 616 | 39.6347 | -120.6244 | No | Clear;32-90 F |  |  | 24-0069210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943805 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | SWITCH | 1260 | 20240523 | 1016 | 20240523 | 1125 | 2465881 | 69 | Distribution Circuit | Company Initiated | Personnel- company | 2280 | 157320 | 38.8051 | -121.2729 | No | Clear;32-90 F | Other | Malfunctioning | 24-0069209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1943804 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8639 | 20240523 | 1448 | 20240523 | 1945 | 2466079 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3267 | 39.145 | -120.9763 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0069334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1943844 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9771 | 20240523 | 1616 | 20240524 | 414 | 2466117 | 718 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 6046 | 39.2022 | -121.0212 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0069420 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1943862 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4145 | 20240523 | 1633 | 20240523 | 1827 | 2466126 | 114 | Distribution Circuit | Animal | Bird found | 30 | 3420 | 39.1978 | -121.1778 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0069430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943868 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 4609 | 20240523 | 1645 | 20240524 | 157 | 2466107 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 79488 | 39.2842 | -121.0669 | No | Clear;32-90 F | Insulator | Broken | 24-0069409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1943858 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30223 | 20240524 | 620 | 20240524 | 731 | 2466327 | 71 | Distribution Circuit | Animal | Squirrel | 23 | 835 | 39.2105 | -120.9854 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0069523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1943932 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4145 | 20240524 | 911 | 20240524 | 1323 | 2466498 | 252 | Distribution Circuit | Animal | Bird found | 30 | 7560 | 39.1978 | -121.1778 | No | Clear;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0069623 | OH | Sus | 31694987 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944028 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222560852770 | 20240524 | 954 | 20240524 | 1440 | 2466544 | 286 | Transformer only | Vegetation | Tree - fell into line | 1 | 286 | 39.1118 | -121.0953 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944045 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | JUMPER | 2 OF 3 OJS @ SAP ID 100059227 | 20240524 | 1226 | 20240524 | 1940 | 2466659 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 533 | 38.7882 | -121.4167 | No | Clear;32-90 F | Jumper | Burned Open | 24-0069881 | OH | Sus | 46251507 | NORTH VALLEY AND SIERRA | MAY | Open Circuit | 0 | No | No | No | 1944096 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222662556824 | 20240524 | 1251 | 20240524 | 1438 | 2466656 | 107 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 428 | 39.2258 | -121.0611 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0069816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944071 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 20240524 | 1325 | 20240524 | 2115 | 2466695 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 17570 | 39.0896 | -120.9657 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0069863 | OH | Sus | 31695146 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1944092 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20240524 | 1826 | 20240525 | 100 | 2466909 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 778 | 238948 | 38.7523 | -120.6821 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0069903 | OH | Sus | 46251615 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | Yes | No | 1944108 | 0 | EPSS Ckt | N | 2024 | ABC & GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2308 | 20240525 | 309 | 20240525 | 542 | 2467220 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 898 | 137394 | 38.9265 | -121.2905 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0069944 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944154 | 0 | EPSS Ckt | N | 2024 | A & B
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222770658241 | 20240525 | 1729 | 20240526 | 52 | 2467599 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 443 | 39.2619 | -121.0226 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070035 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944234 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 7017 | 20240526 | 1012 | 20240526 | 1028 | 2467776 | 16 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 80 | 39.1642 | -121.0627 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1944283 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 693294 | 20240526 | 2052 | 20240527 | 20 | 2468024 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 275 | 57200 | 38.912 | -121.2487 | No | Clear;32-90 F |  |  | 24-0070142 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944319 | 0 | EPSS Ckt | Y | 2024 | B C INSTAN
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21347 | 20240526 | 2154 | 20240527 | 838 | 2468030 | 644 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 8372 | 38.5785 | -120.7537 | No | Clear;32-90 F |  |  | 24-0070162 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944338 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240527 | 1311 | 20240527 | 1559 | 2468264 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 30744 | 38.8694 | -121.0803 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0070216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944382 | 0 | EPSS Ckt | Y | 2024 | DCD SGF
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223370539112 | 20240527 | 1648 | 20240528 | 40 | 2468344 | 472 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 1416 | 38.7345 | -120.819 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0070248 | OH | Sus | 31695322 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944410 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38845 | 20240528 | 436 | 20240528 | 1203 | 2468464 | 447 | Distribution Circuit | 3rd Party | Vehicle | 41 | 7167 | 38.8109 | -121.1335 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944462 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240528 | 1304 | 20240528 | 1423 | 2468986 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 14457 | 38.8694 | -121.0803 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0070550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944654 | 0 | EPSS Ckt | Y | 2024 | SGF+DCD
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | TRANSFORMER | T0063 | 20240528 | 1412 | 20240528 | 1529 | 2469099 | 77 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 1309 | 38.6981 | -121.0814 | No | Clear;32-90 F |  |  | 24-0070667 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1944689 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | FUSE | 5215 | 20240528 | 1800 | 20240529 | 402 | 2469302 | 602 | Distribution Circuit | Animal | Bird found | 55 | 18595 | 38.8845 | -121.1052 | No | Clear;32-90 F | Jumper | Normal | 24-0070717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1944711 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 9073 | 20240529 | 855 | 20240529 | 1420 | 2469597 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 28275 | 39.241 | -121.1126 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0070832 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1944841 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20240529 | 1131 | 20240530 | 144 | 2469809 | 853 | Distribution Circuit | 3rd Party | Vehicle | 842 | 289351 | 38.6858 | -121.0119 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0070912 | OH | Sus | 31695333 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1944937 | 0 | EPSS Ckt | N | 2024 | B+GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223031055584 | 20240529 | 1518 | 20240529 | 1636 | 2470077 | 78 | Transformer only | Animal | Bird found | 1 | 78 | 39.188 | -120.9315 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0071095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945003 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222672753383 | 20240529 | 1603 | 20240529 | 1703 | 2470108 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 420 | 39.1286 | -121.059 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0071055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1944991 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221630245950 | 20240529 | 2304 | 20240530 | 157 | 2470482 | 173 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 346 | 38.9268 | -121.4284 | No | Clear;32-90 F | Secondary | Broken | 24-0071172 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1945068 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223268165885 | 20240530 | 1034 | 20240530 | 1140 | 2470812 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 330 | 39.47 | -120.8434 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945297 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 56468 | 20240530 | 1039 | 20240530 | 1140 | 2470829 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 1610 | 98210 | 39.2411 | -121.0378 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945256 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223267065870 | 20240530 | 1140 | 20240530 | 1805 | 2470914 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1540 | 39.4696 | -120.8435 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1945281 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 868864 | 20240530 | 1322 | 20240530 | 1344 | 2470988 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 41 | 902 | 38.7457 | -120.6289 | No | Clear;32-90 F | Fuse | Normal | 24-0071465 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1945304 | 0 | EPSS Ckt | Y | 2024 | TRIP TARGET A-B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 20240531 | 1306 | 20240531 | 1419 | 2471863 | 73 | Distribution Circuit | Animal | Bird found | 3692 | 269516 | 38.9144 | -121.0197 | No | Clear;32-90 F | Recloser | Normal | 24-0071940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1945600 | 0 | EPSS Ckt | Y | 2024 | A-C- GRD
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | FUSE | 1765 | 20240531 | 1443 | 20240531 | 1747 | 2471971 | 122 | Distribution Circuit | Equipment Failure/Involved | Underground | 185 | 19690 | 38.7998 | -121.2622 | No | Clear;Above 90 | Connector or Splice (UG) | Broken | 24-0072054 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945637 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39055 | 20240601 | 6 | 20240601 | 325 | 2472308 | 199 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 995 | 39.0419 | -121.0691 | No | Clear;32-90 F |  |  | 24-0072121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1945690 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240601 | 1200 | 20240601 | 1222 | 2472500 | 22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2114 | 46508 | 39.2042 | -121.2005 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0072180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | Yes | No | No | 1945755 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223768038410 | 20240601 | 1338 | 20240601 | 1916 | 2472567 | 338 | Transformer only | 3rd Party | Customer Equipment | 2 | 676 | 38.715 | -120.6805 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0072210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1945772 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2218 | 20240601 | 1503 | 20240601 | 2257 | 2472611 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 26143 | 38.9803 | -121.4147 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0072206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1945769 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221669445552 | 20240602 | 901 | 20240602 | 1109 | 2473120 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 128 | 38.9159 | -121.4147 | No | Clear;32-90 F |  |  | 24-0072318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1945886 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20240603 | 757 | 20240603 | 819 | 2473723 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 1003 | 22066 | 38.6779 | -120.8495 | No | Partly Cloudy;32-90 F | Fuse | Normal | 24-0072446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946008 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 37183 | 20240603 | 1737 | 20240604 | 58 | 2474434 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1323 | 38.8613 | -121.1223 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0072755 | OH | Sus | 31696204 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946218 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8497 | 20240604 | 1031 | 20240604 | 1308 | 2474972 | 157 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 44 | 6908 | 38.8782 | -120.998 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0068921 | OH | Sus | 35293506 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | Yes | Yes | 1946446 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222363357020 | 20240604 | 1414 | 20240604 | 2137 | 2475293 | 443 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 443 | 39.2296 | -121.1663 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073256 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946536 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 4901 | 20240604 | 1530 | 20240604 | 1605 | 2475274 | 35 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 665 | 38.7608 | -121.1916 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0073216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1946521 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | OCB | 1102/2 | 20240604 | 1550 | 20240604 | 1946 | 2475303 | 236 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 113180 | 39.0363 | -120.9882 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0073219 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1946522 | 0 | EPSS Ckt | Y | 2024 | A+C
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20240604 | 1600 | 20240604 | 1712 | 2475328 | 72 | Distribution Circuit | Vegetation | Tree - branch fell on line | 220 | 15840 | 38.8964 | -121.1202 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0073225 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1946525 | 0 | EPSS Ckt | Y | 2024 | A+C
SIERRA | PLACER | LINCOLN-1101 | 153701101 | INTERRUPTER | 317246 | 20240604 | 1604 | 20240604 | 1653 | 2475334 | 49 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 147 | 38.8687 | -121.2217 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0073211 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1946529 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | 222827737821 | 20240604 | 1735 | 20240605 | 138 | 2475397 | 483 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2415 | 38.7004 | -121.0098 | No | Clear;Above 90 | Fuse | Burned Open | 24-0073292 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946564 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5169 | 20240605 | 22 | 20240605 | 229 | 2475717 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1143 | 39.0232 | -121.0928 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0073360 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1946631 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | RECLOSER | 429574 | 20240605 | 520 | 20240605 | 1256 | 2475768 | 456 | Distribution Circuit | Equipment Failure/Involved | Overhead | 521 | 51957 | 38.928 | -121.0688 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073368 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1946642 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | TRANSFORMER | T115796 | 20240605 | 703 | 20240605 | 1100 | 2475786 | 237 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 237 | 38.6925 | -121.0483 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0073396 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946648 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20240605 | 1656 | 20240605 | 2123 | 2476511 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 533 | 111882 | 39.214 | -120.8098 | No | Clear;32-90 F |  |  | 24-0073768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946907 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223653940155 | 20240605 | 1844 | 20240606 | 1120 | 2477286 | 996 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2988 | 38.7622 | -120.7193 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947042 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32155 | 20240605 | 1906 | 20240606 | 1639 | 2476795 | 1293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 13293 | 38.7891 | -121.257 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0073847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946969 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222829943617 | 20240605 | 1909 | 20240606 | 320 | 2477064 | 491 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 491 | 38.86 | -121.0068 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947016 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20240605 | 1909 | 20240606 | 1137 | 2476820 | 988 | Distribution Circuit | Equipment Failure/Involved | Overhead | 721 | 278908 | 38.6615 | -120.9109 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0073812 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946937 | 0 | EPSS Ckt | Y | 2024 | B
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 5285 | 20240605 | 2035 | 20240605 | 2153 | 2477014 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1482 | 38.8082 | -121.0752 | No | Clear;32-90 F | Insulator | Broken | 24-0073842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1946964 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 32813 | 20240606 | 852 | 20240606 | 1130 | 2477559 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 474 | 39.1189 | -121.0837 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0074015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947135 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20240606 | 951 | 20240606 | 1317 | 2477687 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1560 | 301392 | 38.8328 | -120.8176 | No | Clear;32-90 F |  |  | 24-0074053 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947190 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222621254211 | 20240606 | 1026 | 20240607 | 45 | 2477872 | 859 | Transformer only | Vegetation | Tree - fell into line | 1 | 859 | 39.1515 | -121.0771 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074283 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947275 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | FUSE | 9671 | 20240606 | 1243 | 20240606 | 1439 | 2477326 | 116 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 116 | 38.8111 | -121.3121 | No | Clear;32-90 F | Secondary | Bent or Twisted | 24-0074164 | UG | Sus | 31696275 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947242 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | OTHER | WIRE DOWN AT CGC 222378152594 | 20240606 | 1259 | 20240606 | 1914 | 2477987 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 17688 | 39.1063 | -121.1628 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0074227 | OH | Sus | 46256510 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | Yes | 1947258 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222587549639 | 20240606 | 1803 | 20240607 | 252 | 2478388 | 529 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 529 | 39.0258 | -121.0904 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0074388 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947318 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2109 | 152582109 | RECLOSER | 75802 | 20240606 | 1946 | 20240607 | 1139 | 2478597 | 953 | Distribution Circuit | Equipment Failure/Involved | Underground | 2832 | 149751 | 38.8488 | -121.2315 | No | Clear;Above 90 | Elbow | Burned/flashed | 24-0074400 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947326 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 32933 | 20240606 | 2121 | 20240606 | 2304 | 2478653 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2472 | 39.2264 | -121.224 | No | Clear;32-90 F |  |  | 24-0074462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947377 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32155 | 20240607 | 140 | 20240607 | 442 | 2478774 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 8918 | 38.7891 | -121.257 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0074476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947386 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223468539160 | 20240607 | 310 | 20240607 | 950 | 2478786 | 400 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2000 | 38.7353 | -120.7853 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074487 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947397 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30337 | 20240607 | 400 | 20240607 | 638 | 2478833 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 948 | 39.095 | -121.054 | No | Clear;32-90 F |  |  | 24-0074498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947406 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 38395 | 20240607 | 849 | 20240607 | 928 | 2478990 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 546 | 38.8279 | -121.2012 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0074562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947465 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20240607 | 1056 | 20240607 | 1524 | 2479186 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 244727 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0074644 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947538 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | OCB | 2105/2 | 20240607 | 1212 | 20240607 | 1224 | 2479240 | 12 | Distribution Circuit | Vegetation | Tree - fell into line | 4022 | 48264 | 38.6597 | -120.9472 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0074695 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947552 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222703657736 | 20240607 | 1531 | 20240607 | 2145 | 2479527 | 374 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 374 | 39.248 | -121.0463 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947595 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20240608 | 348 | 20240608 | 1613 | 2479863 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 75064 | 38.9945 | -121.026 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0074915 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947668 | 0 | EPSS Ckt | Y | 2024 | A-C INST OC
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38011 | 20240608 | 1035 | 20240608 | 1205 | 2480043 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 90 | 38.8253 | -121.1611 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0074949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947718 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | OCB | 1101/2 | 20240608 | 1036 | 20240608 | 1234 | 2480045 | 118 | Distribution Circuit | Animal | Squirrel | 2080 | 187853 | 38.8853 | -121.0674 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 24-0074950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947719 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | PLACER | PENRYN-1106 | 152561106 | FUSE | 38401 | 20240609 | 806 | 20240609 | 1043 | 2480479 | 157 | Distribution Circuit | Animal | Squirrel | 4 | 628 | 38.8327 | -121.2011 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0075095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947852 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 21531 | 20240609 | 1046 | 20240609 | 1425 | 2480544 | 219 | Distribution Circuit | Animal | Bird found | 24 | 2682 | 38.6809 | -120.8237 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0075108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947858 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240609 | 1102 | 20240610 | 130 | 2480558 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 2114 | 133232 | 39.2042 | -121.2005 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0075098 | OH | Sus | 46257705 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1947855 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240609 | 1630 | 20240609 | 1853 | 2480640 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 189 | 27027 | 38.8694 | -121.0803 | No | Clear;32-90 F |  |  | 24-0075126 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947870 | 0 | EPSS Ckt | Y | 2024 | A IOC
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 20240609 | 2245 | 20240610 | 327 | 2480703 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1410 | 39.3404 | -121.1319 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0075175 | OH | Sus | 31696721 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947919 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | RECLOSER | 51738 | 20240610 | 403 | 20240610 | 1344 | 2480771 | 581 | Distribution Circuit | Equipment Failure/Involved | Underground | 2209 | 527043 | 38.6795 | -120.9797 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0075186 | UG | Sus | 46257818 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947930 | 0 | EPSS Ckt | Y | 2024 | A- GRD
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 8327 | 20240610 | 1038 | 20240610 | 2119 | 2481224 | 641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 14102 | 38.8974 | -121.3606 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0075286 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1948086 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7595 | 20240610 | 1144 | 20240610 | 1354 | 2481385 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 260 | 38.8243 | -121.45 | No | Clear;32-90 F |  |  | 24-0075374 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1948129 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222907049425 | 20240611 | 1612 | 20240611 | 1700 | 2482570 | 48 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 240 | 39.0186 | -120.9785 | No | Clear;Above 90 |  |  | 24-0075976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1948514 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 80680 | 20240611 | 2118 | 20240611 | 2309 | 2482827 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 16206 | 38.9639 | -121.105 | No | Clear;32-90 F |  |  | 24-0076008 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1948545 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | FUSE | ECHO SUMMIT | 20240611 | 2222 | 20240612 | 137 | 2482893 | 74 | Distribution Circuit | 3rd Party | Other | 308 | 23408 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0076033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1948567 | 1 | Non-EPSS | Y | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | FLYING BELLS 1 SPAN SS OF CGC 223617035009 | 20240611 | 2247 | 20240612 | 107 | 2482906 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 420 | 38.6212 | -120.7345 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0076032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1948566 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | SWITCH | 50007 | 20240611 | 2326 | 20240612 | 244 | 2482930 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 11880 | 39.2596 | -121.0169 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0075968 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1948572 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240612 | 1036 | 20240612 | 1528 | 2483534 | 292 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 29600 | 38.8694 | -121.0803 | No | Clear;32-90 F |  |  | 24-0076202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1948751 | 0 | EPSS Ckt | N | 2024 | DCD & SGF
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 817491 | 20240612 | 1123 | 20240612 | 1258 | 2483586 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2945 | 38.854 | -121.2101 | No | Clear;Above 90 |  |  | 24-0076229 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1948764 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 878418 | 20240612 | 1310 | 20240612 | 1345 | 2483713 | 35 | Distribution Circuit | Company Initiated | Personnel- company | 82 | 2870 | 38.6606 | -120.9901 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0076302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1948791 | 0 | EPSS Ckt | Y | 2024 | AC
SIERRA | PLACER | LINCOLN 2109 | 153702109 | FUSE | 609011 | 20240612 | 1556 | 20240612 | 1606 | 2483786 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 7 | 38.8948 | -121.271 | No | Clear;Above 90 |  |  | 24-0076400 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1948814 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | RECLOSER | 75884 | 20240612 | 1837 | 20240612 | 2343 | 2483962 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1089 | 76740 | 38.6555 | -121.0509 | No | Clear;Above 90 | Pothead(Riser Termination) | Failed/Faulted | 24-0076437 | OH | Sus | 46262961 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1948830 | 0 | EPSS Ckt | Y | 2024 | A C GRD
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | SWITCH | 51610 | 20240613 | 338 | 20240613 | 419 | 2484148 | 41 | Distribution Circuit | Company Initiated | Return Circuit Normal | 100 | 4100 | 38.6607 | -121.0046 | No | Clear;32-90 F | Switch (UG) | Normal | 24-0076437 | UG | Sus | 46262961 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1948894 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240613 | 1251 | 20240613 | 1538 | 2484673 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 192 | 32064 | 38.8694 | -121.0803 | No | Clear;32-90 F |  |  | 24-0076744 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949116 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 33327 | 20240613 | 1413 | 20240614 | 229 | 2484771 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1472 | 38.9122 | -121.0846 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0076848 | OH | Sus | 31697084 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1949137 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 222976753100 | 20240613 | 1525 | 20240614 | 235 | 2484862 | 670 | Transformer only | 3rd Party | Customer Equipment | 2 | 1340 | 39.1193 | -120.9516 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076893 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949147 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 20240613 | 2251 | 20240614 | 253 | 2485059 | 242 | Distribution Circuit | 3rd Party | Vehicle | 3941 | 698622 | 38.7934 | -120.62 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0076946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1949193 | 0 | EPSS Ckt | Y | 2024 | AC- INST OC- SET A RLY
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | JUMPER | OJ'S @ 223640939133 | 20240614 | 904 | 20240614 | 1141 | 2485330 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1099 | 38.7339 | -120.724 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0077015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1949302 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ'S @ LINE AND BUCK OFF HARD TAP | 20240614 | 1222 | 20240614 | 1330 | 2485529 | 68 | Distribution Circuit | 3rd Party | Vehicle | 3 | 204 | 38.6969 | -120.7617 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | Yes | No | 1949394 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | SWITCH | 700379 | 20240614 | 1247 | 20240614 | 1353 | 2485650 | 66 | Distribution Circuit | Equipment Failure/Involved | Underground | 4 | 264 | 38.8523 | -121.0881 | No | Clear;32-90 F | Elbow | Normal | 24-0077140 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1949397 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20240615 | 330 | 20240615 | 817 | 2486218 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 596 | 171052 | 39.0443 | -120.9859 | No | Clear;32-90 F |  |  | 24-0077322 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1949490 | 0 | EPSS Ckt | Y | 2024 | A& C PH INST
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 941844 | 20240615 | 650 | 20240615 | 831 | 2486266 | 101 | Distribution Circuit | Animal | Bird found | 598 | 42578 | 39.0933 | -120.9512 | No | Clear;32-90 F | Fuse | Normal | 24-0077334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949498 | 0 | EPSS Ckt | Y | 2024 | A & GRD
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | OCB | 2110/2 | 20240615 | 2350 | 20240616 | 2006 | 2486826 | 1216 | Distribution Circuit | Equipment Failure/Involved | Underground | 4413 | 1427887 | 38.6555 | -121.0602 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0077441 | UG | Sus | 35561023 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949601 | 0 | EPSS Ckt | N | 2024 | SET A C PHA OC
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 8323 | 20240616 | 728 | 20240616 | 1356 | 2486880 | 388 | Distribution Circuit | Animal | Bird found | 22 | 8536 | 38.897 | -121.4004 | No | Clear;32-90 F | Bushing | Normal | 24-0077491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1949646 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20240616 | 743 | 20240616 | 1237 | 2486890 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 60010 | 39.2562 | -120.7669 | No | Clear;Above 90 |  |  | 24-0077457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1949617 | 0 | EPSS Ckt | Y | 2024 | A-B GRD
SIERRA | PLACER | WISE-1102 | 152271102 | TRANSFORMER | 222509544948 | 20240616 | 1033 | 20240616 | 1338 | 2486935 | 185 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 370 | 38.8974 | -121.1192 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0077466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949625 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221744548790 | 20240617 | 1241 | 20240617 | 1745 | 2487819 | 304 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 304 | 39.0048 | -121.3871 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0077738 | OH | Sus | 31697585 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1949907 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | RECLOSER | 748992 | 20240617 | 1444 | 20240618 | 59 | 2488023 | 615 | Distribution Circuit | 3rd Party | Vehicle | 43 | 26445 | 38.8458 | -121.4821 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0077761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1949916 | 0 | Non-EPSS | N | 2024 | A-B-C GRD TIME OC
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20240617 | 2239 | 20240618 | 7 | 2488702 | 88 | Distribution Circuit | Animal | Squirrel | 633 | 54194 | 39.0014 | -121.0224 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077913 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950018 | 0 | EPSS Ckt | Y | 2024 | GRD & INST OC
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 8509 | 20240618 | 115 | 20240618 | 206 | 2488810 | 51 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 3680 | 38.7803 | -121.2628 | No | Clear;32-90 F | Elbow | Broken | 24-0052997 | UG | Sus | 46141004 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950032 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | OCB | 1104/2 | 20240618 | 244 | 20240618 | 456 | 2488841 | 132 | Distribution Circuit | Animal | Squirrel | 3096 | 345336 | 39.0444 | -121.0911 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950038 | 0 | EPSS Ckt | Y | 2024 | GRD
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | FUSE | 9671 | 20240618 | 729 | 20240618 | 1250 | 2488924 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 321 | 38.8111 | -121.3121 | No | Clear;32-90 F | Jumper | Burned Open | 24-0078017 | OH | Sus | 31697666 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950137 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222207056060 | 20240618 | 823 | 20240618 | 846 | 2489032 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 23 | 39.2032 | -121.2225 | No | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 24-0078010 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950122 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1106 | 152561106 | TRANSFORMER | 222284842101 | 20240618 | 919 | 20240618 | 1646 | 2488974 | 447 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1788 | 38.8197 | -121.1989 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0078041 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950189 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 20240618 | 1214 | 20240618 | 1332 | 2489318 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 624 | 38.9807 | -120.9404 | No | Clear;32-90 F | Insulator | Broken | 24-0078152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950241 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 533042 | 20240618 | 1555 | 20240618 | 1617 | 2489506 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 247 | 5434 | 38.9971 | -121.1168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950282 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 867 | 20240618 | 1751 | 20240619 | 100 | s1950299 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 14093 | 39.5538 | -120.7768 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0078296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950299 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20240618 | 2043 | 20240619 | 1442 | 2489642 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 938 | 883411 | 38.7391 | -120.6681 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0078318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1950306 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | RECLOSER | 19582 | 20240618 | 2146 | 20240619 | 705 | 2489681 | 559 | Distribution Circuit | 3rd Party | Vehicle | 411 | 74008 | 38.753 | -120.823 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0078325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950314 | 0 | EPSS Ckt | Y | 2024 | A/B
SIERRA | NEVADA | ALLEGHANY SUB | 15210 | OCB | 52G | 20240619 | 147 | 20240619 | 159 | 2489735 | 12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 352 | 4224 | 39.5686 | -120.6283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950342 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 973602 | 20240619 | 838 | 20240619 | 1013 | 2489871 | 95 | Distribution Circuit | Animal | Bird found | 29 | 2755 | 39.2173 | -121.1917 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950399 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | JUMPER | OJ'S SS OF CGC 223311555726 | 20240619 | 956 | 20240619 | 1248 | 2489897 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 172 | 39.1906 | -120.8315 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0078415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950417 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ'S 4 SPANS SS OF CGC 222445360625 | 20240619 | 1004 | 20240619 | 1112 | 2489970 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 68 | 39.3259 | -121.1386 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0078429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950435 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 663774 | 20240619 | 1102 | 20240619 | 1119 | 2490001 | 17 | Distribution Circuit | Vegetation | Tree - fell into line | 1433 | 24361 | 39.1182 | -121.0373 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950449 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20240619 | 1711 | 20240620 | 206 | 2490198 | 535 | Distribution Circuit | 3rd Party | Customer Equipment | 173 | 33905 | 39.3251 | -120.6429 | No | Clear;32-90 F | Other | Failed/Faulted | 24-0078516 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950481 | 0 | EPSS Ckt | Y | 2024 | A- GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 172898 | 20240620 | 1107 | 20240620 | 1205 | 2490789 | 58 | Distribution Circuit | Company Initiated | Personnel- company | 144 | 8352 | 38.7717 | -120.5839 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078682 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950611 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31873 | 20240620 | 1717 | 20240620 | 2122 | 2491056 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1715 | 39.2951 | -120.9696 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0078822 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1950659 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222528051150 | 20240620 | 1852 | 20240620 | 2053 | 2491093 | 121 | Transformer only | Animal | Other | 1 | 121 | 39.0675 | -121.1111 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0078847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950678 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | SWITCH | 2795 | 20240620 | 1904 | 20240621 | 441 | 2491084 | 577 | Distribution Circuit | 3rd Party | Vehicle | 370 | 213490 | 39.191 | -120.9761 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0078835 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950669 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2084 | 20240620 | 2046 | 20240621 | 139 | 2491146 | 293 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 353 | 82906 | 39.0318 | -120.9741 | No | Clear;32-90 F |  |  | 24-0078846 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950677 | 0 | EPSS Ckt | Y | 2024 | AB INST OC
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20240621 | 616 | 20240621 | 912 | 2491250 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 238 | 41888 | 38.9847 | -121.366 | No | Clear;32-90 F |  |  | 24-0078909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950735 | 0 | EPSS Ckt | N | 2024 | C GRD TIME OC
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1101/2 | 20240621 | 830 | 20240621 | 848 | 2491497 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 2284 | 36842 | 39.02 | -120.8294 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078975 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950820 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | RECLOSER | 51738 | 20240621 | 1123 | 20240621 | 1210 | 2491773 | 47 | Distribution Circuit | Animal | Squirrel | 2209 | 103823 | 38.6795 | -120.9797 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950904 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 19772 | 20240621 | 1204 | 20240621 | 1518 | 2491848 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 247 | 47918 | 38.713 | -121.0455 | No | Clear;32-90 F |  |  | 24-0079126 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950915 | 0 | EPSS Ckt | Y | 2024 | GRD INST OC
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 2102 | 20240621 | 1204 | 20240621 | 1227 | 2491826 | 23 | Distribution Circuit | 3rd Party | Metallic Balloon | 1081 | 24863 | 38.6825 | -120.8522 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950911 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 365826 | 20240621 | 1244 | 20240621 | 1323 | 2491889 | 39 | Distribution Circuit | Company Initiated | Personnel- company | 66 | 2574 | 38.798 | -120.8222 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1950932 | 0 | EPSS Ckt | N | 2024 | A-C
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | OCB | 2105/2 | 20240621 | 1938 | 20240621 | 2338 | 2492155 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4021 | 587035 | 38.6597 | -120.9472 | No | Clear;32-90 F |  |  | 24-0079317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950962 | 0 | EPSS Ckt | Y | 2024 | A- GRD SET A RLY TARGET- TRIP
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 465074 | 20240621 | 2042 | 20240622 | 430 | 2492177 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 19944 | 38.8911 | -121.0981 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0079324 | OH | Sus | 31697908 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | Yes | No | 1950968 | 0 | EPSS Ckt | Y | 2024 | A- C
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7591 | 20240622 | 1015 | 20240622 | 1449 | 2492446 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 914 | 38.7362 | -121.4363 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0079401 | OH | Sus | 46267660 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951053 | 1 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223166441174 | 20240622 | 1207 | 20240622 | 1420 | 2492436 | 133 | Transformer only | 3rd Party | Vehicle | 1 | 133 | 38.7918 | -120.89 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951064 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18531 | 20240622 | 1241 | 20240622 | 1731 | 2492531 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 598 | 38.7627 | -120.7061 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079424 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951065 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | TRANSFORMER | 221809647842 | 20240622 | 1921 | 20240622 | 2032 | 2492723 | 71 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 71 | 38.9785 | -121.3647 | No | Clear;Above 90 |  |  | 24-0079473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951088 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20240623 | 906 | 20240623 | 1636 | 2492917 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 674 | 164970 | 39.2129 | -121.0129 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079513 | OH | Sus | 46267803 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951139 | 0 | EPSS Ckt | Y | 2024 | C- GRD INST OC
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222609054476 | 20240623 | 927 | 20240623 | 1258 | 2492884 | 211 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 211 | 39.1583 | -121.0808 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951144 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223473539157 | 20240623 | 950 | 20240623 | 1123 | 2492938 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 279 | 38.7355 | -120.7834 | No | Clear;32-90 F | Secondary | Broken | 24-0079525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951150 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | TRANSFORMER | 221907639528 | 20240623 | 2044 | 20240623 | 2103 | 2493141 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 38 | 38.7517 | -121.3305 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0079578 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951195 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20240624 | 212 | 20240625 | 45 | 2493254 | 1353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 722 | 384266 | 38.6091 | -120.7023 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079605 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951218 | 0 | EPSS Ckt | Y | 2024 | A/GRD
SIERRA | PLACER | WEIMAR-1102 | 152491102 | JUMPER | OJ AT CGC 222823549505 TWD SOUTH | 20240624 | 803 | 20240624 | 1902 | 2494488 | 659 | Distribution Circuit | Animal | Other | 13 | 8567 | 39.0216 | -121.0072 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0079919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1951506 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1104 | 152461104 | OTHER | WIRE DOWN SS OF 222664545833 | 20240624 | 826 | 20240624 | 1639 | 2493446 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 36413 | 38.9212 | -121.0649 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0079666 | OH | Sus | 46268067 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1951306 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 56468 | 20240624 | 905 | 20240624 | 925 | 2493552 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 1628 | 32560 | 39.2411 | -121.0378 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951338 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20240624 | 1117 | 20240624 | 1357 | 2493743 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1028 | 136088 | 38.7759 | -120.4031 | No | Clear;32-90 F |  |  | 24-0079751 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951406 | 0 | EPSS Ckt | Y | 2024 | A & GRD
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20240624 | 1300 | 20240624 | 1426 | 2493811 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 602 | 38.7521 | -120.6282 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0079771 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1951418 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 294550 | 20240624 | 2122 | 20240624 | 2130 | 2494728 | 8 | Distribution Circuit | 3rd Party | Metallic Balloon | 947 | 7576 | 38.6674 | -120.9933 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080025 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1951591 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | BELL-1108 | 152701108 | JUMPER | OJ 2 SPANS W/OF 35023 | 20240624 | 2144 | 20240625 | 226 | 2494741 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 9588 | 38.9529 | -121.0941 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0080024 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1951590 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 56026 | 20240625 | 658 | 20240625 | 1109 | 2494968 | 251 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 233 | 58483 | 38.6906 | -120.7644 | No | Partly Cloudy;32-90 F |  |  | 24-0080146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1951690 | 0 | EPSS Ckt | Y | 2024 | A-B-GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 9683 | 20240625 | 658 | 20240625 | 944 | 2495256 | 166 | Distribution Circuit | Animal | Squirrel | 1 | 166 | 38.6936 | -120.8212 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0080222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951818 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223239945635 | 20240625 | 1157 | 20240625 | 1233 | 2495409 | 36 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 36 | 38.9138 | -120.8623 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0080341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951895 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRANSFORMER | 222597156798 | 20240625 | 1528 | 20240625 | 1603 | 2495647 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 70 | 39.2225 | -121.0844 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0080453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1951934 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240625 | 1744 | 20240625 | 1855 | 2495765 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 12283 | 39.1986 | -121.0343 | No | Partly Cloudy;32-90 F |  |  | 24-0080526 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951961 | 0 | EPSS Ckt | Y | 2024 | C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240626 | 529 | 20240627 | 157 | 2496092 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 2111 | 128635 | 39.2042 | -121.2005 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0080650 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1952033 | 0 | EPSS Ckt | Y | 2024 | B/GRD
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20240626 | 800 | 20240626 | 1028 | 2496338 | 148 | Distribution Circuit | Animal | Bird found | 840 | 52597 | 38.6858 | -121.0119 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0080717 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952103 | 0 | EPSS Ckt | Y | 2024 | A & C
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223045834931 | 20240626 | 1727 | 20240627 | 156 | 2497042 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2299 | 38.6213 | -120.9341 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0081044 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952272 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 37071 | 20240626 | 2003 | 20240627 | 252 | 2497162 | 409 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 15951 | 38.7934 | -121.0413 | No | Clear;32-90 F |  |  | 24-0081118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952328 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20240626 | 2101 | 20240627 | 27 | 2497188 | 206 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 456 | 93936 | 38.8637 | -121.1283 | No | Clear;32-90 F |  |  | 24-0081074 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952290 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | OCB | 1103/2 | 20240627 | 23 | 20240627 | 734 | 2497263 | 431 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1301 | 313393 | 38.7393 | -120.6773 | No | Clear;32-90 F |  |  | 24-0081117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1952327 | 0 | EPSS Ckt | Y | 2024 | A- GRD PH INST OC
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | JUMPER | OJ'S @ CGC 222690838734 | 20240627 | 725 | 20240627 | 1105 | 2497369 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 220 | 38.7264 | -121.057 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0081157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952355 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20240627 | 913 | 20240627 | 1235 | 2497523 | 202 | Distribution Circuit | Animal | Bird found | 426 | 86052 | 39.2034 | -121.0788 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952443 | 0 | EPSS Ckt | Y | 2024 | B-C- INST OC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223788235985 | 20240627 | 1309 | 20240627 | 2108 | 2497765 | 479 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 479 | 38.6474 | -120.6748 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0081445 | OH | Sus | 46269506 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1952534 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | OTHER | J452 TWD T5254 | 20240627 | 1642 | 20240628 | 126 | 2497908 | 524 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 524 | 38.7765 | -121.2599 | No | Clear;Above 90 | Transformer (UG) | Leaking | 24-0081332 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952548 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20240627 | 1648 | 20240627 | 1952 | 2497906 | 171 | Distribution Circuit | Vegetation | Tree - fell into line | 1042 | 91986 | 38.8154 | -120.8221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952549 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | FLINT-1101 | 152531101 | SWITCH | 958726 | 20240627 | 1756 | 20240628 | 516 | 2497935 | 680 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4760 | 38.8934 | -121.0678 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081513 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952560 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 50324 | 20240627 | 1922 | 20240628 | 223 | 2497994 | 421 | Distribution Circuit | 3rd Party | Vehicle | 1958 | 241981 | 38.6953 | -120.818 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0081525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952568 | 0 | EPSS Ckt | Y | 2024 | A-C INST OC
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 19632 | 20240627 | 2047 | 20240627 | 2228 | 2498039 | 101 | Distribution Circuit | 3rd Party | Vehicle | 1520 | 153520 | 38.6873 | -121.0085 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0081540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952580 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7883 | 20240628 | 737 | 20240628 | 1058 | 2498286 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 603 | 38.8972 | -121.415 | No | Clear;32-90 F |  |  | 24-0081778 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952820 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224086039830 | 20240628 | 1051 | 20240628 | 1429 | 2498630 | 218 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 436 | 38.7512 | -120.568 | No | Clear;32-90 F |  |  | 24-0081802 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1952839 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 176597 | 20240628 | 1535 | 20240628 | 2113 | 2498835 | 338 | Distribution Circuit | Animal | Other | 69 | 23322 | 38.9096 | -120.8454 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0081780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952890 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222052955135 | 20240628 | 1757 | 20240629 | 112 | 2498960 | 435 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 870 | 39.1787 | -121.277 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0081968 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1952904 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | TRANSFORMER | 222502845552 | 20240629 | 730 | 20240629 | 1255 | 2499113 | 325 | Transformer only | Vegetation | Tree - fell into line | 2 | 650 | 38.9139 | -121.1214 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0082019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952956 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20240629 | 1542 | 20240630 | 2105 | 2499418 | 1763 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1038 | 89302 | 38.8932 | -120.9965 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0082094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1953016 | 0 | EPSS Ckt | N | 2024 | none
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 37071 | 20240629 | 1941 | 20240629 | 2154 | 2499516 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 5187 | 38.7934 | -121.0413 | No | Clear;Above 90 |  |  | 24-0082124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1953044 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | JUMPER | OJ TWD CGC 222703852548 | 20240629 | 2210 | 20240630 | 1159 | 2499521 | 829 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1658 | 39.1063 | -121.0494 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0082140 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1953061 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20240630 | 210 | 20240630 | 1324 | 2499569 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 1760 | 113200 | 38.7309 | -120.8421 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0082146 | OH | Sus | 46270441 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | Yes | No | 1953066 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20240630 | 604 | 20240630 | 1141 | 2499633 | 337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1602 | 146157 | 38.9052 | -120.8374 | No | Clear;32-90 F |  |  | 24-0082155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1953075 | 0 | EPSS Ckt | Y | 2024 | AB
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | TRANSFORMER | 223320137191 | 20240630 | 1315 | 20240630 | 1923 | 2499690 | 368 | Transformer only | Vegetation | Tree - fell into line | 2 | 736 | 38.682 | -120.8382 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0082206 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1953117 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | OCB | 2106/2 | 20240630 | 1844 | 20240701 | 406 | 2500119 | 420 | Distribution Circuit | Equipment Failure/Involved | Underground | 8113 | 1889086 | 38.6555 | -121.0603 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 24-0082238 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1953151 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 13751 | 20240630 | 1845 | 20240630 | 2046 | 2500087 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 4477 | 38.663 | -120.9939 | No | Clear;Above 90 |  |  | 24-0082247 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1953160 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20240701 | 522 | 20240701 | 705 | 2500371 | 103 | Distribution Circuit | Animal | Bird found | 522 | 46761 | 38.9452 | -121.1218 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082280 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953199 | 0 | EPSS Ckt | Y | 2024 | A- B -INST OC
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | SWITCH | 20615 | 20240701 | 838 | 20240701 | 1148 | 2500566 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1710 | 38.6834 | -120.8142 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0082345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953263 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | RECLOSER | 19642 | 20240701 | 1547 | 20240702 | 950 | 2501015 | 793 | Distribution Circuit | Equipment Failure/Involved | Underground | 2058 | 280064 | 38.6832 | -121.0684 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0082630 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953368 | 0 | EPSS Ckt | Y | 2024 | C- GRD
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | FUSE | 18259 | 20240701 | 1845 | 20240701 | 2040 | 2501175 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1380 | 38.7072 | -121.0949 | No | Clear;Above 90 |  |  | 24-0082727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953407 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 22011 | 20240702 | 917 | 20240702 | 1335 | 2501729 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 2506 | 90832 | 38.7017 | -120.8317 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0082882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1953550 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20240702 | 1100 | 20240702 | 1116 | 2501858 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 1029 | 16464 | 38.9052 | -120.8374 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0063883 | OH | Sus | 8205118 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953592 | 0 | EPSS Ckt | Y | 2024 | b & grd
SIERRA | PLACER | DEL MAR-2110 | 152582110 | FUSE | 2625 | 20240702 | 1532 | 20240703 | 942 | 2502341 | 884 | Distribution Circuit | Equipment Failure/Involved | Underground | 96 | 20762 | 38.8145 | -121.2367 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0083196 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953666 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20240702 | 1555 | 20240702 | 1838 | 2502379 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 533 | 85115 | 39.214 | -120.8098 | No | Clear;Above 90 |  |  | 24-0083157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953648 | 0 | EPSS Ckt | Y | 2024 | INST OC- GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222919155369 | 20240702 | 1905 | 20240702 | 2039 | 2502852 | 94 | Transformer only | Vegetation | Tree - fell into line | 1 | 94 | 39.1823 | -120.9719 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0083268 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1953709 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | OTHER | 1 SPAN OF 1 WIRE DOWN SS OF FUCO 10695 | 20240702 | 2010 | 20240703 | 331 | 2503101 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 377 | 101797 | 38.593 | -121.0143 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0083294 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1953729 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223664537620 | 20240703 | 28 | 20240703 | 128 | 2503332 | 60 | Transformer only | 3rd Party | Vehicle | 4 | 240 | 38.6926 | -120.7172 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0083385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953828 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20240703 | 217 | 20240703 | 409 | 2503413 | 112 | Distribution Circuit | Animal | Bird found | 198 | 22176 | 38.8543 | -121.1728 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083386 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953829 | 0 | EPSS Ckt | Y | 2024 | B- C
SIERRA | PLACER | PENRYN-1106 | 152561106 | RECLOSER | 51674 | 20240703 | 730 | 20240703 | 758 | 2503510 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 932 | 9832 | 38.8252 | -121.192 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0075781 | OH | Sus | 35550363 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953860 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | PENRYN-1106 | 152561106 | SWITCH | 2482 | 20240703 | 1228 | 20240703 | 1246 | 2503789 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 76 | 1368 | 38.831 | -121.1921 | No | Clear-Heat Wave;Above 90 | Switch (UG) | Normal | 24-0075781 | UG | Sus | 35550363 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953917 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3901 | 20240703 | 1334 | 20240703 | 1509 | 2503825 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 475 | 39.2548 | -121.1329 | No | Clear-Heat Wave;Above 90 | Crossarm- Wood | Broken | 24-0083603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953922 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 4079 | 20240703 | 1341 | 20240703 | 1554 | 2503845 | 133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 10113 | 38.9282 | -121.0708 | No | Clear-Heat Wave;Above 90 | Cutout- fuse holder | Burned/flashed | 24-0083656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953931 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | OCB | 1102/2 | 20240703 | 1611 | 20240703 | 1724 | 2504063 | 73 | Distribution Circuit | Animal | Other | 499 | 36427 | 38.7444 | -121.1609 | No | Clear-Heat Wave;Above 90 | Recloser | Burned/flashed | 24-0083724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1953959 | 0 | Non-EPSS | N | 2024 | A-B-C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 458102 | 20240703 | 1807 | 20240703 | 2118 | 2504199 | 191 | Distribution Circuit | Company Initiated | Coordination failure | 264 | 50424 | 39.1494 | -121.0345 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 24-0083774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953981 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222741554834 | 20240703 | 1823 | 20240704 | 1003 | 2504527 | 940 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 940 | 39.1682 | -121.0339 | No | Clear;32-90 F | Bushing | Broken | 24-0083926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954096 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 20240703 | 1850 | 20240704 | 159 | 2504266 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 233 | 42653 | 38.8435 | -120.8737 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken | 24-0083798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953994 | 0 | EPSS Ckt | Y | 2024 | C- GRD
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222775158324 | 20240703 | 1924 | 20240703 | 2105 | 2504336 | 101 | Transformer only | Environmental/External | Fire- Forest/Grass | 7 | 707 | 39.2641 | -121.0209 | No | Heat Wave-Clear;Above 90 | Transformer | Burned/flashed | 24-0083816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954008 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222775158324 | 20240703 | 1924 | 20240703 | 2105 | 2504336 | 101 | Transformer only | Environmental/External | Fire- Forest/Grass | 7 | 707 | 39.2641 | -121.0209 | No | Heat Wave-Clear;Above 90 | Transformer | Burned/flashed | 24-0083816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954008 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224111840193 | 20240703 | 1947 | 20240703 | 2159 | 2504264 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 528 | 38.7608 | -120.5589 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954027 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224111840193 | 20240703 | 1947 | 20240703 | 2159 | 2504264 | 132 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 528 | 38.7608 | -120.5589 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954027 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 2471 | 20240704 | 142 | 20240704 | 1333 | 2504653 | 711 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 710 | 38.7831 | -121.2637 | No | Clear;32-90 F | Connector or Splice (UG) | Failed/Faulted | 24-0083916 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954088 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | FUSE | 4603 | 20240704 | 434 | 20240704 | 1213 | 2504692 | 459 | Distribution Circuit | Equipment Failure/Involved | Underground | 90 | 30297 | 38.7142 | -121.0918 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0083949 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954109 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 2718 | 20240704 | 1022 | 20240704 | 1249 | 2504945 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3432 | 291507 | 39.2349 | -121.2209 | No | Clear-Heat Wave;Above 90 |  |  | 24-0083977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954127 | 0 | EPSS Ckt | Y | 2024 | GRD
SIERRA | PLACER | LINCOLN-1102 | 153701102 | FUSE | 8361 | 20240704 | 1057 | 20240704 | 1358 | 2504965 | 181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 7059 | 38.8961 | -121.303 | No | Clear-Heat Wave;Above 90 | Jumper | Burned Open | 24-0083998 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954136 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | RECLOSER | 385236 | 20240704 | 1346 | 20240704 | 1458 | 2505056 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1253 | 90216 | 38.6481 | -121.0728 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954151 | 0 | EPSS Ckt | Y | 2024 | A AND GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20240704 | 1406 | 20240704 | 1850 | 2505087 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 871 | 39207 | 39.1911 | -120.9965 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0084032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1954153 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | OCB | 1101/2 | 20240704 | 1758 | 20240705 | 956 | 2505326 | 958 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2085 | 608550 | 39.0363 | -120.9881 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084090 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954177 | 0 | EPSS Ckt | Y | 2024 | C PHASE & INST OC
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | TRANSFORMER | T1919 | 20240704 | 1858 | 20240704 | 2003 | 2505418 | 65 | Transformer only | Equipment Failure/Involved | Underground | 12 | 780 | 38.7471 | -121.2177 | No | Clear-Heat Wave;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084121 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954204 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222240556812 | 20240704 | 2319 | 20240705 | 426 | 2505594 | 307 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 307 | 39.2246 | -121.2101 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084175 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954260 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | RECLOSER | 18754 | 20240705 | 404 | 20240705 | 1738 | 2505805 | 814 | Distribution Circuit | Equipment Failure/Involved | Underground | 1255 | 344301 | 38.6774 | -121.0868 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0084236 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1954298 | 0 | EPSS Ckt | Y | 2024 | A C GRD
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222311845334 | 20240705 | 742 | 20240705 | 1355 | 2505748 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 559 | 38.9076 | -121.1891 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0084248 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954303 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | TRANSFORMER | 222302539227 | 20240705 | 1140 | 20240705 | 1203 | 2505980 | 23 | Transformer only | Vegetation | Tree - fell into line | 2 | 46 | 38.7408 | -121.1937 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0084300 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954333 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20240705 | 1649 | 20240705 | 1757 | 2506296 | 68 | Distribution Circuit | 3rd Party | Customer Equipment | 666 | 45288 | 38.9128 | -120.82 | No | Clear;Above 90 | Generator | Normal | 24-0084393 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954383 | 0 | EPSS Ckt | Y | 2024 | A-C INST
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222807655926 | 20240705 | 1924 | 20240705 | 2235 | 2506550 | 191 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 382 | 39.1982 | -121.0103 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954411 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2106 | 152582106 | OTHER | T10447 TWD T10448 | 20240705 | 2018 | 20240705 | 2320 | 2507198 | 182 | Distribution Circuit | Equipment Failure/Involved | Underground | 52 | 9464 | 38.7902 | -121.1882 | No | Clear;Above 90 | Transformer (UG) | Failed/Faulted | 24-0084461 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954458 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32311 | 20240705 | 2235 | 20240706 | 847 | 2507204 | 612 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 612 | 38.862 | -120.8474 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084489 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954462 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 9432 | 20240705 | 2344 | 20240706 | 640 | 2507230 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 557 | 157420 | 38.7312 | -120.8428 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0084494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | Yes | No | 1954467 | 0 | EPSS Ckt | Y | 2024 | A-C SGF DCD
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20240706 | 616 | 20240706 | 940 | 2507354 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 1675 | 298668 | 39.0162 | -120.8351 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0084522 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954498 | 0 | EPSS Ckt | Y | 2024 | A+C
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223222539504 | 20240706 | 732 | 20240706 | 821 | 2507379 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 49 | 38.7458 | -120.8707 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0084532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954502 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 22131 | 20240706 | 1442 | 20240709 | 1432 | 2507639 | 3968 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1957 | 3942 | 38.7274 | -120.742 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0084625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 500639 | No | No | No | 1954535 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | TRANSFORMER | 223405639007 | 20240706 | 1504 | 20240706 | 1535 | 2507657 | 31 | Transformer only | Environmental/External | Fire- Forest/Grass | 3 | 93 | 38.7318 | -120.8074 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0084637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954543 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 663774 | 20240706 | 1533 | 20240706 | 1745 | 2507691 | 132 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1432 | 186564 | 39.1182 | -121.0373 | No | Clear;Above 90 | Recloser | Normal | 24-0084638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954544 | 0 | EPSS Ckt | Y | 2024 | C INST OC
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | OCB | 1103/2 | 20240706 | 1731 | 20240706 | 2046 | 2507851 | 195 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2875 | 542343 | 39.0444 | -121.0912 | No | Clear;Above 90 | Circuit Breaker | Normal | 24-0084660 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954558 | 0 | EPSS Ckt | Y | 2024 | SET A RLY & TRIP TGT
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 663774 | 20240706 | 1752 | 20240706 | 2355 | 2507918 | 363 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1432 | 259676 | 39.1182 | -121.0373 | No | Clear;Above 90 | Recloser | Normal | 24-0084638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954567 | 0 | EPSS Ckt | N | 2024 | A C
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2084 | 20240706 | 1823 | 20240707 | 1334 | 2508045 | 1151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 352 | 52025 | 39.0318 | -120.9741 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954582 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 48894 | 20240706 | 1829 | 20240706 | 2114 | 2508121 | 165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 206 | 15540 | 39.1191 | -120.9513 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084685 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954583 | 0 | EPSS Ckt | Y | 2024 | C.GRD- INST OC
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222335039412 | 20240706 | 1855 | 20240706 | 2236 | 2508119 | 221 | Transformer only | Vegetation | Tree - branch fell on line | 8 | 1768 | 38.7458 | -121.1821 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0084698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954596 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | OCB | 1103/2 | 20240706 | 2104 | 20240706 | 2331 | 2508432 | 147 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2875 | 205194 | 39.0444 | -121.0912 | No | Clear;Above 90 | Circuit Breaker | Normal | 24-0084660 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954638 | 0 | EPSS Ckt | Y | 2024 | A B C ST A RLY
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | SWITCH | NG PHA AT 778538 | 20240706 | 2113 | 20240707 | 146 | 2508590 | 273 | Distribution Circuit | Equipment Failure/Involved | Underground | 2008 | 423680 | 38.8287 | -121.2659 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0084792 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1954690 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 941844 | 20240707 | 249 | 20240707 | 953 | 2508641 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 598 | 94628 | 39.0933 | -120.9512 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0084799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1954698 | 0 | EPSS Ckt | Y | 2024 | b grd inst oc
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | SWITCH | 20615 | 20240707 | 1120 | 20240707 | 1146 | 2508861 | 26 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 416 | 38.6834 | -120.8142 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0084850 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954736 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240707 | 1353 | 20240707 | 1824 | 2508992 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2683 | 349703 | 38.6943 | -120.6784 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954752 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | SWITCH | 50057 | 20240707 | 1620 | 20240707 | 1820 | 2509134 | 120 | Distribution Circuit | Equipment Failure/Involved | Underground | 472 | 56640 | 38.8208 | -121.2716 | No | Clear;Above 90 | Switch (UG) | Failed/Faulted | 24-0084792 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954775 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 663774 | 20240707 | 1634 | 20240707 | 2123 | 2509164 | 289 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1433 | 224183 | 39.1182 | -121.0373 | No | Clear;Above 90 | Recloser | Normal | 24-0084913 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954777 | 0 | EPSS Ckt | Y | 2024 | C INST OC
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | OCB | 1103/2 | 20240707 | 1757 | 20240707 | 2133 | 2509291 | 216 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 2875 | 214258 | 39.0444 | -121.0912 | No | Clear;Above 90 | Circuit Breaker | Normal | 24-0084925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954784 | 0 | EPSS Ckt | Y | 2024 | ABC
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 32127 | 20240707 | 1849 | 20240708 | 715 | 2509344 | 746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 21736 | 39.0379 | -121.0515 | No | Clear;Above 90 | Conductor- Overhead | Arcing | 24-0084940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954796 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20240707 | 1914 | 20240708 | 220 | 2509376 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 272 | 34030 | 38.8995 | -120.8545 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0084949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954806 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | PLACER | PLEASANT GROVE-2109 | 152442109 | INTERRUPTER | 338324 | 20240707 | 2006 | 20240707 | 2236 | 2509448 | 122 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 86 | 12900 | 38.8286 | -121.2659 | No | Clear;Above 90 | Interrupter | Normal | 24-0084970 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954826 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20711 | 20240707 | 2137 | 20240707 | 2328 | 2509524 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2775 | 38.6169 | -120.9542 | No | Clear;32-90 F |  |  | 24-0085022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1954872 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15317 | 20240708 | 746 | 20240708 | 1008 | 2509902 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 284 | 38.9979 | -121.3167 | No | Clear;32-90 F |  |  | 24-0085142 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955009 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50008 | 20240708 | 1358 | 20240708 | 1449 | 2510462 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 2652 | 39.2226 | -121.0515 | No | Clear;Above 90 | Crossarm- Steel | Broken | 24-0085253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955073 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 501650 | 20240708 | 1704 | 20240708 | 1904 | 2510638 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4920 | 38.692 | -120.7038 | No | Clear;Above 90 |  |  | 24-0085331 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1955090 | 0 | EPSS Ckt | Y | 2024 | AC INST OC
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 8399 | 20240708 | 2246 | 20240708 | 2333 | 2510940 | 47 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 329 | 39.2222 | -121.2058 | No | Clear;32-90 F | Conductor- Overhead | Arcing | 24-0085428 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955151 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224031840095 | 20240708 | 2257 | 20240709 | 855 | 2510962 | 598 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2392 | 38.7592 | -120.5871 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0085446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955173 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240709 | 554 | 20240709 | 707 | 2511130 | 73 | Distribution Circuit | Animal | Bird found | 2113 | 147781 | 39.2042 | -121.2005 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0085459 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955180 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 16747 | 20240709 | 1112 | 20240709 | 1239 | 2511499 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 435 | 38.8462 | -121.3908 | No | Clear;32-90 F |  |  | 24-0085654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1955330 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223658434345 | 20240709 | 1256 | 20240709 | 1914 | 2511575 | 378 | Transformer only | Vegetation | Tree - fell into line | 4 | 1512 | 38.6025 | -120.721 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0085750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955357 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | SWITCH | 4603 | 20240709 | 1415 | 20240709 | 1502 | 2511730 | 47 | Distribution Circuit | Company Initiated | Return Circuit Normal | 39 | 1273 | 38.7142 | -121.0918 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0083949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955362 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK SUB | 15229 | OTHER | TAMARACK | 20240709 | 2257 | 20240710 | 157 | 2511994 | 180 | Distribution Circuit | 3rd Party | Vehicle | 1900 | 342000 | 0 | 0 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0085884 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1955439 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 881364 | 20240710 | 58 | 20240710 | 412 | 2512022 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 134 | 24344 | 38.8856 | -121.2378 | No | Clear;32-90 F |  |  | 24-0085891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955449 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | PLACER | TAMARACK-1101 | 152291101 | RECLOSER | 58642 | 20240710 | 158 | 20240710 | 601 | 2512029 | 179 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1405 | 316055 | 39.325 | -120.3797 | No | Clear;32-90 F | Recloser | Normal | 24-0085884 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1955450 | 0 | EPSS Ckt | Y | 2024 | A-C
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | T4033 | 20240710 | 950 | 20240710 | 1053 | 2512334 | 63 | Transformer only | 3rd Party | Customer Equipment | 5 | 315 | 38.6953 | -121.0069 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0086093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955616 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRANSFORMER | 222806150217 | 20240710 | 1104 | 20240710 | 1832 | 2512450 | 448 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 448 | 39.0408 | -121.013 | No | Clear;Above 90 |  |  | 24-0086181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1955632 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 34649 | 20240710 | 1254 | 20240710 | 1331 | 2512527 | 37 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 296 | 38.7505 | -121.1722 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086161 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955629 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJ'S 4 POLES SS OF CGC 222389852660 | 20240710 | 1505 | 20240710 | 1758 | 2512626 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 173 | 39.1069 | -121.1596 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955645 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20240710 | 1541 | 20240710 | 1703 | 2512705 | 82 | Distribution Circuit | Vegetation | Tree - branch fell on line | 633 | 51906 | 39.0014 | -121.0224 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955656 | 0 | EPSS Ckt | Y | 2024 | B & INST OC
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20240710 | 1544 | 20240710 | 1751 | 2512707 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 12065 | 38.9858 | -121.022 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1955670 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | PLACER-1104 | 152461104 | TRANSFORMER | 222639545616 | 20240710 | 2348 | 20240711 | 220 | 2513046 | 152 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 760 | 38.9153 | -121.0735 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0086468 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955729 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | SWITCH | 1405 | 20240711 | 121 | 20240711 | 134 | 2513104 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 377 | 4901 | 39.1561 | -121.0634 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086409 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955738 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20240711 | 655 | 20240711 | 837 | 2513192 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 239 | 24378 | 38.9847 | -121.366 | No | Clear;32-90 F |  |  | 24-0086513 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1955756 | 0 | EPSS Ckt | N | 2024 | B- C GRD TIME OC
SIERRA | PLACER | TAMARACK SUB | 15229 | OCB | TAMARACK | 20240711 | 755 | 20240711 | 805 | 2513336 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2009 | 20090 | 0 | 0 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086552 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955792 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2740 | 20240711 | 1421 | 20240711 | 1439 | 2513900 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 446 | 8028 | 39.0342 | -120.9744 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1955979 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | TAMARACK-1101 | 152291101 | RECLOSER | 58642 | 20240711 | 1755 | 20240711 | 1843 | s1981276 | 48 | Distribution Circuit | Company Initiated | Coordination failure | 1404 | 67392 | 39.325 | -120.3797 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0086907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Three Phase Fault | 0 | No | No | No | 1981276 | 0 | EPSS Ckt | Y | 2024 | ABC
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 324510 | 20240711 | 1858 | 20240711 | 1949 | 2514291 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 10506 | 39.1033 | -121.0435 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0086935 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956023 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223283737709 | 20240711 | 2117 | 20240712 | 155 | 2514467 | 278 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 556 | 38.6962 | -120.8506 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956101 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 52763 | 20240712 | 631 | 20240712 | 808 | 2514697 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 388 | 38.912 | -121.2434 | No | Clear;32-90 F |  |  | 24-0087096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956162 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 36037 | 20240712 | 808 | 20240712 | 1133 | 2514825 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 205 | 38.9897 | -120.8721 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0087110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956190 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 8935 | 20240712 | 824 | 20240712 | 1012 | 2514777 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1728 | 39.2044 | -120.9583 | No | Clear-Heat Wave;32-90 F | Crossarm- Steel | Broken | 24-0087100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956166 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20240712 | 828 | 20240712 | 1013 | 2514810 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 261 | 18045 | 38.8415 | -121.0158 | No | Clear-Heat Wave;32-90 F |  |  | 24-0087107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956181 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | JUMPER | OJ 2 SS OF CGC# 223319039427 | 20240712 | 840 | 20240712 | 1044 | 2514841 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 248 | 38.743 | -120.8367 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0087114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956198 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 2414 | 20240712 | 936 | 20240712 | 1139 | 2514936 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 408 | 50184 | 38.9663 | -121.0352 | No | Clear-Heat Wave;Above 90 |  |  | 24-0087146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956234 | 0 | EPSS Ckt | Y | 2024 | B IOC
SIERRA | PLACER | WEIMAR-1102 | 152491102 | OCB | 1102/2 | 20240712 | 1253 | 20240712 | 1416 | 2515139 | 83 | Distribution Circuit | 3rd Party | Vehicle | 610 | 36030 | 39.0363 | -120.9882 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Together | 24-0087278 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956286 | 0 | EPSS Ckt | Y | 2024 | B C IOC
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | RECLOSER | 50514 | 20240712 | 1329 | 20240713 | 359 | 2515171 | 870 | Distribution Circuit | 3rd Party | Vehicle | 953 | 184114 | 38.8385 | -121.3225 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 24-0087290 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1956294 | 0 | Non-EPSS | N | 2024 | B GRD
SIERRA | PLACER | BELL-1108 | 152701108 | TRANSFORMER | 222532447893 | 20240712 | 1336 | 20240712 | 1530 | 2515178 | 114 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 228 | 38.9782 | -121.1102 | No | Clear-Heat Wave;Above 90 |  |  | 24-0087358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1956318 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9521 | 20240712 | 1744 | 20240712 | 2122 | 2515411 | 218 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 8 | 645 | 38.8844 | -121.4144 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Leaking | 24-0087412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956342 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | OCB | 2103/2 | 20240712 | 1800 | 20240713 | 1003 | 2515429 | 963 | Distribution Circuit | Equipment Failure/Involved | Underground | 3387 | 1446909 | 38.6555 | -121.0604 | No | Clear-Heat Wave;Above 90 | Elbow | Broken | 24-0087402 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956336 | 0 | EPSS Ckt | N | 2024 | A- GRD INST
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20240712 | 1832 | 20240712 | 2005 | 2515486 | 92 | Distribution Circuit | Animal | Bird found | 922 | 40782 | 38.6615 | -120.9109 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Normal | 24-0087407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956339 | 0 | EPSS Ckt | Y | 2024 | A
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7595 | 20240713 | 1000 | 20240713 | 1015 | 2515851 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 30 | 38.8243 | -121.45 | No | Partly Cloudy;32-90 F |  |  | 24-0087519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956459 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 9789 | 20240713 | 1034 | 20240713 | 1223 | 2515923 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2834 | 39.212 | -121.0191 | No | Partly Cloudy;32-90 F |  |  | 24-0087546 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956475 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 2414 | 20240713 | 1652 | 20240713 | 1821 | 2516172 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 36312 | 38.9663 | -121.0352 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0087596 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1956505 | 0 | EPSS Ckt | Y | 2024 | A-B- GRD INST
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20240713 | 1652 | 20240713 | 1817 | 2516170 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 903 | 76755 | 38.9732 | -121.0141 | No | Clear;Above 90 |  |  | 24-0087595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956504 | 0 | EPSS Ckt | Y | 2024 | B
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 164068 | 20240713 | 1652 | 20240713 | 1831 | 2516173 | 99 | Distribution Circuit | Company Initiated | Coordination failure | 975 | 96525 | 38.9466 | -121.0478 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0087597 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956506 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 16747 | 20240713 | 2003 | 20240713 | 2118 | 2516277 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 375 | 38.8462 | -121.3908 | No | Clear;32-90 F |  |  | 24-0087619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956531 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222409143623 | 20240713 | 2105 | 20240714 | 1014 | 2516300 | 789 | Transformer only | Vegetation | Tree - fell into line | 3 | 2367 | 38.861 | -121.155 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0087652 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1956563 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 7351 | 20240714 | 737 | 20240714 | 934 | 2516539 | 117 | Distribution Circuit | Animal | Bird found | 63 | 7371 | 38.9451 | -121.1196 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0087700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956610 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224335060258 | 20240714 | 1245 | 20240714 | 1751 | 2516662 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 306 | 39.3131 | -120.4693 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0087733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956645 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 84017 | 20240714 | 1634 | 20240714 | 2332 | 2516746 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 763 | 38.9121 | -121.2416 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0087742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | Yes | No | 1956653 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 8605 | 20240714 | 1952 | 20240714 | 2253 | 2516817 | 181 | Distribution Circuit | Animal | Bird found | 20 | 3620 | 38.8676 | -121.4787 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0087795 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956704 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJS 1 S/O CGC#222832549015 | 20240715 | 1050 | 20240715 | 1325 | 2517306 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 155 | 39.0082 | -121.0046 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0087956 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956878 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 13322 | 20240715 | 1137 | 20240715 | 1352 | 2517369 | 135 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 652 | 88020 | 38.769 | -120.9276 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0087996 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1956895 | 0 | EPSS Ckt | Y | 2024 | A+B+INST
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | TRANSFORMER | 223483938983 | 20240715 | 1600 | 20240715 | 1644 | 2517602 | 44 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 308 | 38.7295 | -120.779 | No | Clear;Above 90 | Secondary | Normal | 24-0088197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1956951 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9235 | 20240715 | 1710 | 20240715 | 2219 | 2517649 | 309 | Distribution Circuit | Vegetation | Tree - grew into line | 60 | 18540 | 38.9217 | -120.8957 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0088194 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956950 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 2194 | 20240716 | 4 | 20240716 | 24 | 2517785 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 3148 | 39.1529 | -121.0614 | No | Partly Cloudy;32-90 F | Switch (OH) | Burned/flashed | 24-0087917 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957002 | 0 | EPSS Ckt | Y | 2024 | BC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240716 | 525 | 20240716 | 1015 | 2517843 | 290 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2683 | 296241 | 38.6943 | -120.6784 | No | Clear;32-90 F |  |  | 24-0088258 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | No | No | 1957016 | 0 | EPSS Ckt | Y | 2024 | AB- SGF- DCD
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30349 | 20240716 | 846 | 20240716 | 912 | 2518019 | 26 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 37 | 962 | 39.1189 | -121.0365 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088333 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957105 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8967 | 20240716 | 940 | 20240716 | 949 | 2518103 | 9 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 47 | 423 | 39.138 | -121.0461 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957162 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8961 | 20240716 | 1116 | 20240716 | 1137 | 2518204 | 21 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 29 | 609 | 39.1453 | -121.0557 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957198 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8963 | 20240716 | 1249 | 20240716 | 1329 | 2518285 | 40 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 52 | 2080 | 39.1431 | -121.0565 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088500 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957222 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 887684 | 20240716 | 1300 | 20240717 | 145 | 2518201 | 765 | Distribution Circuit | 3rd Party | Vehicle | 547 | 197101 | 38.7891 | -120.1684 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0088514 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957225 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20240716 | 1417 | 20240716 | 1634 | 2518403 | 137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 873 | 117080 | 38.8963 | -121.1379 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1957244 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | TAMARACK-1101 | 152291101 | OCB | 1101/2 | 20240716 | 1848 | 20240717 | 1108 | 2518565 | 980 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1861 | 1795780 | 39.314 | -120.4962 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0088651 | OH | Sus | 31701109 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1957268 | 0 | EPSS Ckt | Y | 2024 | A- GRD INST
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222302339736 | 20240717 | 907 | 20240717 | 1347 | 2519300 | 280 | Transformer only | Unknown Cause | Patrol - not conducted | 6 | 1680 | 38.7547 | -121.1937 | No | Clear;32-90 F |  |  | 24-0088784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1957454 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | SWITCH | 1491 | 20240717 | 1048 | 20240717 | 1334 | 2519392 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 15936 | 39.1374 | -121.0436 | No | Clear;32-90 F | Insulator | Broken | 24-0088709 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957481 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | RECLOSER | 58642 | 20240717 | 1108 | 20240717 | 1438 | -2518565 | 210 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1403 | 262097 | 39.325 | -120.3797 | No | Clear;32-90 F | Recloser | Normal | 24-0088651 | OH | Sus | 31701109 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1957486 | 0 | EPSS Ckt | Y | 2024 | ABC
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | OCB | 1109/2 | 20240717 | 1151 | 20240717 | 1227 | 2519503 | 36 | Distribution Circuit | Animal | Bird found | 1103 | 39122 | 39.0444 | -121.091 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0088873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957493 | 0 | EPSS Ckt | Y | 2024 | A C INST
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 8971 | 20240717 | 2051 | 20240717 | 2202 | 2519914 | 71 | Distribution Circuit | Animal | Bird found | 54 | 3834 | 38.6756 | -120.6646 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089104 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957578 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1105 | 152571105 | FUSE | 1873 | 20240718 | 1039 | 20240719 | 35 | 2520183 | 836 | Distribution Circuit | Equipment Failure/Involved | Underground | 114 | 42117 | 38.7234 | -121.2091 | No | Clear;32-90 F | Elbow | Failed/Faulted | 24-0089290 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1957682 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4347 | 20240718 | 1345 | 20240718 | 1724 | 2520313 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 876 | 39.2094 | -121.2026 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0089363 | OH | Sus | 31701156 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957706 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | JUMPER | OJS 2 SPANS SS OF CGC 223437738743 | 20240718 | 1544 | 20240718 | 1815 | 2520384 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1208 | 38.724 | -120.7969 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0089457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957730 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 51582 | 20240719 | 542 | 20240719 | 856 | 2520744 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 289 | 47174 | 39.2062 | -121.2633 | No | Clear;32-90 F |  |  | 24-0089565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957795 | 0 | EPSS Ckt | Y | 2024 | A+INST OC
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 5669 | 20240719 | 630 | 20240719 | 818 | 2520773 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1944 | 38.9143 | -121.0837 | No | Clear;32-90 F | Jumper | Burned Open | 24-0089623 | OH | Sus | 46282183 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1957852 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 223000851923 | 20240719 | 745 | 20240719 | 841 | 2520801 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 56 | 39.0877 | -120.9438 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0089602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957812 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | OCB | 1109/2 | 20240719 | 811 | 20240719 | 827 | 2520841 | 16 | Distribution Circuit | Animal | Other | 937 | 14992 | 38.947 | -121.0911 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0089615 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957841 | 0 | EPSS Ckt | Y | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 501650 | 20240719 | 827 | 20240719 | 1012 | 2520856 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 4305 | 38.692 | -120.7038 | No | Clear;32-90 F |  |  | 24-0089627 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957855 | 0 | EPSS Ckt | Y | 2024 | A C INSTA OC
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240719 | 1329 | 20240719 | 1418 | 2521174 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 173 | 8477 | 39.1986 | -121.0343 | No | Clear;Above 90 |  |  | 24-0089791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1957974 | 0 | EPSS Ckt | Y | 2024 | C
SIERRA | PLACER | WISE-1102 | 152271102 | SWITCH | 173855 | 20240719 | 1703 | 20240719 | 2247 | 2521329 | 344 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 166 | 57104 | 38.8833 | -121.1518 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0089890 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957994 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6119 | 20240719 | 1743 | 20240719 | 2056 | 2521350 | 193 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 240 | 46320 | 39.0426 | -120.9732 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0089899 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1957998 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2740 | 20240719 | 1744 | 20240719 | 1900 | s1981346 | 76 | Distribution Circuit | Company Initiated | Coordination failure | 210 | 15960 | 39.0342 | -120.9744 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0089899 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1981346 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 51676 | 20240719 | 1750 | 20240720 | 114 | 2521355 | 444 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1061 | 1693 | 38.8519 | -121.1638 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0089900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 85736 | No | No | No | 1957999 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20240720 | 804 | 20240720 | 1032 | 2521613 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 208 | 30784 | 39.274 | -120.9698 | No | Clear;32-90 F |  |  | 24-0089984 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958076 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20240720 | 806 | 20240720 | 835 | 2521611 | 29 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1239 | 35931 | 39.2408 | -121.0301 | No | Clear;32-90 F |  |  | 24-0089986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958079 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 3261 | 20240720 | 807 | 20240720 | 1128 | 2521609 | 201 | Distribution Circuit | Animal | Squirrel | 2 | 402 | 39.2221 | -121.0568 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0090021 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958110 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 11321 | 20240720 | 949 | 20240720 | 1446 | 2521685 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3267 | 38.7054 | -120.7628 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0090033 | OH | Sus | 46282483 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958121 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 774186 | 20240720 | 1511 | 20240720 | 2324 | 2521876 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 1240 | 85984 | 38.7259 | -120.7943 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0090057 | OH | Sus | 46282366 | NORTH VALLEY AND SIERRA | JUL | Multi-Fault | 0 | No | Yes | No | 1958131 | 0 | EPSS Ckt | N | 2024 | ABC GRD TIME OC INSTA OC
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 37579 | 20240720 | 1747 | 20240721 | 314 | 2521998 | 567 | Distribution Circuit | Animal | Bird found | 14 | 2413 | 38.8244 | -121.4606 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090089 | OH | Sus | 31701550 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958165 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20240720 | 1828 | 20240720 | 2019 | 2522038 | 111 | Distribution Circuit | Animal | Bird found | 1878 | 131108 | 39.0997 | -121.05 | No | Clear;Above 90 | Insulator | Normal | 24-0090080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958157 | 0 | EPSS Ckt | Y | 2024 | A C INSTA OC
SIERRA | PLACER | PLACER-1102 | 152461102 | TRANSFORMER | 222583744937 | 20240720 | 1830 | 20240721 | 553 | 2522036 | 683 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 683 | 38.8968 | -121.0929 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0090111 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958189 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222636356741 | 20240720 | 2222 | 20240721 | 553 | 2522180 | 451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 8923 | 39.2209 | -121.0705 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090120 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958195 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20240721 | 613 | 20240721 | 1321 | 2522266 | 428 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 445976 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0090132 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958207 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20240721 | 1345 | 20240721 | 1445 | 2522478 | 60 | Distribution Circuit | Animal | Bird found | 524 | 31440 | 39.2191 | -121.0228 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0090184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958251 | 0 | EPSS Ckt | Y | 2024 | GRD INST OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 37071 | 20240721 | 1917 | 20240721 | 2101 | 2522632 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 4056 | 38.7934 | -121.0413 | No | Clear;Above 90 |  |  | 24-0090227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958288 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223177141427 | 20240722 | 552 | 20240722 | 840 | 2522764 | 168 | Transformer only | Animal | Squirrel | 2 | 336 | 38.7986 | -120.8862 | No | Clear;32-90 F | Fuse | Burned Open | 24-0090312 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958400 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221696144889 | 20240722 | 856 | 20240722 | 954 | 2522965 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 58 | 38.8977 | -121.4053 | No | Clear;32-90 F | Fuse | Burned Open | 24-0090355 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958464 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | TRANSFORMER | T6431 | 20240722 | 1021 | 20240722 | 1121 | 2522992 | 60 | Transformer only | Equipment Failure/Involved | Underground | 15 | 900 | 38.8014 | -121.2887 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0090425 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958487 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31105 | 20240722 | 1437 | 20240722 | 1818 | 2523413 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1326 | 38.884 | -120.8622 | No | Clear;Above 90 | Insulator | Broken | 24-0090532 | OH | Sus | 46283045 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958518 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 595280 | 20240722 | 1631 | 20240723 | 404 | 2523535 | 693 | Distribution Circuit | Animal | Bird found | 114 | 18410 | 39.073 | -121.1141 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958532 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 92474 | 20240722 | 1838 | 20240722 | 1845 | 2523631 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 493 | 3451 | 38.8958 | -120.879 | No | Clear;Above 90 | Crossarm- Wood | Deteriorated | 24-0090532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958540 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240722 | 2231 | 20240723 | 1338 | 2523730 | 829 | Distribution Circuit | 3rd Party | Vehicle | 173 | 31928 | 39.1986 | -121.0343 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Three Phase Fault | 0 | No | No | No | 1958580 | 0 | EPSS Ckt | Y | 2024 | A+B+C TRIP TARGETS
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222776552564 | 20240723 | 804 | 20240723 | 1750 | 2523969 | 586 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1172 | 39.1059 | -121.0231 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958832 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222694554095 | 20240723 | 934 | 20240723 | 1128 | 2523955 | 114 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 456 | 39.148 | -121.0508 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0090770 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958637 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | TRANSFORMER | 222283339866 | 20240723 | 1009 | 20240723 | 1039 | 2524242 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 30 | 38.7584 | -121.2007 | No | Clear;Above 90 | Secondary | Broken | 24-0090857 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958781 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | OCB | 2109/2 | 20240723 | 1939 | 20240723 | 2214 | 2524811 | 155 | Distribution Circuit | Company Initiated | Coordination failure | 3042 | 471510 | 38.6555 | -121.0603 | No | Clear;Above 90 | Circuit Breaker | Normal | 24-0091157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958878 | 0 | EPSS Ckt | Y | 2024 | C- GRD- SET A RLY- INSTA OC
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | RECLOSER | 19692 | 20240723 | 1941 | 20240724 | 105 | 2524877 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3077 | 996948 | 38.6772 | -121.0813 | No | Clear;Above 90 | Jumper | Broken | 24-0091163 | OH | Sus | 46283652 | NORTH VALLEY AND SIERRA | JUL | Open Circuit | 0 | No | No | No | 1958881 | 1 | EPSS Ckt | N | 2024 | B C
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20240723 | 1945 | 20240723 | 2108 | 2524899 | 83 | Distribution Circuit | Animal | Bird found | 377 | 31291 | 38.8101 | -121.1629 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0091160 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958879 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1820 | 20240723 | 1958 | 20240724 | 111 | 2524920 | 313 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 150 | 27945 | 39.0336 | -120.7967 | No | Clear;32-90 F |  |  | 24-0091165 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958882 | 0 | EPSS Ckt | Y | 2024 | A C INSTA OC
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 6749 | 20240723 | 2031 | 20240724 | 14 | 2524955 | 223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1561 | 39.2463 | -121.0397 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0091193 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958899 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 722212 | 20240723 | 2034 | 20240723 | 2350 | 2524958 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 25872 | 39.2623 | -121.0728 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0091181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958891 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20240723 | 2109 | 20240724 | 1 | 2524990 | 172 | Distribution Circuit | Vegetation | Tree - branch fell on line | 519 | 89268 | 39.153 | -121.0774 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0091196 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958902 | 0 | EPSS Ckt | Y | 2024 | C
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 3553 | 20240723 | 2111 | 20240724 | 341 | 2524979 | 390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 851 | 27037 | 39.1749 | -121.0946 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0091223 | OH | Sus | 31702025 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958932 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | JUMPER | OJS 2 SS OF CGC#222243844778 | 20240723 | 2115 | 20240724 | 202 | 2525012 | 287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 861 | 38.8936 | -121.2111 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0091229 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958940 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | TRANSFORMER | T0810 | 20240723 | 2120 | 20240723 | 2329 | 2525000 | 129 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 516 | 38.7481 | -121.3548 | No | Clear;Above 90 |  |  | 24-0091220 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1958926 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJS 1 SS OF CGC#222933058306 | 20240724 | 133 | 20240724 | 406 | 2525100 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 306 | 39.2623 | -120.9644 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0091228 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1958938 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240724 | 559 | 20240724 | 705 | 2525204 | 66 | Distribution Circuit | Company Initiated | Personnel- company | 173 | 11418 | 39.1986 | -121.0343 | No | Clear;32-90 F | Recloser | Normal | 24-0091243 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958953 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | 222685457592 | 20240724 | 815 | 20240724 | 1055 | 2525306 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 640 | 39.244 | -121.0529 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0091313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959008 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222436354788 | 20240724 | 815 | 20240724 | 910 | 2525325 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 39.168 | -121.1421 | No | Clear-Heat Wave;32-90 F | Cutout- fuse holder | Failed/Faulted | 24-0091317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959020 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 2406 | 20240724 | 915 | 20240724 | 1103 | 2525441 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 884 | 67823 | 38.8518 | -121.1656 | No | Clear-Heat Wave;32-90 F |  |  | 24-0091362 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1959107 | 0 | EPSS Ckt | Y | 2024 | A-C- INST OC
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | T244 | 20240724 | 936 | 20240724 | 1230 | 2525493 | 174 | Transformer only | Company Initiated | Personnel- company | 2 | 348 | 39.1873 | -120.8335 | No | Heat Wave-Clear;Above 90 | Transformer | Malfunctioning | 24-0091425 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959149 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240724 | 942 | 20240724 | 1057 | 2525517 | 75 | Distribution Circuit | Company Initiated | Personnel- company | 173 | 12975 | 39.1986 | -121.0343 | No | Clear-Heat Wave;32-90 F | Recloser | Normal | 24-0091372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Three Phase Fault | 0 | No | No | No | 1959120 | 0 | EPSS Ckt | Y | 2024 | A-B-C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222437054975 | 20240724 | 943 | 20240724 | 1010 | 2525477 | 27 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 54 | 39.173 | -121.1419 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Normal | 24-0091363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959108 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S @ MTR# 1010656108 | 20240724 | 944 | 20240724 | 1306 | 2525412 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 606 | 38.8471 | -120.7877 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0091350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959080 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20240724 | 1040 | 20240724 | 1214 | 2525421 | 94 | Distribution Circuit | Animal | Bird found | 524 | 4992 | 39.2191 | -121.0228 | No | Clear-Heat Wave;32-90 F | Cutout- fuse holder | Broken | 24-0091352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959083 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | SWITCH | 8843 | 20240724 | 1242 | 20240724 | 1411 | 2525761 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 9078 | 39.2028 | -120.7963 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Broken | 24-0091482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959167 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 285704 | 20240724 | 1436 | 20240724 | 1513 | 2525879 | 37 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 2220 | 39.2409 | -121.0385 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Together | 24-0091581 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959192 | 0 | EPSS Ckt | Y | 2024 | A GRD INST OC
SIERRA | PLACER | LINCOLN-1101 | 153701101 | JUMPER | OJ'S 1 SPAN SS OF CGC 222283544985 | 20240724 | 1644 | 20240724 | 1738 | 2525984 | 54 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 216 | 38.8994 | -121.198 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Broken | 24-0091642 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959208 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222376743684 | 20240724 | 1721 | 20240725 | 611 | 2526019 | 770 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 3080 | 38.8634 | -121.1659 | No | Heat Wave-Clear;Above 90 | Transformer | Broken- wire on ground | 24-0091686 | OH | Sus | 31702030 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | Yes | No | 1959225 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6361 | 20240725 | 907 | 20240725 | 1004 | 2526477 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 342 | 39.1567 | -120.8896 | No | Clear;32-90 F | Other | Broken | 24-0091820 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959404 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222971053950 | 20240725 | 934 | 20240725 | 1044 | 2526507 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 70 | 39.1436 | -120.9537 | No | Clear;32-90 F | Secondary | Broken | 24-0091829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959425 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | JUMPER | CHANCE CLAMPS TWD CGC 221619439953 | 20240725 | 937 | 20240725 | 1350 | 2526530 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 506 | 38.7626 | -121.4328 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0091842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959434 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 7401 | 20240725 | 1104 | 20240725 | 1303 | 2526639 | 119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 714 | 39.3633 | -121.076 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0091906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959478 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 657600 | 20240725 | 1310 | 20240725 | 1353 | 2526738 | 43 | Distribution Circuit | Company Initiated | Personnel- company | 173 | 7439 | 39.1986 | -121.0343 | No | Clear;Above 90 | Recloser | Normal | 24-0092002 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1959513 | 0 | EPSS Ckt | Y | 2024 | A-C
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9523 | 20240725 | 1340 | 20240725 | 1432 | 2526762 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 104 | 38.8788 | -121.4144 | No | Clear;Above 90 |  |  | 24-0092070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1959527 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 847967 | 20240725 | 1440 | 20240725 | 1509 | 2526803 | 29 | Distribution Circuit | Vegetation | Tree - grew into line | 69 | 2001 | 38.7519 | -121.2173 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959529 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9875 | 20240725 | 1725 | 20240726 | 141 | 2526924 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 100688 | 39.2631 | -120.91 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0092170 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959549 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2751 | 20240725 | 2014 | 20240725 | 2237 | 2527014 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 9724 | 39.2809 | -120.9453 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0091900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1959571 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223177141427 | 20240726 | 623 | 20240726 | 802 | 2527170 | 99 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 198 | 38.7986 | -120.8862 | No | Clear;32-90 F |  |  | 24-0092281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1959653 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222615352483 | 20240726 | 804 | 20240726 | 1434 | 2528898 | 390 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 780 | 39.1038 | -121.0796 | No | Clear;32-90 F |  |  | 24-0092985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1960183 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240726 | 856 | 20240726 | 933 | 2527335 | 37 | Distribution Circuit | Company Initiated | Personnel- company | 2594 | 95978 | 38.6943 | -120.6784 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092324 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959715 | 0 | EPSS Ckt | Y | 2024 | SGF -DCD
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 99658 | 20240726 | 1046 | 20240726 | 1109 | 2527497 | 23 | Distribution Circuit | Animal | Other | 946 | 21758 | 38.6947 | -120.8146 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0092399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959768 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20240726 | 1300 | 20240726 | 1344 | 2527618 | 44 | Distribution Circuit | Company Initiated | Personnel- company | 873 | 38412 | 38.8963 | -121.1379 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959799 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 52195 | 20240726 | 1343 | 20240726 | 1503 | 2527659 | 80 | Distribution Circuit | Vegetation | Tree - fell into line | 684 | 54720 | 38.6012 | -120.7195 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959809 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3099 | 20240726 | 1439 | 20240726 | 1721 | 2527707 | 162 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1458 | 39.134 | -120.9401 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0092618 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1959839 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20240726 | 1719 | 20240726 | 2100 | 2527837 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 238 | 46943 | 38.9847 | -121.366 | No | Clear;Above 90 |  |  | 24-0092617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959838 | 0 | EPSS Ckt | Y | 2024 | B & GRD
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222620356407 | 20240727 | 1413 | 20240727 | 2037 | 2528361 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 3072 | 39.2118 | -121.0763 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0092782 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960004 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ'S 1 SS OF 222928454348 | 20240727 | 1427 | 20240727 | 1958 | 2528337 | 331 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 331 | 39.1542 | -120.9685 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092772 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959998 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 31377 | 20240727 | 1945 | 20240727 | 2127 | 2528468 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 3876 | 39.0323 | -121.0725 | No | Clear;32-90 F |  |  | 24-0092810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1960027 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39051 | 20240728 | 1430 | 20240728 | 1526 | 2528722 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 68 | 3808 | 39.0263 | -121.0589 | No | Clear;32-90 F |  |  | 24-0092899 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1960106 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 1117 | 20240729 | 849 | 20240729 | 1218 | 2529030 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 10241 | 38.8983 | -120.8572 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0092312 | OH | Sus | 35568565 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960267 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | FUSE | 19349 | 20240729 | 909 | 20240729 | 1127 | 2529063 | 138 | Distribution Circuit | Equipment Failure/Involved | Underground | 6 | 828 | 38.6809 | -121.0468 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0093053 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960284 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20240729 | 1149 | 20240729 | 1343 | 2529265 | 114 | Distribution Circuit | 3rd Party | Vehicle | 292 | 33288 | 39.0317 | -121.0046 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1960350 | 0 | EPSS Ckt | Y | 2024 | C GRD INST OC
SIERRA | PLACER | BELL-1107 | 152701107 | OCB | 1107/2 | 20240729 | 1646 | 20240729 | 1841 | 2529688 | 115 | Distribution Circuit | Animal | Squirrel | 35 | 4025 | 38.947 | -121.0912 | No | Clear;32-90 F | Pothead(Riser Termination) | Failed/Faulted | 24-0093397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Three Phase Fault | 0 | No | No | No | 1960402 | 0 | EPSS Ckt | N | 2024 | A B C GRD TIME OC
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20240729 | 1646 | 20240729 | 1800 | 2529677 | 74 | Distribution Circuit | Company Initiated | Coordination failure | 522 | 38628 | 38.9452 | -121.1218 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1960403 | 0 | EPSS Ckt | Y | 2024 | B INST OC
SIERRA | PLACER | WEIMAR-1102 | 152491102 | FUSE | 6101 | 20240730 | 741 | 20240730 | 1035 | 2529995 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 26448 | 39.044 | -120.997 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0093583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1960617 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 158335 | 20240730 | 837 | 20240730 | 1310 | 2530063 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 5187 | 39.0423 | -121.0838 | No | Clear;32-90 F | Insulator | Broken | 24-0093549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960551 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 41319 | 20240730 | 1134 | 20240730 | 1400 | 2530313 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 438 | 38.7292 | -120.7588 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0093688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960683 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 3553 | 20240730 | 1445 | 20240731 | 148 | 2530440 | 663 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 4723 | 39.1749 | -121.0946 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0093810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1960724 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224849540787 | 20240730 | 1728 | 20240731 | 446 | 2530571 | 678 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 678 | 38.7739 | -120.3007 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0093969 | OH | Sus | 35569813 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1960791 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 1398 | 20240731 | 641 | 20240731 | 847 | 2530807 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 5834 | 38.905 | -121.2795 | No | Clear;32-90 F |  |  | 24-0094007 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1960827 | 0 | EPSS Ckt | Y | 2024 | B+C
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 31247 | 20240731 | 917 | 20240801 | 19 | 2531055 | 902 | Distribution Circuit | Animal | Squirrel | 8 | 2464 | 39.1762 | -120.9977 | No | Partly Cloudy;32-90 F | Cutout- fuse holder | Burned/flashed | 24-0094129 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1961007 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221618044064 | 20240731 | 1010 | 20240731 | 1135 | 2531130 | 85 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 85 | 38.8749 | -121.4328 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0094199 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1961025 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20240731 | 1742 | 20240731 | 1802 | 2531513 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 522 | 10440 | 38.9452 | -121.1218 | No | Clear;Above 90 | Recloser | Normal | 24-0094444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1961100 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 6687 | 20240801 | 104 | 20240801 | 218 | 2531612 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 1406 | 39.2126 | -120.9878 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0094491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961135 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 39051 | 20240801 | 848 | 20240801 | 1143 | 2531757 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 11900 | 39.0263 | -121.0589 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0094562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961194 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20240801 | 946 | 20240801 | 1143 | 2531877 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 6552 | 38.9463 | -121.2467 | No | Partly Cloudy;32-90 F |  |  | 24-0094608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961264 | 0 | EPSS Ckt | Y | 2024 | a-b
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 2493 | 20240801 | 1256 | 20240801 | 1402 | 2532033 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 8052 | 38.7729 | -120.3034 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0094610 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961315 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 50047 | 20240802 | 703 | 20240802 | 912 | 2532662 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 517 | 28453 | 39.0352 | -121.0957 | No | Partly Cloudy;32-90 F |  |  | 24-0094977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961457 | 0 | EPSS Ckt | Y | 2024 | BC INST OC
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | OTHER | J804 TWD T8190 | 20240802 | 1029 | 20240802 | 1513 | 2532966 | 284 | Distribution Circuit | 3rd Party | Vehicle | 1 | 284 | 38.8128 | -121.2596 | No | Partly Cloudy;32-90 F | Transformer (UG) | Normal | 24-0095092 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961583 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15317 | 20240802 | 1145 | 20240802 | 1345 | 2533017 | 120 | Distribution Circuit | Animal | Bird found | 2 | 240 | 38.9979 | -121.3167 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1961614 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2469 | 20240802 | 1307 | 20240802 | 1355 | 2533057 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 48 | 38.7733 | -120.4844 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 24-0095155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961598 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222940739622 | 20240803 | 123 | 20240803 | 930 | 2533422 | 487 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 974 | 38.7496 | -120.9695 | No | Overcast;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0095351 | OH | Sus | 35570358 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1961694 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 5069 | 20240803 | 1126 | 20240803 | 1315 | 2533621 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 4687 | 38.8171 | -121.164 | No | Clear;Above 90 |  |  | 24-0095423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961750 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 498932 | 20240803 | 1211 | 20240803 | 1327 | 2533643 | 76 | Distribution Circuit | 3rd Party | Vehicle | 155 | 11780 | 39.1181 | -121.0392 | No | Partly Cloudy;32-90 F | Anchor or Guy | Broken | 24-0095417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961745 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 2102 | 20240803 | 1655 | 20240803 | 1741 | 2533826 | 46 | Distribution Circuit | Vegetation | Tree - fell into line | 1082 | 49772 | 38.6825 | -120.8522 | No | Clear;Above 90 | Conductor- Overhead | Together | 24-0095444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961764 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2234 | 20240803 | 2056 | 20240803 | 2259 | 2533923 | 123 | Distribution Circuit | Animal | Bird found | 272 | 33456 | 38.8956 | -121.1358 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961776 | 0 | EPSS Ckt | Y | 2024 | B C INST OC
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20240804 | 825 | 20240804 | 913 | 2534114 | 48 | Distribution Circuit | Animal | Bird found | 517 | 24816 | 39.0351 | -121.0957 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1961849 | 0 | EPSS Ckt | Y | 2024 | A B TIME OC
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 50550 | 20240804 | 1101 | 20240804 | 1222 | 2534145 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 270 | 21060 | 38.8511 | -121.1794 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095540 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961860 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222882038976 | 20240804 | 1656 | 20240804 | 1745 | 2534294 | 49 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 49 | 38.7311 | -120.9868 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0095567 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1961877 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 20240805 | 922 | 20240805 | 1024 | 2534801 | 62 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 1612 | 39.4382 | -120.9965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095747 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962047 | 0 | EPSS Ckt | Y | 2024 | NA
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 5335 | 20240805 | 1030 | 20240805 | 1302 | 2534868 | 152 | Distribution Circuit | Animal | Bird found | 616 | 53184 | 38.9124 | -121.1982 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095810 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962069 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 9625 | 20240805 | 1320 | 20240805 | 1750 | 2535064 | 270 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 11316 | 38.7682 | -121.2038 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0096024 | OH | Sus | 31703450 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1962135 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 458102 | 20240805 | 1724 | 20240806 | 439 | 2535260 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 64728 | 39.1494 | -121.0345 | No | Clear;Above 90 | Crossarm- Wood | Broken- wire on ground | 24-0096078 | OH | Sus | 31703429 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1962151 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222591752772 | 20240805 | 2230 | 20240806 | 926 | 2535401 | 656 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 656 | 39.112 | -121.0875 | No | Clear;32-90 F | Secondary | Broken | 24-0096215 | OH | Sus | 31703430 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962286 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 2100 | 20240806 | 304 | 20240806 | 719 | 2535477 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1192 | 161069 | 38.6928 | -120.7666 | No | Clear;32-90 F | Insulator | Broken | 24-0096149 | OH | Sus | 46289358 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1962215 | 0 | EPSS Ckt | Y | 2024 | A B INST OC
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 20240806 | 957 | 20240806 | 1311 | 2535736 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1076 | 208744 | 39.4655 | -120.8444 | No | Clear;32-90 F |  |  | 24-0096267 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962365 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 9519 | 20240806 | 1156 | 20240806 | 1305 | 2535842 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 506 | 38.8881 | -121.4144 | No | Clear;32-90 F |  |  | 24-0096403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962439 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 164936 | 20240806 | 1839 | 20240806 | 2005 | 2536159 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1376 | 38.9271 | -121.2141 | No | Clear;Above 90 | Insulator | Broken | 24-0096544 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962490 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2108 | 152442108 | SWITCH | 51169 | 20240806 | 1850 | 20240807 | 408 | 2536186 | 558 | Distribution Circuit | 3rd Party | Vehicle | 945 | 250240 | 38.835 | -121.2891 | No | Clear;Above 90 | Switch (UG) | Broken | 24-0096550 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962497 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 88079 | 20240807 | 34 | 20240807 | 202 | 2536316 | 88 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 264 | 38.9115 | -121.1635 | No | Clear;32-90 F |  |  | 24-0096590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1962540 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20240807 | 1415 | 20240808 | 344 | 2536852 | 809 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 845 | 86944 | 38.6858 | -121.0119 | No | Clear;Above 90 | Switch (OH) | Burned/flashed | 24-0096867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962755 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20240807 | 1424 | 20240807 | 1606 | 2536868 | 102 | Distribution Circuit | Vegetation | Tree - fell into line | 1421 | 65760 | 39.1048 | -121.0852 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0096873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962759 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | SWITCH | 1521 | 20240807 | 1623 | 20240807 | 1630 | 2536987 | 7 | Distribution Circuit | Company Initiated | Return Circuit Normal | 195 | 1365 | 39.1571 | -121.0626 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0096873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962779 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | SWITCH | 6305 | 20240807 | 1725 | 20240807 | 2018 | 2537026 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3633 | 39.0899 | -120.98 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0096951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962787 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 32945 | 20240807 | 1937 | 20240808 | 603 | 2537108 | 626 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 2504 | 39.2587 | -121.2119 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 24-0096983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962797 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | SWITCH | 30211BP | 20240807 | 2101 | 20240808 | 531 | 2537159 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 32286 | 38.7469 | -121.2262 | No | Clear;32-90 F | Switch (OH) | Broken | 24-0096316 | OH | Sus | 46289680 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962811 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | RECLOSER | 1070 | 20240808 | 250 | 20240808 | 1155 | 2537274 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 36560 | 39.0212 | -121.0599 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0097047 | OH | Sus | 46292033 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1962842 | 0 | EPSS Ckt | Y | 2024 | A GRD INST OC
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20240808 | 541 | 20240808 | 1238 | 2537308 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 520 | 106945 | 39.153 | -121.0774 | No | Clear;32-90 F | Other | Broken | 24-0097055 | OH | Sus | 46292256 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1962854 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2704 | 20240808 | 748 | 20240808 | 919 | 2537382 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 176 | 10544 | 38.8107 | -121.1649 | No | Clear;32-90 F |  |  | 24-0097102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1962874 | 0 | EPSS Ckt | Y | 2024 | BC
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 817491 | 20240808 | 1025 | 20240808 | 1111 | 2537622 | 46 | Distribution Circuit | Company Initiated | Personnel- company | 31 | 1426 | 38.854 | -121.2101 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963009 | 0 | EPSS Ckt | Y | 2024 | AC
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222995052047 | 20240808 | 1200 | 20240808 | 1458 | 2537804 | 178 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 712 | 39.091 | -120.9461 | No | Clear;Above 90 | Conductor- Overhead | Broken | 24-0097354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963054 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223446037592 | 20240808 | 1311 | 20240808 | 1658 | 2537836 | 227 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 454 | 38.6928 | -120.7938 | No | Clear;Above 90 | Service conductor | Broken | 24-0097297 | OH | Sus | 31703398 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963035 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20240808 | 1407 | 20240808 | 1938 | 2537945 | 331 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1019 | 85365 | 38.8932 | -120.9965 | No | Clear;Above 90 |  |  | 24-0097334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963044 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | TRANSFORMER | 221618044064 | 20240808 | 1611 | 20240808 | 1943 | 2538132 | 212 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 212 | 38.8749 | -121.4328 | No | Clear;Above 90 |  |  | 24-0097462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1963095 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | OTHER | WIRE DOWN 2 N/OF 187731 | 20240808 | 1648 | 20240808 | 2346 | 2538162 | 418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 75179 | 38.7033 | -121.023 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0096867 | OH | Sus | 31704003 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | Yes | 1963071 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 38885 | 20240808 | 2111 | 20240809 | 18 | 2538345 | 187 | Distribution Circuit | Vegetation | Tree - grew into line | 17 | 3179 | 38.8234 | -121.116 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963109 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 7583 | 20240808 | 2243 | 20240809 | 529 | 2538375 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3248 | 39.0876 | -121.0462 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0097482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1963133 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2108 | 152442108 | SWITCH | 51169 | 20240809 | 1158 | 20240809 | 1240 | s1963307 | 42 | Distribution Circuit | Equipment Failure/Involved | Underground | 407 | 17094 | 38.835 | -121.2891 | No | Clear;32-90 F | Interrupter | Malfunctioning | 24-0097600 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963307 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223877039700 | 20240809 | 1304 | 20240809 | 2037 | 2538805 | 453 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 906 | 38.7483 | -120.6409 | No | Clear;Above 90 |  |  | 24-0097825 | OH | Sus | 31704113 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1963331 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20240809 | 2303 | 20240810 | 42 | 2539105 | 99 | Distribution Circuit | Animal | Bird found | 220 | 21780 | 38.8964 | -121.1202 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0097929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963381 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 31295 | 20240810 | 709 | 20240810 | 1458 | 2539192 | 469 | Distribution Circuit | Animal | Squirrel | 4 | 730 | 39.069 | -121.0887 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0097960 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963415 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 51582 | 20240810 | 928 | 20240810 | 1202 | 2539261 | 154 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 289 | 35146 | 39.2062 | -121.2633 | No | Clear;32-90 F |  |  | 24-0097970 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963428 | 0 | EPSS Ckt | Y | 2024 | A-C- INST OC
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | RECLOSER | 63100 | 20240810 | 1207 | 20240810 | 1403 | 2539381 | 116 | Distribution Circuit | Vegetation | Tree - fell into line | 210 | 14410 | 39.2282 | -121.1005 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0097993 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963448 | 0 | EPSS Ckt | Y | 2024 | A-C
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 20240810 | 2025 | 20240810 | 2212 | 2539607 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 9309 | 39.3405 | -121.1318 | No | Clear;32-90 F |  |  | 24-0098034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1963493 | 0 | EPSS Ckt | Y | 2024 | A-C- INST OC
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2416 | 20240811 | 347 | 20240811 | 1549 | 2539673 | 722 | Distribution Circuit | 3rd Party | Vehicle | 980 | 313912 | 39.1593 | -121.0399 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0098050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963512 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 8605 | 20240811 | 533 | 20240811 | 738 | 2539683 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2500 | 38.8676 | -121.4787 | No | Clear;32-90 F |  |  | 24-0098057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963522 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 30703 | 20240811 | 806 | 20240811 | 858 | 2539738 | 52 | Distribution Circuit | Animal | Bird found | 8 | 416 | 38.7994 | -121.2288 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0098064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963535 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | FUSE | 40691 | 20240811 | 923 | 20240811 | 1053 | 2539737 | 90 | Distribution Circuit | Animal | Bird found | 7 | 630 | 38.9967 | -121.1018 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0098070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1963543 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15317 | 20240811 | 1322 | 20240811 | 1506 | 2539797 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 239 | 38.9979 | -121.3167 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0098086 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963556 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ'S @ CGC 223061458466 | 20240812 | 1642 | 20240813 | 312 | 2540591 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1890 | 39.2664 | -120.9199 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0098507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963816 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 164068 | 20240812 | 1921 | 20240812 | 2028 | 2540679 | 67 | Distribution Circuit | Animal | Bird found | 975 | 65325 | 38.9466 | -121.0478 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0098552 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1963831 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 31923 | 20240812 | 2208 | 20240813 | 9 | 2540816 | 121 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 3267 | 39.622 | -120.6131 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0098574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963855 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 67415 | 20240812 | 2219 | 20240813 | 45 | 2540821 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2190 | 38.883 | -120.8795 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0098576 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963857 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223325344657 | 20240813 | 918 | 20240813 | 1127 | 2541104 | 129 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 129 | 38.8867 | -120.8332 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0098816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964069 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | JUMPER | 2P W/ OF CGC 222730555470 | 20240813 | 1010 | 20240813 | 1333 | 2541161 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 406 | 39.185 | -121.0385 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0098735 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964051 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 35823 | 20240814 | 1050 | 20240814 | 1421 | 2542049 | 211 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 844 | 38.8389 | -121.3297 | No | Clear;32-90 F | Insulator | Broken | 24-0099298 | OH | Sus | 46299184 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1964386 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32201 | 20240814 | 1609 | 20240814 | 1718 | 2542298 | 69 | Distribution Circuit | Animal | Bird found | 32 | 2229 | 38.7914 | -121.2549 | No | Clear;Above 90 | Pole-Wood | Normal | 24-0099470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964434 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 406999 | 20240814 | 1751 | 20240814 | 1841 | 2542366 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 3835 | 39.0016 | -120.9074 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0099500 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1964445 | 1 | EPSS Ckt | Y | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | RECLOSER | 2106 | 20240814 | 1829 | 20240814 | 1841 | s1973884 | 12 | Distribution Circuit | Company Initiated | Personnel- company | 313 | 3756 | 39.0198 | -120.8509 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0099500 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1973884 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | RECLOSER | 1402 | 20240815 | 654 | 20240815 | 818 | 2542715 | 84 | Distribution Circuit | Animal | Squirrel | 956 | 80304 | 38.7201 | -120.861 | No | Clear;32-90 F | Pothead(Riser Termination) | Normal | 24-0099555 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964490 | 0 | EPSS Ckt | Y | 2024 | C & GRD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222854350287 | 20240815 | 933 | 20240815 | 1126 | 2542833 | 113 | Transformer only | Company Initiated | Personnel- company | 4 | 452 | 39.043 | -120.9963 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0099675 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1964553 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20240815 | 948 | 20240815 | 1244 | 2542855 | 176 | Distribution Circuit | Animal | Bird found | 871 | 58575 | 39.1911 | -120.9965 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0099618 | OH | Sus | 31705287 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964542 | 0 | EPSS Ckt | Y | 2024 | A & GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20240815 | 2013 | 20240816 | 524 | 2543279 | 551 | Distribution Circuit | 3rd Party | Vehicle | 1421 | 62383 | 39.1048 | -121.0852 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0099840 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1964602 | 0 | EPSS Ckt | Y | 2024 | A / C
SIERRA | PLACER | BELL-1109 | 152701109 | TRANSFORMER | 222660547205 | 20240815 | 2025 | 20240816 | 636 | 2543288 | 611 | Transformer only | 3rd Party | Vehicle | 9 | 5499 | 38.9589 | -121.0655 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0099845 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964608 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 31493 | 20240815 | 2052 | 20240815 | 2315 | 2543300 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1430 | 39.013 | -121.1035 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0099843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964605 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 891 | 20240815 | 2100 | 20240816 | 126 | 2543312 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1064 | 39.553 | -120.859 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099818 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Three Phase Fault | 0 | No | No | No | 1964609 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | JUMPER | 223674038125 | 20240815 | 2110 | 20240815 | 2257 | 2543305 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 315 | 38.7065 | -120.7139 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0099844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964607 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | OTHER | T7343 TWD J795 | 20240815 | 2230 | 20240816 | 202 | 2543334 | 212 | Distribution Circuit | 3rd Party | Vehicle | 73 | 15092 | 38.677 | -121.0143 | No | Clear;32-90 F | Switch (UG) | Broken | 24-0099850 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964625 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 40783 | 20240815 | 2348 | 20240816 | 820 | 2543343 | 512 | Distribution Circuit | Animal | Bird found | 38 | 19456 | 38.7667 | -121.1775 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0099903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1964680 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 940676 | 20240816 | 629 | 20240816 | 1146 | 2543402 | 317 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 233 | 73861 | 38.7476 | -120.8598 | No | Clear;32-90 F |  |  | 24-0099866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1964643 | 0 | EPSS Ckt | Y | 2024 | A+C
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20240816 | 801 | 20240816 | 1001 | 2543474 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 3360 | 38.7533 | -120.6117 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0099906 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964690 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222357056402 | 20240816 | 806 | 20240816 | 1310 | 2543461 | 304 | Transformer only | Animal | Squirrel | 2 | 608 | 39.2126 | -121.1689 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0099928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964753 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20240816 | 1525 | 20240817 | 1445 | 2543892 | 1400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 200 | 41630 | 39.6081 | -120.6068 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964855 | 0 | EPSS Ckt | Y | 2024 | A / GRD
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | TRANSFORMER | T1696 | 20240816 | 1612 | 20240816 | 1924 | 2543929 | 192 | Transformer only | 3rd Party | Fire- house or bldg. | 3 | 576 | 39.2389 | -121.0359 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0100158 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1964861 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20240817 | 936 | 20240817 | 1205 | 2544237 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 676 | 100724 | 39.2129 | -121.0129 | No | Clear;32-90 F |  |  | 24-0100241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1964954 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20240818 | 219 | 20240818 | 652 | 2544650 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 120955 | 39.0443 | -120.9859 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0100345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1965038 | 0 | EPSS Ckt | Y | 2024 | A C INST OC
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 2718 | 20240818 | 820 | 20240818 | 925 | 2544706 | 65 | Distribution Circuit | Animal | Bird found | 1170 | 76050 | 39.2349 | -121.2209 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0100358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1965059 | 0 | EPSS Ckt | Y | 2024 | A C IOC
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 5107 | 20240818 | 844 | 20240818 | 953 | 2544713 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2415 | 38.7517 | -121.3439 | No | Clear;32-90 F |  |  | 24-0100372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1965072 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1101 | 152271101 | SWITCH | 35589 | 20240818 | 905 | 20240818 | 1158 | 2544719 | 173 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 173 | 38.877 | -121.1202 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0100363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965063 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 30617 | 20240818 | 2011 | 20240819 | 57 | 2544892 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 4862 | 38.9632 | -121.1496 | No | Clear;32-90 F | Woodpin | Broken | 24-0100432 | OH | Sus | 46300911 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965122 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20240819 | 846 | 20240819 | 1129 | 2545200 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 873 | 67203 | 38.8963 | -121.1379 | No | Clear;32-90 F |  |  | 24-0100498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1965211 | 0 | EPSS Ckt | Y | 2024 | A-C SGF
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | SWITCH | 1715 | 20240819 | 1048 | 20240819 | 1229 | 2545421 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 2626 | 39.4811 | -120.9928 | No | Clear;32-90 F | Other | Deteriorated | 24-0100557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965296 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | SWITCH | 2211 | 20240819 | 1233 | 20240819 | 1546 | 2545530 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2316 | 38.8791 | -121.1433 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0100574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965325 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240819 | 1347 | 20240819 | 1951 | 2545635 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2741 | 225735 | 38.6943 | -120.6784 | No | Clear;32-90 F |  |  | 24-0100671 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1965337 | 0 | EPSS Ckt | Y | 2024 | A C SGF DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S @ CGC 223819738702 | 20240819 | 1356 | 20240819 | 1551 | 2545743 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 115 | 38.7222 | -120.662 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0100733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965353 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223020556505 | 20240819 | 1646 | 20240819 | 1935 | 2545774 | 169 | Transformer only | Company Initiated | Personnel- company | 1 | 169 | 39.213 | -120.9345 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1965378 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7091 | 20240820 | 1212 | 20240820 | 1400 | 2546253 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 11448 | 39.1884 | -121.0272 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0100923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965560 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 507 | 20240820 | 2112 | 20240821 | 107 | 2546793 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 71183 | 38.9804 | -121.0232 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101151 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965689 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | OJ'S @ LINE AND BUCK TWD 222277655684 | 20240820 | 2301 | 20240821 | 232 | s1965698 | 211 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 211 | 0 | 0 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0101238 | OH | Sus | 31705896 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965698 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | JUMPER | OJS 1 SPAN W/OF CGC 222622052984 | 20240821 | 1337 | 20240821 | 1528 | 2547376 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 666 | 39.1177 | -121.0771 | No | Clear;32-90 F | Insulator | Broken | 24-0101524 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965951 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | JUMPER | FB 2 W/O 2361 | 20240821 | 2202 | 20240822 | 232 | 2547684 | 270 | Distribution Circuit | Company Initiated | Improper Construction | 4 | 1080 | 39.2282 | -121.205 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966003 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 76952 | 20240822 | 705 | 20240822 | 1803 | 2547799 | 658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1746 | 120867 | 39.253 | -121.1971 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0101760 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966041 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | SWITCH | 18097 | 20240822 | 721 | 20240822 | 1217 | 2547813 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 28224 | 38.7253 | -120.8115 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0101458 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966045 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 164092 | 20240822 | 1052 | 20240822 | 1724 | 2548074 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7056 | 39.2626 | -121.0216 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 24-0101898 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966200 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20240822 | 1313 | 20240822 | 1321 | 2548231 | 8 | Distribution Circuit | 3rd Party | Other | 648 | 5184 | 39.0757 | -121.1143 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966230 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21499 | 20240822 | 1852 | 20240822 | 2250 | 2548597 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 238 | 38.6088 | -120.7079 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0102163 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966285 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20240822 | 2120 | 20240823 | 115 | 2548685 | 235 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 804 | 121918 | 38.8695 | -121.02 | No | Clear;32-90 F |  |  | 24-0102198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966314 | 0 | EPSS Ckt | Y | 2024 | A/C DCD
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20240822 | 2127 | 20240823 | 1415 | 2548702 | 1008 | Distribution Circuit | Equipment Failure/Involved | Overhead | 595 | 273349 | 39.0443 | -120.9859 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0102199 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966315 | 0 | EPSS Ckt | Y | 2024 | A/C
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 997576 | 20240822 | 2338 | 20240823 | 353 | 2548751 | 255 | Distribution Circuit | 3rd Party | Metallic Balloon | 113 | 28815 | 39.0227 | -121.2938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966328 | 0 | EPSS Ckt | N | 2024 | A-C INST OC
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 676064 | 20240823 | 739 | 20240823 | 1056 | 2548880 | 197 | Distribution Circuit | Animal | Squirrel | 81 | 12037 | 38.9974 | -120.9795 | No | Partly Cloudy;32-90 F | Transformer (OH) | Normal | 24-0102263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966365 | 0 | EPSS Ckt | Y | 2024 | a-b
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 34523 | 20240823 | 1248 | 20240823 | 1505 | 2549258 | 137 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1507 | 39.0131 | -121.0302 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0102480 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966550 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20240823 | 1900 | 20240823 | 2249 | 2549526 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 595 | 86047 | 39.0443 | -120.9859 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0102638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966593 | 0 | EPSS Ckt | Y | 2024 | A-C INST OC
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 2768 | 20240823 | 2036 | 20240824 | 813 | 2549547 | 697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 184 | 16933 | 39.1028 | -120.96 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 24-0102663 | OH | Sus | 35576526 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966599 | 0 | EPSS Ckt | Y | 2024 | C GRD INST OC
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20240824 | 452 | 20240824 | 855 | 2549626 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 324 | 30100 | 38.9276 | -121.2469 | No | Overcast;32-90 F | Insulator | Arcing | 24-0102682 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966615 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 9453 | 20240824 | 701 | 20240824 | 847 | 2549885 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 278 | 8558 | 38.9421 | -121.1957 | No | Partly Cloudy;32-90 F |  |  | 24-0102700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966633 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2110 | 20240824 | 747 | 20240824 | 935 | 2549897 | 108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 853 | 45190 | 39.2017 | -121.0784 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0102705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966639 | 0 | EPSS Ckt | Y | 2024 | A B IOC
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 164092 | 20240824 | 823 | 20240824 | 1218 | 2549892 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 3792 | 39.2626 | -121.0216 | No | Overcast-Fog-Rain;32-90 F | Bushing | Arcing | 24-0102717 | OH | Sus | 31706400 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966656 | 0 | EPSS Ckt | Y | 2024 | N/A
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 20240824 | 910 | 20240824 | 1255 | 2550026 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 16277 | 38.895 | -120.9113 | No | Overcast;32-90 F | Lightning Arrestor | Burned/flashed | 24-0102731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966685 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | TRANSFORMER | 222609155784 | 20240824 | 922 | 20240824 | 1025 | 2550041 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 39.1945 | -121.0804 | No | Overcast-Fog;32-90 F |  |  | 24-0102757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1966704 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 38141 | 20240824 | 1013 | 20240824 | 1639 | 2550113 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 386 | 38.9378 | -121.0939 | No | Overcast-Drizzle;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0102758 | OH | Sus | 46304558 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966705 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 34667 | 20240824 | 1539 | 20240824 | 2054 | 2550325 | 315 | Distribution Circuit | Environmental/External | Lightning | 7 | 1707 | 38.7492 | -121.1889 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0102827 | OH | Sus | 35576532 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966754 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | RECLOSER | 2700 | 20240824 | 1858 | 20240824 | 2044 | 2550543 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 25334 | 38.9847 | -121.366 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0102849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966774 | 0 | EPSS Ckt | N | 2024 | B-C GRD TIME OC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 1532 | 20240825 | 624 | 20240825 | 1107 | 2550705 | 283 | Distribution Circuit | Animal | Bird found | 2739 | 395910 | 38.6943 | -120.6784 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966817 | 0 | EPSS Ckt | Y | 2024 | A-B SGF DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ N/OF CGC 223692533995 | 20240825 | 624 | 20240825 | 1107 | 2550777 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1132 | 38.5936 | -120.7097 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0102889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966842 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 10069 | 20240825 | 719 | 20240825 | 919 | 2550723 | 120 | Distribution Circuit | Animal | Squirrel | 1017 | 79080 | 38.6881 | -120.8298 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0102880 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966823 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OJ SS OF METER 1004589448 | 20240825 | 928 | 20240825 | 1017 | 2550795 | 49 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 49 | 39.0138 | -121.3289 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0102894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1966851 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | RECLOSER | 359542 | 20240825 | 1318 | 20240825 | 1451 | 2550863 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 322 | 29946 | 39.0189 | -120.8917 | No | Clear;32-90 F |  |  | 24-0102911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1966868 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 35645 | 20240826 | 1120 | 20240826 | 1146 | 2551569 | 26 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 78 | 38.7914 | -121.4696 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1967146 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 8975 | 20240826 | 1955 | 20240827 | 7 | s1989432 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 51660 | 38.8049 | -120.1402 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0103311 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1989432 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1104 | 152571104 | TRANSFORMER | 222404739135 | 20240827 | 800 | 20240827 | 1047 | 2552190 | 167 | Transformer only | Equipment Failure/Involved | Overhead | 11 | 1837 | 38.738 | -121.1579 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0103436 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1967279 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 164092 | 20240827 | 1136 | 20240827 | 1458 | 2552617 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 3636 | 39.2626 | -121.0216 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0103557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1967502 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50008 | 20240827 | 1309 | 20240827 | 1503 | 2552721 | 114 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2751 | 182286 | 39.2226 | -121.0515 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0103628 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1967525 | 0 | EPSS Ckt | N | 2024 | NA
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 542186 | 20240827 | 1717 | 20240827 | 1844 | 2552926 | 87 | Distribution Circuit | Company Initiated | Personnel- company | 92 | 8004 | 39.2144 | -120.8088 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0103763 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Three Phase Fault | 0 | No | No | No | 1967565 | 0 | EPSS Ckt | Y | 2024 | ABC
SIERRA | PLACER | BELL-1107 | 152701107 | RECLOSER | 2400 | 20240828 | 726 | 20240828 | 1146 | 2553391 | 260 | Distribution Circuit | 3rd Party | Vehicle | 523 | 39074 | 38.9452 | -121.1218 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0103883 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1967661 | 0 | EPSS Ckt | Y | 2024 | B GRD INST
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20240828 | 1405 | 20240828 | 1713 | 2553949 | 188 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 533 | 75295 | 39.214 | -120.8098 | No | Clear;32-90 F |  |  | 24-0104216 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1967902 | 0 | EPSS Ckt | Y | 2024 | A GRD INST OC
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | TRANSFORMER | 222665956326 | 20240828 | 1537 | 20240828 | 1744 | 2554029 | 127 | Transformer only | Company Initiated | Personnel- company | 19 | 2413 | 39.2094 | -121.0601 | No | Clear;32-90 F | Other | Normal | 24-0104337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1967927 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 20240828 | 1605 | 20240829 | 200 | 2554154 | 595 | Distribution Circuit | 3rd Party | Vehicle | 4977 | 535179 | 38.7394 | -120.6774 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0104336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1967926 | 0 | EPSS Ckt | Y | 2024 | PH INST OC
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2784 | 20240829 | 656 | 20240829 | 741 | 2554478 | 45 | Distribution Circuit | Animal | Squirrel | 1283 | 57735 | 39.2591 | -121.0188 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0104496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1968005 | 0 | EPSS Ckt | Y | 2024 | B GRD INST OC
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222963045779 | 20240829 | 849 | 20240829 | 1035 | 2554647 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 106 | 38.9187 | -120.9598 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0104568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1968113 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 6552 | 20240829 | 1004 | 20240829 | 1507 | 2554837 | 303 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3546 | 314076 | 38.6817 | -120.6632 | No | Clear;32-90 F |  |  | 24-0104649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1968210 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
SIERRA | PLACER | PLEASANT GROVE-2104 | 152442104 | OCB | 2104/2 | 20240829 | 1009 | 20240829 | 1057 | 2554862 | 48 | Distribution Circuit | Equipment Failure/Involved | Underground | 3982 | 191136 | 38.8222 | -121.3061 | No | Clear;32-90 F | Cable Termination(live front | Failed/Faulted | 24-0104655 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1968212 | 0 | Non-EPSS | N | 2024 | C GRD
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2230 | 20240829 | 1426 | 20240829 | 1553 | 2555154 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 875 | 76125 | 38.8963 | -121.1379 | No | Clear;Above 90 | Capacitor | Broken | 24-0104866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1968270 | 0 | EPSS Ckt | Y | 2024 | B-C SGF- DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223608034980 | 20240829 | 1932 | 20240829 | 1938 | 2555251 | 6 | Transformer only | Vegetation | Tree - fell into line | 1 | 6 | 38.6201 | -120.7384 | No | Clear;32-90 F | Service conductor | Bent or Twisted | 24-0105036 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1968302 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 40783 | 20240830 | 921 | 20240830 | 1050 | 2555793 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 3382 | 38.7667 | -121.1775 | No | Clear;32-90 F |  |  | 24-0105239 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1968510 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223830036785 | 20240830 | 1004 | 20240830 | 1045 | 2555835 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 158 | 38.6686 | -120.6603 | No | Clear;32-90 F | Insulator | Broken | 24-0105211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1968492 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | RECLOSER | 750 | 20240830 | 1209 | 20240830 | 1413 | 2555947 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 198 | 24552 | 38.8694 | -121.0803 | No | Clear;32-90 F |  |  | 24-0105320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1968528 | 0 | EPSS Ckt | Y | 2024 | A- INST OC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 795556 | 20240830 | 1328 | 20240830 | 1358 | 2556007 | 30 | Distribution Circuit | Company Initiated | Personnel- company | 40 | 1200 | 39.3126 | -120.9819 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1968545 | 0 | EPSS Ckt | Y | 2024 | A
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 41067 | 20240830 | 1633 | 20240830 | 1732 | 2556115 | 59 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 2537 | 38.7369 | -120.7342 | No | Clear;32-90 F | Insulator | Broken | 24-0105457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1968564 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 325964 | 20240830 | 1924 | 20240831 | 850 | 2556233 | 806 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 9703 | 38.6596 | -120.9832 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0105496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1968579 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7007 | 20240831 | 912 | 20240831 | 1007 | 2556410 | 55 | Distribution Circuit | Animal | Squirrel | 24 | 1320 | 39.2127 | -120.9877 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0105559 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1968636 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 76775 | 20240831 | 940 | 20240831 | 1135 | 2556422 | 115 | Distribution Circuit | 3rd Party | Vehicle | 2 | 230 | 38.9983 | -120.8701 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0105572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1968641 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HIGGINS-1109 | 152691109 | TRANSFORMER | 222586648264 | 20240901 | 639 | 20240901 | 805 | 2557005 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 38.9882 | -121.0914 | No | Clear;32-90 F |  |  | 24-0105668 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1968711 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 223039457981 | 20240901 | 705 | 20240901 | 1149 | 2557012 | 284 | Transformer only | Animal | Squirrel | 1 | 284 | 39.2529 | -120.9282 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0105673 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1968716 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 224335060258 | 20240901 | 1123 | 20240901 | 1414 | 2557092 | 171 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 171 | 39.3131 | -120.4693 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0105700 | OH | Sus | 31707241 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1968736 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 37727 | 20240901 | 1731 | 20240902 | 129 | 2557245 | 478 | Distribution Circuit | 3rd Party | Vehicle | 14 | 855 | 38.9562 | -121.0543 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | Yes | No | 1968762 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 4399 | 20240901 | 1857 | 20240901 | 1947 | 2557286 | 50 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 750 | 39.2322 | -121.1973 | No | Clear;32-90 F |  |  | 24-0105740 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1968770 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240902 | 1312 | 20240903 | 107 | 2557615 | 715 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 2110 | 167128 | 39.2042 | -121.2005 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0105836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1968833 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 674140 | 20240903 | 1015 | 20240903 | 1152 | 2558199 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1261 | 38.9015 | -120.9036 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0105941 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969058 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222702455020 | 20240903 | 1020 | 20240903 | 1045 | 2558250 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 50 | 39.1734 | -121.0477 | No | Clear;32-90 F | Fuse | Normal | 24-0106059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969074 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 337536 | 20240903 | 1222 | 20240903 | 1235 | 2558409 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 92 | 1196 | 38.6781 | -120.7635 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969106 | 0 | EPSS Ckt | N | 2024 | A & B
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 584090 | 20240903 | 1256 | 20240903 | 1322 | 2558451 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 87 | 2262 | 38.9432 | -120.7202 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969111 | 0 | EPSS Ckt | Y | 2024 | A+B
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 3881 | 20240903 | 1352 | 20240903 | 2331 | 2558507 | 579 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 2 | 1158 | 38.8046 | -121.1706 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0106257 | UG | Sus | 46308347 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969142 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 224107939647 | 20240903 | 1510 | 20240903 | 1523 | 2558513 | 13 | Transformer only | Vegetation | Tree - fell into line | 1 | 13 | 38.7464 | -120.561 | No | Clear;32-90 F | Customer Equipment | Broken | 24-0106303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969152 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 35424 | 20240903 | 2002 | 20240904 | 1409 | 2558757 | 1087 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 39550 | 39.3432 | -121.1213 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0106423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1969178 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER | 223121937099 | 20240903 | 2334 | 20240904 | 954 | 2558842 | 620 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1240 | 38.6801 | -120.9077 | No | Clear;32-90 F | Regulator | Failed/Faulted | 24-0106449 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969200 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1820 | 20240904 | 800 | 20240904 | 817 | 2558987 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 105 | 1785 | 39.0336 | -120.7967 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106516 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969257 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 21107 | 20240904 | 832 | 20240904 | 948 | 2559060 | 76 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 34 | 2584 | 38.7267 | -120.7616 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969378 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20240904 | 848 | 20240904 | 1148 | 2559100 | 180 | Distribution Circuit | 3rd Party | Vehicle | 703 | 57793 | 38.6615 | -120.9109 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0106556 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969324 | 0 | EPSS Ckt | Y | 2024 | C+GRD
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | TRANSFORMER | 222797150996 | 20240904 | 912 | 20240904 | 1940 | 2559397 | 628 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 628 | 39.0632 | -121.0158 | No | Clear;Above 90 | Insulator | Failed/Faulted | 24-0106769 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969450 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | JUMPER | OJS SS SIDE OF MTR#100418712 | 20240904 | 1134 | 20240904 | 1535 | 2559301 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 482 | 38.8627 | -121.1963 | No | Clear;Above 90 | Pole-Wood | Broken | 24-0106654 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969417 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 458102 | 20240904 | 1521 | 20240904 | 1659 | 2559533 | 98 | Distribution Circuit | Company Initiated | Coordination failure | 265 | 25970 | 39.1494 | -121.0345 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0106865 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969485 | 0 | EPSS Ckt | Y | 2024 | a-b
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7039 | 20240904 | 1521 | 20240905 | 149 | 2559537 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 32028 | 39.1992 | -121.0201 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0106895 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1969490 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 8089 | 20240904 | 1552 | 20240904 | 1731 | 2559554 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2277 | 38.9194 | -121.112 | No | Clear;Above 90 |  |  | 24-0106956 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969506 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222533145772 | 20240904 | 1838 | 20240905 | 143 | 2559692 | 425 | Transformer only | Animal | Bird found | 1 | 425 | 38.92 | -121.1107 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0106994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969524 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | TRANSFORMER | 221724542223 | 20240904 | 2034 | 20240904 | 2224 | 2559754 | 110 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 110 | 38.8244 | -121.3955 | No | Clear;32-90 F | Insulator | Broken | 24-0107014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969539 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222128046006 | 20240905 | 900 | 20240905 | 1322 | 2559852 | 262 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 786 | 38.9275 | -121.2531 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0107109 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969659 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | RECLOSER | 724884 | 20240905 | 905 | 20240905 | 1104 | 2560105 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 369 | 28305 | 38.9512 | -121.0773 | No | Clear;32-90 F |  |  | 24-0107123 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969686 | 0 | EPSS Ckt | Y | 2024 | A+C
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5719 | 20240905 | 915 | 20240905 | 1202 | 2560076 | 167 | Distribution Circuit | Vegetation | Tree - grew into line | 22 | 3674 | 39.0028 | -121.0268 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107130 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969698 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | 4 POLE SOUTH OF MTR#5000156965 | 20240905 | 1010 | 20240905 | 1411 | 2560152 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1205 | 38.8862 | -120.8893 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0107153 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969717 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 810550 | 20240905 | 1245 | 20240905 | 1259 | 2560323 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 23 | 322 | 38.6733 | -120.6967 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0107340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969764 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 272286 | 20240905 | 1356 | 20240905 | 1516 | 2560397 | 80 | Distribution Circuit | Company Initiated | Personnel- company | 185 | 14800 | 39.263 | -120.9118 | No | Clear;Above 90 | Fuse | Normal | 24-0107435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969785 | 1 | EPSS Ckt | Y | 2024 | B
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222338557125 | 20240905 | 2046 | 20240906 | 347 | 2560671 | 421 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 842 | 39.2324 | -121.1751 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0107623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1969846 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 68859 | 20240905 | 2305 | 20240906 | 246 | 2560689 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 442 | 38.9839 | -121.0233 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0107616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969841 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 6842 | 20240906 | 940 | 20240906 | 1032 | 2561017 | 52 | Distribution Circuit | 3rd Party | Aircraft | 2917 | 151684 | 38.6419 | -121.0734 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970035 | 0 | EPSS Ckt | N | 2024 | TIME OC
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | OTHER | J40L TWD T9897 | 20240906 | 1054 | 20240906 | 1118 | 2561099 | 24 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 172 | 4128 | 38.6841 | -120.9974 | No | Clear;Above 90 | Connector or Splice (UG) | Broken | 24-0107508 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1970050 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 458102 | 20240906 | 1221 | 20240906 | 1234 | 2561206 | 13 | Distribution Circuit | Company Initiated | Personnel- company | 226 | 2938 | 39.1494 | -121.0345 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0107935 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970079 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | SWITCH | 3834 | 20240906 | 1350 | 20240906 | 1412 | 2561321 | 22 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 172 | 3784 | 38.6794 | -120.9916 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0107508 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1970094 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 20240906 | 1537 | 20240906 | 1915 | 2561438 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2500 | 212476 | 38.7393 | -120.6773 | No | Clear;Above 90 |  |  | 24-0108083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1970130 | 0 | EPSS Ckt | Y | 2024 | a
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223793639402 | 20240906 | 2235 | 20240906 | 2244 | 2561614 | 9 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 36 | 38.7407 | -120.6714 | No | Clear;32-90 F |  |  | 24-0108152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1970172 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 30651 | 20240907 | 733 | 20240907 | 1017 | 2561812 | 162 | Distribution Circuit | Animal | Squirrel | 9 | 1458 | 39.0009 | -121.0239 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0108217 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970259 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | JUMPER | OJ LD SIDE CGC 223200040131 | 20240907 | 928 | 20240907 | 1158 | 2561892 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 600 | 38.7632 | -120.8783 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0108201 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1970250 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | OCB | 2108/2 | 20240907 | 1407 | 20240907 | 1536 | 2562074 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3064 | 254520 | 38.6597 | -120.947 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108265 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970293 | 0 | EPSS Ckt | Y | 2024 | a-b
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 7255 | 20240907 | 1729 | 20240907 | 1832 | 2562156 | 63 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 504 | 39.2693 | -121.1123 | No | Partly Cloudy;Above 90 | Cutout- fuse holder | Normal | 24-0108296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | No | No | 1970309 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 20240907 | 1843 | 20240908 | 1753 | 2562184 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 36140 | 39.4382 | -120.9965 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1970314 | 0 | EPSS Ckt | Y | 2024 | B-C INST OC
SIERRA | PLACER | WEIMAR-1101 | 152491101 | RECLOSER | 2084 | 20240908 | 1512 | 20240908 | 1722 | 2562673 | 130 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 373 | 46810 | 39.0318 | -120.9741 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108400 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1970395 | 0 | EPSS Ckt | N | 2024 | none
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | RECLOSER | 542186 | 20240909 | 1107 | 20240909 | 1132 | 2563330 | 25 | Distribution Circuit | Company Initiated | Personnel- company | 4 | 100 | 39.2144 | -120.8088 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970641 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | PLEASANT GROVE-2107 | 152442107 | OCB | 2107/2 | 20240909 | 1143 | 20240910 | 405 | 2563368 | 835 | Distribution Circuit | Equipment Failure/Involved | Underground | 3871 | 480334 | 38.8222 | -121.306 | No | Clear;Above 90 | Elbow | Failed/Faulted | 24-0108658 | UG | Sus | 46312397 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1970650 | 0 | Non-EPSS | N | 2024 | C GRD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 23190 | 20240909 | 1438 | 20240910 | 55 | 2563596 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 2034 | 122749 | 38.7384 | -120.7798 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0108798 | OH | Sus | 31708222 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970692 | 0 | EPSS Ckt | Y | 2024 | BC
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 997576 | 20240910 | 623 | 20240910 | 1104 | 2564040 | 281 | Distribution Circuit | Animal | Other | 113 | 31753 | 39.0227 | -121.2938 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0108976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970761 | 0 | EPSS Ckt | Y | 2024 | A C INST OC
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 40743 | 20240910 | 848 | 20240910 | 1104 | 2564235 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 680 | 38.7325 | -121.0902 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0109038 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1970876 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 467470 | 20240910 | 904 | 20240910 | 955 | 2564302 | 51 | Distribution Circuit | Company Initiated | Personnel- company | 1431 | 71813 | 38.9583 | -121.1016 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1970902 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 7919 | 20240910 | 1013 | 20240910 | 1545 | 2564425 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 21580 | 38.7507 | -120.632 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1970957 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222287656599 | 20240910 | 1421 | 20240910 | 1948 | 2564616 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 1635 | 39.2186 | -121.1936 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0109275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971037 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 644180 | 20240910 | 1453 | 20240910 | 1507 | 2564702 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 427 | 5978 | 39.2182 | -121.1913 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109289 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971040 | 0 | EPSS Ckt | Y | 2024 | GRD INSTA OC
SIERRA | PLACER | DEL MAR-2105 | 152582105 | TRANSFORMER | 222183141265 | 20240911 | 251 | 20240911 | 441 | 2564982 | 110 | Transformer only | Animal | Other | 1 | 110 | 38.797 | -121.235 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0109429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971097 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20240911 | 949 | 20240912 | 240 | 2565322 | 1011 | Distribution Circuit | Company Initiated | Coordination failure | 2136 | 779652 | 38.7138 | -120.9394 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0109584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971289 | 0 | EPSS Ckt | Y | 2024 | DCD
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7927 | 20240911 | 1022 | 20240911 | 1245 | 2565362 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1001 | 38.8464 | -121.4237 | No | Clear;32-90 F |  |  | 24-0109733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971335 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 8881 | 20240911 | 1352 | 20240911 | 1832 | 2565604 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 3920 | 39.2723 | -120.9957 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109793 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1971357 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 223035835909 | 20240911 | 1409 | 20240911 | 1542 | 2565634 | 93 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 6 | 558 | 38.6484 | -120.9377 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109883 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971386 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2105 | 152582105 | FUSE | 32201 | 20240911 | 1610 | 20240911 | 1646 | 2565797 | 36 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 1163 | 38.7914 | -121.2549 | No | Clear;32-90 F |  |  | 24-0109916 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1971401 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 8171 | 20240911 | 1646 | 20240911 | 1827 | 2565848 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 3131 | 39.1114 | -121.144 | No | Clear;32-90 F |  |  | 24-0109946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971417 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 935216 | 20240912 | 653 | 20240912 | 1127 | 2566186 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 244 | 62404 | 38.7571 | -120.7681 | No | Clear;32-90 F |  |  | 24-0110049 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971487 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | OCB | 1106/2 | 20240912 | 1010 | 20240912 | 1038 | 2566508 | 28 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2040 | 57120 | 38.7444 | -121.161 | No | Clear;32-90 F | Insulator | Broken | 24-0110180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1971662 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 3685 | 20240912 | 1831 | 20240912 | 2013 | 2566910 | 102 | Distribution Circuit | Animal | Other | 4 | 408 | 39.2767 | -121.1943 | No | Clear;32-90 F | Anchor or Guy | Normal | 24-0110521 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971741 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20240913 | 117 | 20240913 | 1304 | 2567036 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 685 | 109750 | 38.8546 | -121.1508 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0110543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971771 | 0 | EPSS Ckt | Y | 2024 | A-B INST OC
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 7155 | 20240913 | 950 | 20240913 | 1208 | 2567334 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 276 | 38.8107 | -121.1871 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0110674 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1971921 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20240913 | 1447 | 20240913 | 1632 | 2567645 | 105 | Distribution Circuit | Animal | Bird found | 648 | 50640 | 39.0757 | -121.1143 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972001 | 0 | EPSS Ckt | Y | 2024 | A-B INST OC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 6761 | 20240914 | 1147 | 20240914 | 1707 | 2568210 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1280 | 39.3231 | -120.886 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0111058 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972147 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21111 | 20240914 | 1504 | 20240914 | 1720 | 2568351 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 816 | 38.6937 | -120.7115 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0111082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972173 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 168616 | 20240914 | 1550 | 20240914 | 1656 | 2568366 | 66 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 13068 | 38.8543 | -121.1728 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0111088 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972176 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | JUMPER | OJ 2 SPANS SS OF CGC 222209150496 | 20240914 | 1856 | 20240914 | 2225 | 2568419 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1045 | 39.0495 | -121.2216 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0111099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972188 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 467470 | 20240915 | 758 | 20240916 | 53 | 2568580 | 1015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1595 | 568919 | 38.9583 | -121.1016 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0111145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972224 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | ROCKLIN-1101 | 152061101 | FUSE | 30303 | 20240915 | 954 | 20240915 | 1134 | 2568667 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 7800 | 38.7834 | -121.2279 | No | Partly Cloudy;32-90 F |  |  | 24-0111165 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972248 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 78862 | 20240915 | 1002 | 20240915 | 1058 | 2568684 | 56 | Distribution Circuit | Vegetation | Tree - branch fell on line | 247 | 13832 | 39.2548 | -121.0242 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972241 | 0 | EPSS Ckt | Y | 2024 | AB
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2708 | 20240915 | 1112 | 20240915 | 1238 | 2568720 | 86 | Distribution Circuit | Animal | Bird found | 384 | 33024 | 38.7961 | -121.1633 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111167 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972249 | 0 | EPSS Ckt | Y | 2024 | AB
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJS @ CGC 222809456238 | 20240915 | 1150 | 20240915 | 1728 | 2568740 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3380 | 39.2067 | -121.0097 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0111171 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972253 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 6842 | 20240915 | 1354 | 20240915 | 1626 | 2568862 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2917 | 255230 | 38.6419 | -121.0734 | No | Clear;32-90 F |  |  | 24-0111189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972269 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 693294 | 20240915 | 1838 | 20240915 | 2055 | 2569001 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 286 | 17288 | 38.912 | -121.2487 | No | Partly Cloudy;32-90 F | Secondary | Burned Open | 24-0111219 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | No | No | 1972291 | 0 | EPSS Ckt | Y | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 76088 | 20240916 | 639 | 20240916 | 857 | 2569227 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 407 | 53401 | 38.6737 | -120.76 | No | Overcast;32-90 F | Fuse | Broken | 24-0111299 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972366 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18747 | 20240916 | 1017 | 20240916 | 1524 | 2569589 | 307 | Distribution Circuit | Company Initiated | Insulator washing | 58 | 17806 | 38.5601 | -120.8471 | No | Partly Cloudy;32-90 F | Pole-Wood | Contaminated | 24-0111445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972541 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 3137 | 20240916 | 1046 | 20240916 | 1552 | 2569632 | 306 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 306 | 39.2559 | -121.0277 | No | Clear;32-90 F | Conductor- Underground | Contaminated | 24-0111506 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972565 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222052055790 | 20240916 | 1151 | 20240916 | 1307 | 2569690 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 76 | 39.1961 | -121.2766 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0111511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972568 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 8419 | 20240916 | 1207 | 20240916 | 1443 | 2569722 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 468 | 39.0588 | -121.0794 | No | Partly Cloudy;32-90 F |  |  | 24-0111619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972612 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222064656338 | 20240916 | 1352 | 20240916 | 1451 | 2569837 | 59 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 59 | 39.2114 | -121.2725 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0111603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1972608 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20240917 | 155 | 20240917 | 730 | 2570216 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1116 | 198561 | 38.7607 | -120.505 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0111798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972695 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20240917 | 754 | 20240917 | 1037 | 2570299 | 163 | Distribution Circuit | Company Initiated | Personnel- company | 671 | 59603 | 39.2129 | -121.0129 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0111850 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972728 | 0 | EPSS Ckt | Y | 2024 | A B INST OC
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20240917 | 833 | 20240917 | 847 | 2570448 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 1171 | 16394 | 39.2408 | -121.0301 | No | Overcast;32-90 F | Elbow | Normal | 24-0111877 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972794 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | TRANSFORMER | 222621356355 | 20240917 | 901 | 20240917 | 1335 | 2570531 | 274 | Transformer only | Animal | Squirrel | 4 | 1096 | 39.2104 | -121.076 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 24-0111981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972912 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 3137 | 20240917 | 1324 | 20240917 | 1330 | 2570790 | 6 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 6 | 39.2559 | -121.0277 | No | Partly Cloudy;32-90 F | Metering Equipment | Malfunctioning | 24-0112043 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1972951 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | FUSE | 8417 | 20240917 | 1441 | 20240917 | 1522 | 2570844 | 41 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 41 | 38.7224 | -120.7917 | No | Partly Cloudy;32-90 F |  |  | 24-0112115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972964 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222587552460 | 20240917 | 2322 | 20240918 | 805 | 2571189 | 523 | Transformer only | 3rd Party | Vehicle | 1 | 523 | 39.1036 | -121.0891 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0112292 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1973093 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223243455393 | 20240918 | 925 | 20240918 | 1057 | 2571488 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 828 | 39.1824 | -120.8568 | No | Overcast;32-90 F | Insulator | Broken | 24-0112353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973213 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 33331 | 20240918 | 1030 | 20240918 | 1118 | 2571561 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 768 | 38.7432 | -121.1662 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0112383 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973253 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 227062 | 20240918 | 1111 | 20240918 | 1118 | 2571624 | 7 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 1204 | 39.1876 | -120.9498 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0112418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973273 | 0 | EPSS Ckt | N | 2024 | none
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7803 | 20240918 | 1205 | 20240918 | 1707 | 2571654 | 302 | Distribution Circuit | 3rd Party | Vehicle | 21 | 4262 | 39.1066 | -121.0874 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0112430 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973279 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 889106 | 20240918 | 1355 | 20240918 | 1530 | 2571780 | 95 | Distribution Circuit | Environmental/External | Lightning | 35 | 3325 | 38.8035 | -120.046 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0112590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Multi-Fault | 0 | No | No | No | 1973325 | 0 | EPSS Ckt | Y | 2024 | B-C- GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223656034245 | 20240918 | 1735 | 20240918 | 1753 | 2571956 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 38.5999 | -120.7211 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 24-0112743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973358 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 222948735138 | 20240918 | 2314 | 20240919 | 224 | 2572088 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 950 | 38.6269 | -120.969 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0112801 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1973391 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20240919 | 633 | 20240919 | 752 | 2572200 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 324 | 15412 | 38.9276 | -121.2469 | No | Partly Cloudy;32-90 F |  |  | 24-0112831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1973410 | 0 | EPSS Ckt | Y | 2024 | AC
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | FUSE | 9769 | 20240919 | 832 | 20240919 | 933 | 2572306 | 61 | Distribution Circuit | Animal | Squirrel | 11 | 671 | 38.7392 | -121.0826 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0112908 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1973508 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | JUMPER | 449475 | 20240919 | 916 | 20240919 | 1612 | 2572558 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7473 | 38.696 | -120.6069 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0113065 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | Yes | Yes | 1973559 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 20991 | 20240919 | 1100 | 20240919 | 1500 | 2572534 | 240 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 480 | 38.8056 | -120.0436 | No | Partly Cloudy;32-90 F | Customer Equipment | Burned/flashed | 24-0113036 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973546 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 533042 | 20240919 | 1302 | 20240919 | 1313 | 2572584 | 11 | Distribution Circuit | Company Initiated | Personnel- company | 202 | 2222 | 38.9971 | -121.1168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0113096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1973574 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20240919 | 1326 | 20240919 | 1427 | 2572605 | 61 | Distribution Circuit | Animal | Squirrel | 525 | 32025 | 39.2191 | -121.0228 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0113110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1973579 | 0 | EPSS Ckt | Y | 2024 | GRD
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20240919 | 1451 | 20240919 | 1605 | 2572698 | 74 | Distribution Circuit | Animal | Bird found | 458 | 33892 | 38.8637 | -121.1283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0113180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1973596 | 0 | EPSS Ckt | Y | 2024 | AC
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | SWITCH | 992864 | 20240919 | 1718 | 20240919 | 1744 | 2572819 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 984 | 25584 | 38.8042 | -120.1031 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0111798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1973620 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2796 | 20240920 | 1132 | 20240920 | 1814 | 2573469 | 402 | Distribution Circuit | 3rd Party | Vehicle | 1497 | 58060 | 39.1981 | -121.0285 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0113626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Multi-Fault | 0 | No | Yes | No | 1973889 | 0 | EPSS Ckt | Y | 2024 | B - C DCD
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | SWITCH | 58935 | 20240920 | 1632 | 20240920 | 1824 | 2573701 | 112 | Distribution Circuit | Vegetation | Tree - grew into line | 32 | 3584 | 38.7525 | -120.8224 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0113863 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973944 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223055053365 | 20240921 | 903 | 20240921 | 1015 | 2573936 | 72 | Transformer only | Animal | Squirrel | 2 | 144 | 39.1271 | -120.9242 | No | Clear;32-90 F | Transformer (OH) |  | 24-0113947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974063 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2109 | 152582109 | RECLOSER | 75802 | 20240921 | 1928 | 20240921 | 2017 | 2574244 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2834 | 110546 | 38.8488 | -121.2315 | No | Clear;32-90 F |  |  | 24-0114067 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1974130 | 0 | EPSS Ckt | Y | 2024 | AB
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222961856817 | 20240921 | 1950 | 20240921 | 2116 | 2574257 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 39.2221 | -120.9557 | No | Clear;32-90 F |  |  | 24-0114080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1974142 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222521957858 | 20240922 | 715 | 20240922 | 829 | 2574372 | 74 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 148 | 39.252 | -121.1104 | No | Clear;32-90 F |  |  | 24-0114108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974199 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | OTHER | T2251 TWD T2252 | 20240922 | 1440 | 20240922 | 1718 | 2574585 | 158 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 2528 | 38.782 | -121.2485 | No | Clear;32-90 F | Secondary | Broken | 24-0114125 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1974254 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | DEL MAR-2109 | 152582109 | FUSE | 37433 | 20240923 | 1201 | 20240923 | 1433 | 2575472 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1368 | 38.849 | -121.2316 | No | Clear;32-90 F |  |  | 24-0114482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1974561 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222865057511 | 20240923 | 1625 | 20240923 | 2240 | 2575609 | 375 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 750 | 39.2413 | -120.9894 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0114572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974595 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7265 | 20240924 | 12 | 20240924 | 547 | 2575851 | 335 | Distribution Circuit | Equipment Failure/Involved | Underground | 31 | 10385 | 39.2001 | -121.1785 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0114631 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1974635 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20240924 | 725 | 20240924 | 1019 | 2575956 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 208 | 36192 | 39.274 | -120.9698 | No | Clear;32-90 F |  |  | 24-0114689 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974673 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 50008 | 20240924 | 725 | 20240924 | 809 | 2575961 | 44 | Distribution Circuit | Animal | Squirrel | 1284 | 56496 | 39.2226 | -121.0515 | No | Clear;32-90 F | Pothead/Riser Termination | Normal | 24-0114692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974677 | 1 | EPSS Ckt | Y | 2024 | A- GRD
SIERRA | PLACER | DEL MAR-1104 | 152581104 | OCB | 1104/2 | 20240924 | 908 | 20240924 | 1242 | 2576209 | 87 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 276 | 10290 | 38.7989 | -121.2215 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 24-0114799 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974838 | 0 | Non-EPSS | N | 2024 | A & GRD
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 39947 | 20240924 | 942 | 20240924 | 1316 | 2576275 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 5136 | 38.9019 | -121.0718 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0114851 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1974870 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | FUSE | 31617 | 20240924 | 1117 | 20240924 | 1539 | 2576220 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 4978 | 38.9345 | -121.0884 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0114876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1974883 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20240924 | 1653 | 20240924 | 1822 | 2576720 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1878 | 111966 | 39.0997 | -121.05 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974974 | 0 | EPSS Ckt | Y | 2024 | B PHASE
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | T4035 | 20240924 | 1840 | 20240924 | 1939 | 2576781 | 59 | Transformer only | Equipment Failure/Involved | Underground | 4 | 236 | 38.6944 | -121.0069 | No | Clear;Above 90 | Fuse | Normal | 24-0115155 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1975000 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20240924 | 1918 | 20240924 | 2134 | 2576800 | 136 | Distribution Circuit | Animal | Bird found | 458 | 33938 | 38.8637 | -121.1283 | No | Clear;32-90 F | Fuse | Burned Open | 24-0115150 | OH | Sus | 2055305 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1974994 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222879154949 | 20240924 | 1958 | 20240924 | 2046 | 2576602 | 48 | Transformer only | 3rd Party | Vehicle | 1 | 48 | 39.1704 | -120.986 | No | Clear;32-90 F | Service conductor | Broken | 24-0115158 | OH | Sus | 31709638 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1975004 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 9432 | 20240925 | 823 | 20240925 | 1056 | 2577088 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 551 | 84303 | 38.7312 | -120.8428 | No | Clear;32-90 F |  |  | 24-0115253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1975117 | 0 | EPSS Ckt | Y | 2024 | BC GRD
SIERRA | PLACER | DEL MAR-1103 | 152581103 | FUSE | 31577 | 20240925 | 850 | 20240925 | 1006 | 2577148 | 76 | Distribution Circuit | Animal | Bird found | 2 | 152 | 38.8077 | -121.1845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975231 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 236062 | 20240925 | 918 | 20240925 | 1032 | 2577215 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 258 | 19092 | 38.7471 | -120.6442 | No | Clear;32-90 F | Other | Malfunctioning | 24-0115347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975245 | 0 | EPSS Ckt | Y | 2024 | N/A
SIERRA | PLACER | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20240925 | 1552 | 20240925 | 1654 | 2577663 | 62 | Distribution Circuit | Vegetation | Tree - fell into line | 467 | 28954 | 38.9945 | -121.026 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0115649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975338 | 0 | EPSS Ckt | Y | 2024 | A+B INST OC
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 21797 | 20240925 | 1706 | 20240925 | 1916 | 2577721 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 390 | 38.7935 | -120.912 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0115678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975351 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20240926 | 807 | 20240926 | 823 | 2577998 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 1028 | 16448 | 38.6779 | -120.8495 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115793 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1975443 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 467470 | 20240926 | 833 | 20240926 | 848 | 2578080 | 15 | Distribution Circuit | Company Initiated | Personnel- company | 1544 | 23160 | 38.9583 | -121.1016 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115807 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1975477 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | SWITCH | 65637 | 20240926 | 951 | 20240926 | 1630 | 2578226 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 75937 | 39.1893 | -121.0269 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0115747 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975564 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1102 | 152291102 | FUSE | 4259 | 20240926 | 1407 | 20240926 | 1926 | 2578317 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 13717 | 39.3059 | -120.5204 | No | Clear;32-90 F | Insulator | Broken | 24-0116124 | OH | Sus | 46327569 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975648 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | OTHER | T9286L TWD T5683 | 20240926 | 2025 | 20240926 | 2346 | 2578801 | 201 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 2469 | 38.6961 | -120.9018 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0116275 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975708 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20240927 | 41 | 20240927 | 342 | 2578916 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 648 | 54280 | 39.0757 | -121.1143 | No | Clear;32-90 F |  |  | 24-0116298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975734 | 0 | EPSS Ckt | Y | 2024 | A & B INST
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 307494 | 20240927 | 601 | 20240927 | 831 | 2578976 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 278 | 37540 | 38.934 | -121.1793 | No | Clear;32-90 F |  |  | 24-0116311 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1975755 | 0 | EPSS Ckt | Y | 2024 | B- C INST OC
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223490038510 | 20240927 | 1145 | 20240927 | 1246 | 2579410 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 122 | 38.7178 | -120.7792 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0116595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975946 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2104 | 153612104 | TRANSFORMER | T4035 | 20240927 | 1553 | 20240927 | 1808 | 2579599 | 135 | Transformer only | Equipment Failure/Involved | Underground | 4 | 540 | 38.6944 | -121.0069 | No | Clear;Above 90 | Fuse | Normal | 24-0116822 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1976022 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8479 | 20240927 | 2028 | 20240928 | 956 | 2579717 | 808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 42016 | 38.9916 | -121.0154 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0116838 | OH | Sus | 46328527 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1976042 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BRUNSWICK-1106 | 152481106 | RECLOSER | 2768 | 20240928 | 1132 | 20240928 | 1220 | 2580057 | 48 | Distribution Circuit | 3rd Party | Gun Shot | 184 | 8832 | 39.1028 | -120.96 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0116888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976175 | 0 | EPSS Ckt | Y | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 236062 | 20240928 | 1244 | 20240929 | 110 | 2580113 | 746 | Distribution Circuit | Animal | Squirrel | 258 | 37076 | 38.7471 | -120.6442 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0116907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1976197 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | OCB | 1110/2 | 20240929 | 731 | 20240929 | 1406 | 2580526 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1404 | 182022 | 39.0444 | -121.0909 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0117004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1976283 | 0 | EPSS Ckt | Y | 2024 | A-B-C
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20240929 | 1119 | 20240929 | 1433 | 2580655 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2113 | 160405 | 39.2042 | -121.2005 | No | Clear;32-90 F |  |  | 24-0117056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1976336 | 0 | EPSS Ckt | Y | 2024 | B&C
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 156136 | 20240930 | 1057 | 20240930 | 1449 | 2581358 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 464 | 38.6975 | -120.8355 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0117298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1976594 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10671 | 20240930 | 1734 | 20240930 | 1928 | 2581685 | 114 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 342 | 38.6113 | -120.6699 | No | Clear;32-90 F |  |  | 24-0117528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1976666 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 2226 | 20240930 | 2307 | 20241001 | 509 | 2581827 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 847 | 84934 | 38.9598 | -121.1016 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0117559 | OH | Sus | 46329486 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1976691 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | JUMPER | 4299 CENTER PHASE JUMPER OPEN | 20241001 | 727 | 20241001 | 1152 | 2581907 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 265 | 38.7361 | -121.1707 | No | Clear;32-90 F | Jumper | Burned Open | 24-0117632 | OH | Sus | 46329489 | NORTH VALLEY AND SIERRA | OCT | Open Circuit | 0 | No | No | No | 1976743 | 1 | Non-EPSS | N | 2024
SIERRA | PLACER | FLINT-1101 | 152531101 | TRANSFORMER | 222653844951 | 20241001 | 850 | 20241001 | 1030 | 2582087 | 100 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 900 | 38.8971 | -121.0687 | No | Clear;32-90 F | Service conductor | Broken | 24-0117658 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1976829 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | AUBURN-1101 | 152161101 | TRANSFORMER | 222654444998 | 20241001 | 1052 | 20241001 | 1144 | 2582257 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 468 | 38.8984 | -121.0684 | No | Clear;Above 90 | Service conductor | Broken | 24-0117744 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Open Circuit | 0 | No | No | No | 1976922 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | OCB | 2103/2 | 20241001 | 1106 | 20241001 | 1122 | 2582301 | 16 | Distribution Circuit | Company Initiated | Operating error | 3376 | 54016 | 38.6555 | -121.0604 | No | Clear;32-90 F | Circuit Breaker | Normal | 24-0050113 | OH | Sus | 45709854 | NORTH VALLEY AND SIERRA | OCT | Open Circuit | 0 | No | No | No | 1976935 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223869539293 | 20241001 | 1233 | 20241001 | 1330 | 2582382 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 38.7355 | -120.6447 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0117847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1976966 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | OCB | 2110/2 | 20241001 | 1621 | 20241002 | 309 | 2582675 | 648 | Distribution Circuit | Equipment Failure/Involved | Underground | 8024 | 745834 | 38.6597 | -120.947 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0118010 | UG | Sus | 46330026 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1977031 | 0 | EPSS Ckt | Y | 2024 | B- GRD INST OC
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | FUSE | 40783 | 20241002 | 722 | 20241002 | 812 | 2583029 | 50 | Distribution Circuit | Animal | Bird found | 38 | 1900 | 38.7667 | -121.1775 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0118153 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1977130 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20241002 | 925 | 20241002 | 1728 | 2583293 | 483 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 373 | 44904 | 39.3251 | -120.6429 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0118222 | OH | Sus | 31710743 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1977255 | 0 | EPSS Ckt | Y | 2024 | A-GRD
SIERRA | PLACER | FLINT-1101 | 152531101 | TRANSFORMER | 222652044948 | 20241002 | 1221 | 20241002 | 1325 | 2583543 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 192 | 38.897 | -121.0693 | No | Clear;Above 90 | Connector or Splice (OH) | Burned/flashed | 24-0118342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1977318 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 584090 | 20241002 | 1458 | 20241003 | 101 | 2583704 | 603 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 87 | 16358 | 38.9432 | -120.7202 | No | Clear;Above 90 | Conductor- Underground | Broken | 24-0118562 | UG | Sus | 46330435 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1977370 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222706355179 | 20241002 | 1550 | 20241003 | 327 | 2583750 | 697 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 6273 | 39.1778 | -121.0463 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0118598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977381 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | TRANSFORMER | 222809349699 | 20241002 | 1904 | 20241003 | 320 | 2584102 | 496 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1488 | 39.0269 | -121.012 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0118669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977428 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 222852845142 | 20241003 | 920 | 20241003 | 1133 | 2584557 | 133 | Transformer only | Vegetation | Other ground vegetation | 3 | 399 | 38.902 | -120.9987 | No | Drizzle-Clear;32-90 F | Other | Normal | 24-0118876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977599 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222758054064 | 20241003 | 1024 | 20241003 | 1344 | 2584572 | 200 | Transformer only | 3rd Party | Vehicle | 1 | 200 | 39.1471 | -121.0285 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0118911 | OH | Sus | 31710863 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1977609 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 77546 | 20241003 | 1127 | 20241003 | 1306 | 2584774 | 99 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 429 | 42471 | 38.5709 | -120.7329 | No | Clear;Above 90 |  |  | 24-0118926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1977610 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 644180 | 20241003 | 1619 | 20241004 | 22 | 2585016 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 469 | 52527 | 39.2182 | -121.1913 | No | Clear;Above 90 | Transformer (OH) | Broken | 24-0119143 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977656 | 0 | EPSS Ckt | Y | 2024 | C- GRD
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222335656236 | 20241003 | 1837 | 20241004 | 249 | 2585156 | 492 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 984 | 39.2084 | -121.1771 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119231 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977690 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1101 | 152461101 | FUSE | 3819 | 20241003 | 1949 | 20241003 | 2151 | 2585198 | 122 | Distribution Circuit | Vegetation | Tree - branch fell on line | 148 | 18056 | 38.8993 | -121.0799 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1977692 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | TRANSFORMER | T4446 | 20241003 | 2003 | 20241003 | 2038 | 2585205 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 70 | 38.6833 | -120.9557 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0119236 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977696 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | OCB | 1101/2 | 20241004 | 753 | 20241004 | 1239 | 2585463 | 286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2390 | 392267 | 39.0363 | -120.9881 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0119330 | OH | Sus | 31711067 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1977769 | 0 | EPSS Ckt | Y | 2024 | GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20241004 | 1204 | 20241004 | 1306 | 2585846 | 62 | Distribution Circuit | Company Initiated | Personnel- company | 3510 | 217620 | 39.1995 | -121.017 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0119536 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1977915 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10077 | 20241005 | 911 | 20241005 | 1251 | 2586664 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 10340 | 38.7967 | -120.9107 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0119762 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978041 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20241005 | 1457 | 20241005 | 1908 | 2586866 | 251 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 648 | 54790 | 39.0757 | -121.1143 | No | Clear;Above 90 |  |  | 24-0119833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978093 | 0 | EPSS Ckt | Y | 2024 | a b
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | RECLOSER | 8582 | 20241005 | 1906 | 20241005 | 2200 | 2587023 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 385 | 66990 | 38.7245 | -120.802 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0119879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978120 | 0 | EPSS Ckt | Y | 2024 | A- C
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 20241005 | 2348 | 20241006 | 409 | 2587089 | 261 | Distribution Circuit | Animal | Squirrel | 3938 | 884504 | 38.7934 | -120.62 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978131 | 0 | EPSS Ckt | Y | 2024 | C+GRD
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | RECLOSER | 357568 | 20241006 | 752 | 20241006 | 826 | 2587225 | 34 | Distribution Circuit | Animal | Squirrel | 257 | 8738 | 39.2214 | -121.067 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119909 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978159 | 0 | EPSS Ckt | Y | 2024 | C GRD INST OC
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9465 | 20241006 | 1003 | 20241006 | 1104 | 2587340 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 549 | 38.9175 | -121.2469 | No | Clear;32-90 F |  |  | 24-0119937 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978190 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 37579 | 20241007 | 1057 | 20241007 | 1239 | 2588280 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 1428 | 38.8244 | -121.4606 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 24-0120197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978502 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 817491 | 20241007 | 1201 | 20241007 | 1233 | 2588383 | 32 | Distribution Circuit | Company Initiated | Personnel- company | 6 | 192 | 38.854 | -121.2101 | No | Partly Cloudy;Above 90 | Jumper | Normal | 24-0120235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978525 | 0 | EPSS Ckt | N | 2024 | A-C
SIERRA | PLACER | FLINT-1101 | 152531101 | FUSE | 5541 | 20241007 | 1226 | 20241007 | 1325 | 2588358 | 59 | Distribution Circuit | Animal | Squirrel | 1 | 59 | 38.8794 | -121.0688 | No | Partly Cloudy;Above 90 | Pole-Wood | Normal | 24-0120249 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978540 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 471915 | 20241007 | 1510 | 20241007 | 1532 | 2588535 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 968 | 38.8782 | -120.9981 | No | Clear;Above 90 | Insulator | Broken | 24-0120344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978587 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20241007 | 1603 | 20241007 | 1710 | 2588620 | 67 | Distribution Circuit | 3rd Party | Vehicle | 458 | 27493 | 38.8637 | -121.1283 | No | Clear;Above 90 | Anchor or Guy | Broken | 24-0120385 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978603 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 223978140313 | 20241007 | 1646 | 20241008 | 5 | 2588621 | 439 | Transformer only | Vegetation | Tree - bark fell into line | 1 | 439 | 38.7659 | -120.6044 | No | Clear;32-90 F | Transformer | Burned/flashed | 24-0120404 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978614 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | RECLOSER | 19542 | 20241007 | 1945 | 20241008 | 258 | 2588926 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 616 | 211684 | 38.7617 | -120.5776 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0120433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978634 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
SIERRA | PLACER | PLACER-1101 | 152461101 | JUMPER | OJS @ CGC#222621844670 | 20241008 | 10 | 20241008 | 228 | 2589005 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 552 | 38.889 | -121.08 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0120479 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978656 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222808258377 | 20241008 | 52 | 20241008 | 749 | 2589017 | 417 | Transformer only | Vegetation | Tree - fell into line | 1 | 417 | 39.2655 | -121.0091 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0120484 | OH | Sus | 31711290 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1978660 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 307494 | 20241008 | 633 | 20241008 | 837 | 2589081 | 124 | Distribution Circuit | Animal | Bird found | 278 | 34472 | 38.934 | -121.1793 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978667 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE INST
SIERRA | EL DORADO | CLARKSVILLE-2109 | 153612109 | RECLOSER | 51742 | 20241008 | 709 | 20241008 | 952 | 2589102 | 163 | Distribution Circuit | Animal | Squirrel | 1264 | 150412 | 38.7292 | -121.082 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978676 | 0 | EPSS Ckt | Y | 2024 | A & GRD
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | RECLOSER | 11142 | 20241008 | 939 | 20241008 | 945 | 2589426 | 6 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1203 | 7218 | 38.7088 | -121.0888 | No | Clear;32-90 F | Jumper | Burned/flashed | 24-0101578 | OH | Sus | 35541058 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978860 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | SS CGC 222681055495 HIGH SIDE JUMPERS | 20241008 | 1033 | 20241008 | 1256 | 2589488 | 143 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 4 | 572 | 39.1861 | -121.0544 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0120642 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978878 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15281 | 20241008 | 1900 | 20241008 | 2127 | 2589963 | 147 | Distribution Circuit | Animal | Bird found | 1 | 147 | 38.9411 | -121.2876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0120943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1978983 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | SWITCH | 342355 | 20241008 | 2128 | 20241008 | 2306 | 2590043 | 98 | Distribution Circuit | Equipment Failure/Involved | Underground | 46 | 4508 | 38.7989 | -120.8856 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0120944 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1978984 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223675434385 | 20241009 | 926 | 20241009 | 1015 | 2590458 | 49 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 49 | 38.6032 | -120.7158 | No | Clear;32-90 F |  |  | 24-0121184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1979211 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1101 | 152461101 | OCB | 1101/2 | 20241009 | 1354 | 20241009 | 1454 | 2590748 | 60 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 86 | 5160 | 38.9014 | -121.0879 | No | Partly Cloudy;32-90 F |  |  | 24-0121345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1979273 | 0 | EPSS Ckt | Y | 2024 | A & B PHASE INST
SIERRA | PLACER | HALSEY-1101 | 152241101 | JUMPER | OJ'S 1 N/OF CGC 222721949034 | 20241009 | 2030 | 20241009 | 2110 | 2591081 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 234 | 39.0092 | -121.0431 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 24-0121560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1979325 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 37005 | 20241009 | 2050 | 20241010 | 248 | 2591084 | 358 | Distribution Circuit | 3rd Party | Vehicle | 2 | 716 | 38.8026 | -121.4003 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0121561 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1979326 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | TRANSFORMER | 222865750170 | 20241010 | 909 | 20241010 | 1455 | 2591382 | 346 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 3 | 1038 | 39.0399 | -120.9925 | No | Clear;32-90 F | Transformer | Normal | 24-0121742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1979520 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32373 | 20241010 | 1053 | 20241010 | 1511 | 2591518 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 602 | 38.8417 | -121.0217 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 24-0121754 | OH | Sus | 46337232 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1979526 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | RECLOSER | 1278 | 20241010 | 1103 | 20241010 | 1444 | 2591525 | 221 | Distribution Circuit | 3rd Party | Vehicle | 135 | 3742 | 38.8897 | -121.3401 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0121757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1979528 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | PLACER | WISE-1102 | 152271102 | SWITCH | 228639 | 20241011 | 802 | 20241011 | 827 | 2592079 | 25 | Distribution Circuit | Company Initiated | Return Circuit Normal | 82 | 2050 | 38.8833 | -121.1605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0109242 | OH | Sus | 35268210 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1979685 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 533042 | 20241011 | 1422 | 20241011 | 1442 | 2592471 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 155 | 3100 | 38.9971 | -121.1168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0122377 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1979856 | 0 | EPSS Ckt | N | 2024 | B C
SIERRA | PLACER | PENRYN-1105 | 152561105 | SWITCH | 2213BP | 20241011 | 1701 | 20241011 | 1711 | 2592578 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 82 | 820 | 38.893 | -121.1778 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0109242 | OH | Sus | 35268210 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1979874 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 32059 | 20241012 | 734 | 20241012 | 842 | 2592736 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 408 | 38.8406 | -121.1683 | No | Clear;32-90 F |  |  | 24-0122521 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1979959 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1105 | 153701105 | FUSE | 33367 | 20241012 | 1852 | 20241012 | 2044 | 2593260 | 112 | Distribution Circuit | Animal | Bird found | 1 | 112 | 38.8918 | -121.3402 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0122636 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1980069 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PLACER-1104 | 152461104 | RECLOSER | 51732 | 20241014 | 326 | 20241014 | 529 | 2593822 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 803 | 98769 | 38.9058 | -121.0824 | No | Clear;32-90 F |  |  | 24-0122746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1980176 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 8699 | 20241014 | 812 | 20241014 | 955 | 2593963 | 103 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 103 | 39.0463 | -121.0737 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0122789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1980247 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20241014 | 955 | 20241014 | 1122 | 2594214 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 721 | 62727 | 38.6615 | -120.9109 | No | Clear;32-90 F | Capacitor | Failed/Faulted | 24-0122861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1980381 | 0 | EPSS Ckt | Y | 2024 | B C
SIERRA | PLACER | FLINT-1101 | 152531101 | OCB | 1101/2 | 20241014 | 1657 | 20241014 | 1741 | 2594598 | 44 | Distribution Circuit | Animal | Squirrel | 2098 | 92312 | 38.8853 | -121.0674 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1980479 | 0 | EPSS Ckt | Y | 2024 | A-B GRD INST OC
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 584090 | 20241014 | 1716 | 20241014 | 1800 | 2594620 | 44 | Distribution Circuit | Company Initiated | Personnel- company | 6 | 264 | 38.9432 | -120.7202 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1980483 | 0 | EPSS Ckt | Y | 2024 | B
SIERRA | PLACER | CATLETT-1102 | 153761102 | TRANSFORMER | 221490639431 | 20241014 | 2207 | 20241014 | 2321 | 2594723 | 74 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 74 | 38.7482 | -121.4783 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0123142 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1980506 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | 223266538055 | 20241015 | 903 | 20241015 | 1103 | 2595072 | 120 | Transformer only | Animal | Squirrel | 2 | 240 | 38.7064 | -120.8564 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0123332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1980726 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 4105 | 20241015 | 1051 | 20241015 | 1937 | 2595145 | 526 | Distribution Circuit | 3rd Party | Vehicle | 12 | 6312 | 38.9138 | -120.6791 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0123350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1980745 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20241015 | 1201 | 20241015 | 1213 | 2595295 | 12 | Distribution Circuit | Company Initiated | Personnel- company | 2122 | 25464 | 39.1995 | -121.017 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1980756 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | COLUMBIA HILL TEMP GEN | 20241015 | 1517 | 20241015 | 1616 | 2595489 | 59 | Distribution Circuit | Company Initiated | Personnel- company | 978 | 57702 | 39.333 | -121.0999 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0100880 | OH | Sus | 35555475 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1980807 | 0 | EPSS Ckt | N | 2024 | A B C
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | OCB | 1102/2 | 20241015 | 1719 | 20241016 | 155 | 2595607 | 516 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 933 | 227128 | 39.1155 | -120.954 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123560 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1980826 | 0 | EPSS Ckt | Y | 2024 | A C INSTA OC
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20241016 | 807 | 20241016 | 1025 | 2595824 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 7168 | 38.9463 | -121.2467 | No | Overcast;32-90 F |  |  | 24-0123724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1980924 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 46965 | 20241016 | 834 | 20241016 | 1146 | 2595806 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 384 | 38.7175 | -120.8508 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0123718 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1980905 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 223046136361 | 20241016 | 1030 | 20241016 | 1415 | 2596022 | 225 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 225 | 38.6599 | -120.9344 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0123947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981072 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 19552 | 20241016 | 1455 | 20241016 | 2009 | 2596405 | 314 | Distribution Circuit | 3rd Party | Other | 519 | 13553 | 38.7436 | -120.7818 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0124122 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981150 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20241016 | 2320 | 20241017 | 259 | 2596684 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 9417 | 38.748 | -121.4698 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0124277 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981195 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222841355238 | 20241017 | 145 | 20241017 | 1057 | 2596788 | 552 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 552 | 39.1794 | -120.9998 | Yes | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0124324 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981214 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 7399 | 20241017 | 900 | 20241017 | 927 | 2596891 | 27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 729 | 38.953 | -121.0923 | Yes | Overcast;32-90 F | Crossarm- Wood | Deteriorated | 24-0124391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981244 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | JUMPER | OJ HARD TAP TWD CGC 221957546357 | 20241017 | 1234 | 20241017 | 1920 | 2597153 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 406 | 38.9375 | -121.316 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0124556 | OH | Sus | 46340373 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981319 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | WC 1101/2 | 20241017 | 1541 | 20241018 | 1013 | 2597505 | 1112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 103177 | 39.364 | -120.7923 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981428 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 297538 | 20241017 | 1631 | 20241017 | 1656 | 2597499 | 25 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 237 | 39.2336 | -121.0286 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981427 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11313 | 20241017 | 1756 | 20241017 | 1932 | 2597638 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1536 | 38.7837 | -120.8169 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981510 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 889106 | 20241017 | 1851 | 20241018 | 942 | 2597790 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 24334 | 38.8035 | -120.046 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 24-0124784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981506 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 20241017 | 2201 | 20241018 | 810 | 2598019 | 609 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1043 | 150420 | 38.8435 | -120.8737 | Yes | Clear;32-90 F |  |  | 24-0124814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981578 | 0 | EPSS Ckt | Y | 2024 | A & C
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 33213 | 20241017 | 2305 | 20241018 | 159 | 2598046 | 174 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 174 | 38.8867 | -121.2917 | Yes | Clear;32-90 F | Transformer (UG) | Leaking | 24-0124824 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981592 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 51584 | 20241017 | 2351 | 20241018 | 40 | 2598052 | 49 | Distribution Circuit | Animal | Other | 261 | 7797 | 38.8415 | -121.0158 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981594 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | PLACER | TAMARACK-1101 | 152291101 | OCB | 1101/2 | 20241017 | 2355 | 20241018 | 1329 | 2598058 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 1861 | 1396568 | 39.314 | -120.4962 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0124828 | OH | Sus | 31713016 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1981597 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20241018 | 18 | 20241018 | 1307 | 2598087 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 719 | 292980 | 38.773 | -120.2933 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0124830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981604 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | FUSE | 2613 | 20241018 | 925 | 20241018 | 1430 | 2598463 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2745 | 38.8228 | -120.0643 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981745 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 12802 | 20241018 | 1413 | 20241018 | 1439 | 2598753 | 26 | Distribution Circuit | Company Initiated | Return Circuit Normal | 40 | 1025 | 38.8036 | -120.0992 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981822 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | DEL MAR-2105 | 152582105 | SWITCH | 84138 | 20241018 | 1452 | 20241018 | 1520 | s1999248 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 2104 | 54732 | 38.8041 | -121.2421 | No | Clear;32-90 F | Recloser | Normal | 24-0110888 | OH | Sus | 35553345 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1999248 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222906354026 | 20241018 | 1608 | 20241018 | 2137 | 2598867 | 329 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 658 | 39.1459 | -120.9764 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0125255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981845 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | RECLOSER | 930180 | 20241018 | 1623 | 20241018 | 2137 | 2598876 | 314 | Distribution Circuit | 3rd Party | Vehicle | 9 | 2826 | 38.7516 | -121.4321 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0125223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981839 | 0 | Non-EPSS | N | 2024 | NA
SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 20241018 | 1933 | 20241018 | 1956 | 2598979 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 165 | 3687 | 39.3638 | -120.7923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0094752 | OH | Sus | 31649085 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981853 | 0 | Non-EPSS | N | 2024 | N/A
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20241018 | 1945 | 20241018 | 2235 | 2598984 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1043 | 83466 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0125274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981857 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | NEVADA | PIKE CITY SUB | 15220 | RECLOSER | PIKE CITY GENERATOR | 20241018 | 2009 | 20241018 | 2026 | 2599004 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 438 | 7446 | 39.438 | -120.996 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100603 | OH | Sus | 35559799 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981866 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | NEVADA | SIERRA CITY DIESEL SUB | 15801 | OCB | 52G | 20241018 | 2056 | 20241018 | 2107 | 2599021 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 448 | 4928 | 39.5686 | -120.6283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0094752 | OH | Sus | 31649085 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981871 | 0 | Non-EPSS | N | 2024 | N/A
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20241019 | 707 | 20241019 | 923 | 2599109 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 680 | 38.8986 | -120.8986 | No | Clear;32-90 F |  |  | 24-0125327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981952 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ'S @ CGC 222916756574 | 20241019 | 1154 | 20241019 | 1630 | 2599327 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 552 | 39.2156 | -120.9716 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0125391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981991 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 50072 | 20241020 | 6 | 20241020 | 515 | 2599603 | 309 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 648 | 200232 | 39.0757 | -121.1143 | No | Clear;32-90 F |  |  | 24-0125485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982048 | 0 | EPSS Ckt | Y | 2024 | A C INST OC
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | OCB | 1103/2 | 20241020 | 309 | 20241020 | 2002 | 2599629 | 1013 | Distribution Circuit | Equipment Failure/Involved | Underground | 1555 | 208027 | 38.7444 | -121.1609 | No | Clear;32-90 F | Switch (UG) | Failed/Faulted | 24-0125490 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Three Phase Fault | 0 | No | No | No | 1982054 | 0 | Non-EPSS | N | 2024 | A B C GRD
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | SWITCH | 87111 | 20241020 | 945 | 20241020 | 1252 | 2599742 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 17391 | 38.7779 | -121.2451 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0125512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1982097 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 680290 | 20241021 | 155 | 20241021 | 832 | 2599971 | 397 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 391 | 63987 | 38.8963 | -121.1806 | No | Partly Cloudy;32-90 F |  |  | 24-0125586 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982149 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | LINCOLN-1104 | 153701104 | JUMPER | OJ'S 2 SPANS SS OF CGC 222022548830 | 20241021 | 1742 | 20241021 | 2002 | 2600699 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 140 | 39.0066 | -121.2901 | No | Clear;32-90 F | Insulator | Broken | 24-0126014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1982407 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 4257 | 20241022 | 1506 | 20241023 | 240 | 2601497 | 694 | Distribution Circuit | Animal | Bird found | 40 | 5647 | 39.1039 | -121.0923 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0126531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982722 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222690053170 | 20241022 | 1618 | 20241022 | 1842 | 2601542 | 144 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 432 | 39.124 | -121.0533 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0126512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1982719 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 7722 | 20241023 | 704 | 20241023 | 924 | 2601778 | 140 | Distribution Circuit | Animal | Bird found | 1173 | 137679 | 38.6779 | -120.8495 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126651 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982780 | 0 | EPSS Ckt | Y | 2024 | A / B
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20241023 | 712 | 20241023 | 849 | 2601787 | 97 | Distribution Circuit | Animal | Bird found | 458 | 44426 | 38.8637 | -121.1283 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982781 | 0 | EPSS Ckt | Y | 2024 | B / C
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 8087 | 20241023 | 753 | 20241023 | 1035 | 2601815 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3402 | 38.9205 | -121.1133 | No | Clear;32-90 F |  |  | 24-0126780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1982970 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 37999 | 20241023 | 1002 | 20241023 | 1008 | 2602093 | 6 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 2 | 12 | 38.7516 | -121.4511 | No | Clear;32-90 F | Customer Equipment | Burned/flashed | 24-0126770 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1982963 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1110 | 152701110 | TRANSFORMER | T3951 | 20241023 | 1223 | 20241023 | 1356 | 2602230 | 93 | Transformer only | Animal | Squirrel | 1 | 93 | 38.9325 | -121.1055 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0126948 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983029 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | OTHER | T7279 TWD T7280 | 20241023 | 1325 | 20241023 | 1419 | 2602300 | 54 | Distribution Circuit | Equipment Failure/Involved | Underground | 12 | 648 | 38.8327 | -121.1467 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0112409 | UG | Sus | 35463945 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983025 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ TWD CGC 223955535637 | 20241024 | 1656 | 20241024 | 2235 | 2603270 | 339 | Distribution Circuit | Vegetation | Other ground vegetation | 1 | 339 | 38.6369 | -120.6146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983350 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | OCB | 1104/2 | 20241024 | 2011 | 20241024 | 2033 | 2603401 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4498 | 98956 | 39.0444 | -121.0911 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 24-0112919 | OH | Sus | 35444605 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983371 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 37238 | 20241025 | 1533 | 20241025 | 1634 | 2604019 | 61 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 6222 | 39.0474 | -120.7852 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983606 | 0 | EPSS Ckt | N | 2024 | n/a
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | OTHER | WIRE DOWN | 20241026 | 232 | 20241026 | 1142 | s1983656 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8038 | 38.7896 | -120.7353 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128108 | OH | Sus | 46344796 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | Yes | 1983656 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 285704 | 20241026 | 821 | 20241026 | 921 | 2604608 | 60 | Distribution Circuit | Company Initiated | Personnel- company | 60 | 3600 | 39.2409 | -121.0385 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128122 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983705 | 0 | EPSS Ckt | Y | 2024 | B - C INST
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18647 | 20241026 | 824 | 20241026 | 1000 | 2604609 | 96 | Distribution Circuit | Animal | Squirrel | 5 | 480 | 38.7021 | -120.7182 | No | Clear;32-90 F | Fuse | Normal | 24-0128147 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983751 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20241026 | 940 | 20241026 | 1203 | 2604709 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2115 | 108724 | 39.2042 | -121.2005 | No | Clear;32-90 F |  |  | 24-0128139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983746 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20241026 | 1138 | 20241026 | 1444 | 2604835 | 186 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1018 | 124820 | 38.8932 | -120.9965 | No | Clear;32-90 F |  |  | 24-0128172 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983778 | 0 | EPSS Ckt | Y | 2024 | A - B
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 935730 | 20241026 | 1216 | 20241026 | 1423 | 2604886 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 11049 | 39.4387 | -120.9996 | No | Clear;32-90 F |  |  | 24-0128182 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983785 | 0 | EPSS Ckt | Y | 2024 | A
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | SWITCH | 1063 | 20241026 | 1514 | 20241026 | 1520 | 2604962 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 272 | 1632 | 39.2843 | -121.057 | No | Partly Cloudy;32-90 F | Booster | Leaking | 24-0128197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983813 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | SWITCH | 2135 | 20241026 | 1538 | 20241026 | 1803 | 2604966 | 145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 140 | 20300 | 39.2666 | -121.0425 | No | Partly Cloudy;32-90 F | Booster | Leaking | 24-0128197 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983814 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 2557 | 20241026 | 1626 | 20241026 | 2143 | 2604991 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 951 | 38.8015 | -120.1164 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0128213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983820 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2110 | 153612110 | TRANSFORMER | T9445 | 20241026 | 2315 | 20241027 | 1803 | 2605170 | 1128 | Distribution Circuit | 3rd Party | Vehicle | 667 | 59150 | 38.7086 | -121.0844 | No | Clear;32-90 F | Transformer (UG) | Broken | 24-0128248 | UG | Sus | 35593000 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983860 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20241027 | 219 | 20241027 | 358 | 2605172 | 99 | Distribution Circuit | 3rd Party | Vehicle | 344 | 34056 | 38.8544 | -121.1507 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0128249 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983861 | 0 | EPSS Ckt | Y | 2024 | B & C
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 7179 | 20241027 | 231 | 20241027 | 624 | 2605189 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 12269 | 39.2418 | -121.0544 | No | Clear;32-90 F |  |  | 24-0128253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983866 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1102 | 152031102 | TRANSFORMER | 222660056528 | 20241027 | 728 | 20241027 | 1525 | 2605257 | 477 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2862 | 39.2149 | -121.0622 | No | Clear;32-90 F | Sectionalizer | Arcing | 24-0128264 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983882 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20241027 | 1549 | 20241027 | 1647 | 2605472 | 58 | Distribution Circuit | 3rd Party | Metallic Balloon | 450 | 26100 | 39.0473 | -121.0486 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0128320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983941 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20241027 | 2034 | 20241027 | 2221 | 2605603 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 881 | 94267 | 39.2609 | -120.9817 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Normal | 24-0128341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983962 | 0 | EPSS Ckt | Y | 2024 | A-C
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 663774 | 20241028 | 711 | 20241028 | 852 | 2605667 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1433 | 69733 | 39.1182 | -121.0373 | No | Overcast-Fog;32-90 F |  |  | 24-0128368 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983983 | 0 | EPSS Ckt | Y | 2024 | a+b+inst oc
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20241028 | 712 | 20241028 | 840 | 2605672 | 88 | Distribution Circuit | Animal | Bird found | 582 | 32176 | 38.9 | -120.9074 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0128371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983985 | 0 | EPSS Ckt | Y | 2024 | b+c
SIERRA | EL DORADO | CLARKSVILLE-2106 | 153612106 | OTHER | T9997 TWD 19401 | 20241028 | 849 | 20241028 | 910 | 2606018 | 21 | Distribution Circuit | Company Initiated | Improper Construction | 23 | 483 | 38.6907 | -121.0581 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0128384 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984120 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20241028 | 850 | 20241028 | 910 | 2605910 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 1194 | 23880 | 39.2408 | -121.0301 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0128426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1984073 | 0 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJS 5P S/E OF 94515 | 20241028 | 1102 | 20241028 | 1644 | 2606094 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1710 | 38.9057 | -120.9738 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0128486 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984150 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1102 | 152571102 | FUSE | 33331 | 20241028 | 1620 | 20241028 | 1825 | 2606494 | 125 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 2000 | 38.7432 | -121.1662 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0128703 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984236 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 85766 | 20241029 | 622 | 20241029 | 701 | 2606782 | 39 | Distribution Circuit | Company Initiated | Coordination failure | 1138 | 44382 | 38.8027 | -120.9071 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082590 | OH | Sus | 45331070 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1984301 | 1 | EPSS Ckt | Y | 2024 | DCD
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20241029 | 724 | 20241029 | 1017 | 2606823 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3061 | 160043 | 38.7716 | -120.8148 | No | Clear;32-90 F |  |  | 24-0128839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1984311 | 0 | EPSS Ckt | Y | 2024 | B-C INST OC
SIERRA | PLACER | TAMARACK-1101 | 152291101 | SWITCH | 47786 | 20241029 | 729 | 20241029 | 1804 | 2606875 | 635 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1852 | 765795 | 39.3291 | -120.3427 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0128846 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | No | 1984315 | 0 | EPSS Ckt | Y | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 2543 | 20241029 | 735 | 20241030 | 1559 | 2607679 | 1944 | Distribution Circuit | Company Initiated | Other Circuits | 52 | 2352 | 39.3365 | -120.3505 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0128846 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984603 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | T3599 | 20241029 | 735 | 20241030 | 1517 | 2607680 | 1902 | Distribution Circuit | Company Initiated | Other Circuits | 1 | 1902 | 39.33 | -120.3369 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0128846 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984604 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | T70923 | 20241029 | 735 | 20241030 | 1524 | 2608657 | 1909 | Transformer only | Company Initiated | Other Circuits | 1 | 1909 | 39.3295 | -120.3471 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0128846 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984966 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 32577 | 20241029 | 1045 | 20241029 | 1433 | 2607205 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3420 | 39.6583 | -120.6278 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128937 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984512 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 173744 | 20241029 | 1119 | 20241029 | 1255 | 2607249 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 12356 | 39.1038 | -121.0837 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0128966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984529 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | BELL-1107 | 152701107 | JUMPER | FLYINGS BELLS LD SIDE OF CGC 222426046450 | 20241029 | 1202 | 20241029 | 1436 | 2607070 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 308 | 38.9391 | -121.1484 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0128891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984434 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | T0974 | 20241029 | 1335 | 20241030 | 1530 | 2607678 | 1555 | Transformer only | Company Initiated | Other Circuits | 1 | 1555 | 39.337 | -120.3499 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0128846 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984602 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 102513 | 20241029 | 1335 | 20241030 | 1457 | 2607677 | 1522 | Distribution Circuit | Company Initiated | Other Circuits | 1 | 1522 | 39.3287 | -120.3491 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0128846 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984601 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9465 | 20241029 | 1711 | 20241029 | 1953 | 2607704 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1458 | 38.9175 | -121.2469 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0129224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984609 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 20241029 | 2145 | 20241030 | 119 | 2607823 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 32528 | 38.7911 | -120.7022 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0129289 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984633 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20241029 | 2156 | 20241029 | 2245 | 2607831 | 49 | Distribution Circuit | Company Initiated | Personnel- company | 628 | 30772 | 38.7523 | -120.6821 | No | Clear;32-90 F | Recloser | Normal | 24-0129295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1984634 | 1 | EPSS Ckt | Y | 2024 | SGF DCD
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | OCB | 1104/2 | 20241030 | 758 | 20241030 | 825 | 2607954 | 27 | Distribution Circuit | Company Initiated | Improper Construction | 3096 | 83592 | 39.0444 | -121.0911 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0110285 | OH | Sus | 35333731 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1984710 | 0 | EPSS Ckt | Y | 2024 | A+B
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 33687 | 20241030 | 935 | 20241030 | 1129 | 2608217 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1710 | 39.243 | -121.0558 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Normal | 24-0129485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984823 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | RECLOSER | 1101/2 | 20241030 | 1329 | 20241030 | 1427 | 2608461 | 58 | Distribution Circuit | Animal | Squirrel | 1891 | 90768 | 39.02 | -120.8294 | No | Partly Cloudy;32-90 F | Switch (OH) | Normal | 24-0129637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1984924 | 0 | EPSS Ckt | Y | 2024 | B- GRD
SIERRA | PLACER | AUBURN-1102 | 152161102 | RECLOSER | 1102/2 | 20241030 | 1711 | 20241030 | 1737 | 2608685 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1020 | 26520 | 38.9036 | -121.0699 | No | Overcast;32-90 F | Switch (OH) | Broken | 24-0102979 | OH | Sus | 35519183 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984968 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | AUBURN-1102 | 152161102 | RECLOSER | 251946 | 20241030 | 1712 | 20241030 | 1721 | s1986606 | 9 | Distribution Circuit | Company Initiated | Personnel- company | 980 | 8820 | 38.904 | -121.0666 | No | Overcast;32-90 F | Recloser | Normal | 24-0102979 | OH | Sus | 35519183 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1986606 | 0 | EPSS Ckt | N | 2024 | A
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20241030 | 1737 | 20241030 | 1900 | 2608698 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 521 | 43243 | 39.153 | -121.0774 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0129670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984971 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | SWITCH | 18760 | 20241030 | 2213 | 20241031 | 215 | 2608813 | 242 | Distribution Circuit | Equipment Failure/Involved | Underground | 38 | 9196 | 38.6961 | -120.832 | No | Overcast;32-90 F | Connector or Splice (UG) | Deteriorated | 24-0129787 | UG | Sus | 35539771 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984998 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20241031 | 204 | 20241031 | 500 | 2608936 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 9464 | 38.9463 | -121.2467 | No | Overcast-Rain;32-90 F | Insulator | Arcing | 24-0129830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1985026 | 0 | EPSS Ckt | Y | 2024 | A & B
SIERRA | PLACER | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20241031 | 437 | 20241101 | 2053 | 2610805 | 2416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 343 | 58369 | 38.8544 | -121.1507 | No | Overcast;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0130754 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1985627 | 0 | EPSS Ckt | Y | 2024 | B- GRD
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20241031 | 552 | 20241031 | 654 | 2609060 | 62 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 3472 | 38.9463 | -121.2467 | No | Overcast-Fog-Drizzle;32-90 F | Insulator | Arcing | 24-0129873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1985063 | 0 | EPSS Ckt | Y | 2024 | A+B
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 1700 | 20241031 | 823 | 20241031 | 1508 | 2609210 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 426 | 59130 | 39.2034 | -121.0788 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0129932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1985115 | 0 | EPSS Ckt | Y | 2024 | N/A
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20241031 | 1213 | 20241031 | 1429 | 2609615 | 136 | Distribution Circuit | 3rd Party | Metallic Balloon | 324 | 35025 | 38.9276 | -121.2469 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0130115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1985266 | 0 | EPSS Ckt | Y | 2024 | B+C
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224071333622 | 20241101 | 923 | 20241101 | 1448 | 2610282 | 325 | Transformer only | Company Initiated | Coordination failure | 2 | 650 | 38.581 | -120.5768 | No | Clear;32-90 F | Fuse | Normal | 24-0130656 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985588 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222353156960 | 20241101 | 951 | 20241101 | 1351 | 2610213 | 240 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 240 | 39.2279 | -121.1701 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0130507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985537 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | TRANSFORMER | 222065449517 | 20241101 | 1209 | 20241101 | 1820 | 2610573 | 371 | Transformer only | Vegetation | Tree - bark fell into line | 2 | 742 | 39.0235 | -121.2734 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0130655 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1985587 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20241101 | 1918 | 20241101 | 2106 | 2610795 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 6048 | 38.9463 | -121.2467 | No | Overcast-Rain;32-90 F | Insulator | Arcing | 24-0130751 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985625 | 0 | EPSS Ckt | Y | 2024 | A - B
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 31361 | 20241101 | 2011 | 20241101 | 2029 | 2610828 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 450 | 39.2025 | -121.0781 | No | Overcast-Fog-Rain;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0130757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985631 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 818790 | 20241101 | 2211 | 20241101 | 2248 | 2610894 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 2072 | 38.9463 | -121.2467 | No | Overcast-Rain;32-90 F | Insulator | Arcing | 24-0130772 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985646 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | BELL-1109 | 152701109 | RECLOSER | 1704 | 20241101 | 2312 | 20241102 | 348 | 2610957 | 276 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2818 | 211418 | 38.9945 | -121.026 | No | Overcast-Drizzle;32-90 F |  |  | 24-0130786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985657 | 0 | EPSS Ckt | Y | 2024 | A-C- INST
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20241101 | 2348 | 20241102 | 325 | 2610980 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 324 | 57176 | 38.9276 | -121.2469 | No | Overcast-Drizzle;32-90 F | Insulator | Arcing | 24-0130789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985659 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20241102 | 446 | 20241102 | 1539 | 2611195 | 653 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 19590 | 39.4553 | -121.053 | No | Overcast-Drizzle;32-90 F |  |  | 24-0130829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985691 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 2070 | 20241102 | 554 | 20241102 | 818 | 2611243 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 324 | 45852 | 38.9276 | -121.2469 | No | Overcast;32-90 F | Insulator | Arcing | 24-0130836 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985700 | 0 | EPSS Ckt | Y | 2024 | A-B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 20241102 | 646 | 20241102 | 1013 | 2611292 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3691 | 247443 | 38.9144 | -121.0197 | No | Overcast-Fog;32-90 F |  |  | 24-0130842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985710 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | RECLOSER | 1402 | 20241102 | 1021 | 20241102 | 1415 | 2611605 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 957 | 43337 | 38.7201 | -120.861 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0130931 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985832 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 81390 | 20241102 | 1143 | 20241102 | 1439 | 2611666 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 913 | 158972 | 38.8008 | -120.9078 | No | Overcast;32-90 F | Bushing | Burned/flashed | 24-0130951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985845 | 0 | EPSS Ckt | Y | 2024 | A GRD
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 790081 | 20241102 | 1455 | 20241102 | 1602 | 2611794 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 134 | 38.7683 | -120.8953 | No | Partly Cloudy;32-90 F |  |  | 24-0131003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985888 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 6765 | 20241102 | 1552 | 20241102 | 1714 | 2611815 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 984 | 39.4912 | -121.0862 | No | Partly Cloudy;32-90 F |  |  | 24-0131021 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985896 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2109 | 152582109 | RECLOSER | 75802 | 20241103 | 607 | 20241103 | 729 | 2612163 | 82 | Distribution Circuit | Animal | Bird found | 2832 | 232224 | 38.8488 | -121.2315 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0131083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985947 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | EL DORADO | SHINGLE SPRINGS-2105 | 153652105 | RECLOSER | 51738 | 20241103 | 825 | 20241104 | 1319 | 2612250 | 1734 | Distribution Circuit | Equipment Failure/Involved | Underground | 2211 | 407082 | 38.6795 | -120.9797 | No | Clear;32-90 F | Conductor- Underground | Broken | 24-0131094 | UG | Sus | 46378726 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985960 | 0 | EPSS Ckt | Y | 2024 | B GRD
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 21093 | 20241103 | 834 | 20241103 | 911 | 2612258 | 37 | Distribution Circuit | Animal | Squirrel | 21 | 777 | 38.73 | -120.7919 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0131098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985965 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 4989 | 20241103 | 923 | 20241103 | 931 | 2612255 | 8 | Distribution Circuit | Animal | Bird found | 29 | 235 | 38.7862 | -121.2501 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0131102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985971 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 904574 | 20241103 | 1047 | 20241104 | 349 | 2612344 | 1022 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 100186 | 39.2679 | -121.0209 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1985985 | 0 | EPSS Ckt | N | 2024 | SGF DCD
SIERRA | PLACER | DEL MAR-2109 | 152582109 | FUSE | 37433 | 20241103 | 1127 | 20241103 | 1329 | 2612494 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1220 | 38.849 | -121.2316 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 24-0131083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986002 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20241103 | 1454 | 20241103 | 1758 | 2612577 | 184 | Distribution Circuit | Animal | Bird found | 1563 | 165540 | 38.8326 | -120.8175 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131155 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986021 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 34655 | 20241103 | 1527 | 20241103 | 1654 | 2612610 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2175 | 38.7488 | -121.177 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131175 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986028 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1107 | 152481107 | FUSE | 7281 | 20241103 | 1805 | 20241104 | 301 | 2612686 | 536 | Distribution Circuit | 3rd Party | Vehicle | 85 | 19707 | 39.2169 | -121.0516 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986042 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 30659 | 20241103 | 1825 | 20241104 | 1314 | 2612702 | 1129 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4610 | 38.9082 | -121.1046 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0131212 | OH | Sus | 46379951 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1986043 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20241104 | 618 | 20241104 | 935 | 2612892 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1563 | 185815 | 38.8326 | -120.8175 | No | Clear;32-90 F |  |  | 24-0131233 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986072 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJS 1 SPAN SS OF CGC 223741240078 | 20241104 | 828 | 20241104 | 1220 | 2612977 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 232 | 38.7593 | -120.6908 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0131271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986100 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | OCB | 1104/2 | 20241104 | 828 | 20241105 | 229 | 2613036 | 1081 | Distribution Circuit | Equipment Failure/Involved | Underground | 2710 | 398458 | 39.2314 | -121.0346 | No | Clear;32-90 F | Switch (UG) | Burned/flashed | 24-0131290 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986146 | 1 | EPSS Ckt | Y | 2024 | B GRD INST OC
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | TRANSFORMER | 222794859362 | 20241104 | 954 | 20241104 | 1028 | 2613175 | 34 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 34 | 39.2926 | -121.0136 | No | Clear;32-90 F |  |  | 24-0131382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1986277 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | SWITCH | 1501 | 20241104 | 1155 | 20241104 | 1209 | 2613346 | 14 | Distribution Circuit | Company Initiated | Other Circuits | 1859 | 25764 | 39.1026 | -120.959 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0107370 | OH | Sus | 35506945 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1986297 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20241104 | 1724 | 20241104 | 2318 | 2613681 | 354 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 70950 | 38.8964 | -121.1202 | No | Clear;32-90 F |  |  | 24-0131679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986377 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 20241105 | 2220 | 20241106 | 619 | 2615034 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1044 | 122076 | 38.8435 | -120.8737 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132298 | OH | Sus | 31716514 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986822 | 0 | EPSS Ckt | Y | 2024 | A/C
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 20241106 | 16 | 20241106 | 1242 | 2615249 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 2827 | 556689 | 38.7716 | -120.8148 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132316 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986879 | 0 | EPSS Ckt | Y | 2024 | LINE TO GRD
SIERRA | PLACER | TAMARACK-1101 | 152291101 | TRANSFORMER | 100000044460 | 20241106 | 619 | 20241106 | 1600 | 2616548 | 581 | Transformer only | Vegetation | Tree - fell into line | 1 | 581 | 39.3287 | -120.4001 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 24-0132614 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1987228 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20241106 | 633 | 20241106 | 937 | 2615685 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 605 | 46682 | 39.5596 | -120.8241 | No | Partly Cloudy;Below 32 F |  |  | 24-0132389 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986964 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | TAMARACK-1101 | 152291101 | FUSE | 6611 | 20241106 | 753 | 20241106 | 1332 | 2615822 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 9831 | 39.3192 | -120.432 | No | Clear;Below 32 F | Conductor- Overhead | Normal | 24-0132622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1987231 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 85766 | 20241106 | 758 | 20241106 | 820 | 2615886 | 22 | Distribution Circuit | Company Initiated | Personnel- company | 1118 | 24596 | 38.8027 | -120.9071 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0101507 | OH | Sus | 35293675 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987033 | 1 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | BELL-1109 | 152701109 | RECLOSER | 724884 | 20241106 | 842 | 20241106 | 921 | s2002875 | 39 | Distribution Circuit | Company Initiated | Personnel- company | 2696 | 105144 | 38.9512 | -121.0773 | No | Clear;32-90 F | Jumper | Normal | 24-0128388 | OH | Sus | 35091142 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 2002875 | 0 | EPSS Ckt | Y | 2024 | SGF
SIERRA | PLACER | PLACER-1104 | 152461104 | RECLOSER | 676064 | 20241106 | 1008 | 20241106 | 1100 | 2616544 | 52 | Distribution Circuit | Company Initiated | Personnel- company | 71 | 3692 | 38.9974 | -120.9795 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987196 | 1 | EPSS Ckt | Y | 2024 | C
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | FUSE | 40927 | 20241106 | 1658 | 20241106 | 1744 | 2617171 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 168 | 38.8123 | -121.3071 | No | Clear;32-90 F |  |  | 24-0132878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987324 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJS LINE & BUCK @ CGC 222649061475 | 20241106 | 1818 | 20241106 | 2221 | 2617229 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 39.3509 | -121.064 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132887 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987326 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20241106 | 2336 | 20241107 | 508 | 2617345 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 73040 | 38.8964 | -121.1202 | No | Clear;32-90 F |  |  | 24-0132928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987356 | 0 | EPSS Ckt | Y | 2024 | DCD
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 878418 | 20241107 | 1052 | 20241107 | 1113 | 2617838 | 21 | Distribution Circuit | Company Initiated | Personnel- company | 82 | 1722 | 38.6606 | -120.9901 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1987547 | 0 | EPSS Ckt | Y | 2024 | A C
SIERRA | PLACER | PLACER-1104 | 152461104 | SWITCH | 2263 | 20241107 | 1157 | 20241107 | 1648 | 2617920 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2619 | 39.0001 | -120.9965 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987561 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | RECLOSER | 2054 | 20241107 | 1743 | 20241107 | 2321 | 2618204 | 338 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 60687 | 38.8964 | -121.1202 | No | Clear;32-90 F |  |  | 24-0133295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987622 | 1 | EPSS Ckt | Y | 2024 | DCD
SIERRA | PLACER | DEL MAR-2109 | 152582109 | OTHER | T8838 TWD T8839 | 20241107 | 2223 | 20241107 | 2333 | 2618305 | 70 | Distribution Circuit | Equipment Failure/Involved | Underground | 24 | 1680 | 38.8483 | -121.2611 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0133343 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987655 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | RECLOSER | 164068 | 20241108 | 622 | 20241108 | 1040 | 2618364 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1102 | 202294 | 38.9466 | -121.0478 | No | Clear;32-90 F |  |  | 24-0133382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1987675 | 0 | EPSS Ckt | Y | 2024 | a-c
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 836878 | 20241108 | 640 | 20241108 | 1608 | 2618410 | 568 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4908 | 1446145 | 38.7371 | -120.6759 | No | Clear;32-90 F |  |  | 24-0133388 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987678 | 0 | EPSS Ckt | Y | 2024 | DCD
SIERRA | PLACER | PENRYN-1105 | 152561105 | FUSE | 8783 | 20241108 | 951 | 20241108 | 1348 | 2618718 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3318 | 38.8577 | -121.1788 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0133490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987844 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1106 | 152571106 | FUSE | 7095 | 20241108 | 1323 | 20241108 | 1541 | 2619117 | 138 | Distribution Circuit | Vegetation | Tree - grew into line | 27 | 3726 | 38.7525 | -121.2046 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133620 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987913 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | TRANSFORMER | 222489046900 | 20241108 | 1810 | 20241109 | 210 | 2619342 | 480 | Distribution Circuit | 3rd Party | Vehicle | 138 | 57400 | 38.9508 | -121.1259 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987951 | 0 | EPSS Ckt | Y | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | RECLOSER | 95756 | 20241109 | 623 | 20241109 | 844 | 2619461 | 141 | Distribution Circuit | Animal | Bird found | 274 | 38602 | 38.887 | -121.2381 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133762 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1987993 | 0 | EPSS Ckt | Y | 2024 | B-C
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 41237 | 20241109 | 856 | 20241109 | 1022 | 2619662 | 86 | Distribution Circuit | Animal | Bird found | 1 | 86 | 39.1771 | -121.0909 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0133797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1988055 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | RECLOSER | 19572 | 20241109 | 1343 | 20241109 | 1533 | 2619832 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 379 | 41690 | 38.6042 | -121.0549 | No | Clear;32-90 F |  |  | 24-0133839 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988102 | 0 | EPSS Ckt | Y | 2024 | C GRD
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 31467 | 20241109 | 1740 | 20241110 | 6 | 2619943 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5018 | 39.1254 | -121.0845 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0133856 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1988119 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20241110 | 806 | 20241110 | 1043 | 2620105 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 467 | 41464 | 39.0351 | -121.0957 | No | Clear;32-90 F |  |  | 24-0133895 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1988175 | 0 | EPSS Ckt | Y | 2024 | B-C INST OC TGT
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 2768 | 20241110 | 1111 | 20241110 | 1302 | 2620181 | 111 | Distribution Circuit | Animal | Squirrel | 184 | 20424 | 39.1028 | -120.96 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133926 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988200 | 0 | EPSS Ckt | Y | 2024 | A AND GRD
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222668355302 | 20241110 | 1338 | 20241110 | 1709 | 2620235 | 211 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 2 | 422 | 39.1811 | -121.0593 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0133962 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988230 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 290705 | 20241110 | 1339 | 20241110 | 1419 | 2620236 | 40 | Distribution Circuit | Animal | Squirrel | 166 | 6640 | 38.687 | -120.8138 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133941 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1988212 | 0 | EPSS Ckt | Y | 2024 | B AND C
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | RECLOSER | 2766 | 20241110 | 1645 | 20241110 | 2129 | 2620295 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 13632 | 39.1981 | -121.0559 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0133951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1988233 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | OTHER | 927328 | 20241111 | 712 | 20241111 | 1111 | 2620482 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 15954 | 38.8205 | -120.0758 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0134020 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | Yes | No | 1988300 | 0 | EPSS Ckt | Y | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223707834685 | 20241111 | 1054 | 20241111 | 1435 | 2620864 | 221 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 442 | 38.612 | -120.7036 | No | Rain-Overcast-Fog;32-90 F | Transformer | Broken | 24-0134133 | OH | Sus | 46386995 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988442 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | RECLOSER | 1010 | 20241111 | 1108 | 20241111 | 1252 | 2620909 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 676 | 45704 | 39.2129 | -121.0129 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0134105 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1988412 | 0 | EPSS Ckt | Y | 2024 | A B
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20241111 | 1205 | 20241111 | 1831 | 2621066 | 386 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 805 | 172830 | 38.8695 | -121.02 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Steel | Burned/flashed | 24-0134123 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988434 | 0 | EPSS Ckt | Y | 2024 | C & GRD
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | OCB | 1109/2 | 20241111 | 1302 | 20241111 | 1522 | 2621163 | 140 | Distribution Circuit | Equipment Failure/Involved | Underground | 599 | 83860 | 38.7313 | -120.784 | No | Overcast-Fog-Rain;32-90 F | Elbow | Failed/Faulted | 24-0134140 | UG | Sus | 46387481 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988451 | 0 | EPSS Ckt | Y | 2024 | B GRD INSTA
SIERRA | EL DORADO | ECHO SUMMIT-1101 | 158031101 | TRANSFORMER | 225488142566 | 20241111 | 1309 | 20241111 | 1852 | 2621168 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1372 | 38.8193 | -120.0747 | No | Overcast-Fog-Snow;32-90 F | Fuse | Normal | 24-0134313 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988614 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 50324 | 20241111 | 1931 | 20241112 | 218 | 2622106 | 407 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1965 | 423633 | 38.6953 | -120.818 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0134326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1988626 | 0 | EPSS Ckt | Y | 2024 | A B INST
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20241112 | 806 | 20241112 | 2117 | 2622413 | 791 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1457 | 68248 | 38.8931 | -120.9977 | No | Fog;32-90 F | Pole-Wood | Burned/flashed | 24-0134475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1988804 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 37327 | 20241112 | 923 | 20241112 | 1233 | 2622655 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1140 | 38.8356 | -121.0996 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0134508 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1988885 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | FUSE | 22405 | 20241112 | 930 | 20241112 | 1042 | 2622688 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 72 | 38.6368 | -121.0591 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0134511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1988902 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | TRANSFORMER | 222715954111 | 20241112 | 934 | 20241112 | 1952 | 2622925 | 618 | Distribution Circuit | Animal | Squirrel | 9 | 5158 | 39.1485 | -121.0437 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0134598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1988998 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222856255570 | 20241112 | 1126 | 20241112 | 1132 | 2622923 | 6 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 12 | 39.1881 | -120.9933 | No | Clear;32-90 F | Secondary | Normal | 24-0134618 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989011 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | JUMPER | OJ'S 1 SPAN NW/OF 1261 | 20241112 | 1130 | 20241112 | 1512 | 2622937 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 222 | 39.0457 | -121.0769 | No | Clear;32-90 F | Switch (OH) | Failed/Faulted | 24-0134481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989003 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | RECLOSER | 2706 | 20241112 | 1453 | 20241112 | 1720 | 2623177 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 377 | 31421 | 38.8101 | -121.1629 | No | Clear;32-90 F |  |  | 24-0134754 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1989064 | 0 | EPSS Ckt | Y | 2024 | AC
SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 38371 | 20241112 | 2325 | 20241113 | 258 | 2623476 | 213 | Distribution Circuit | Company Initiated | Other Circuits | 24 | 5112 | 39.4746 | -121.033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0134875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989133 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 38311 | 20241113 | 731 | 20241113 | 856 | 2623602 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1134 | 38.897 | -121.433 | No | Partly Cloudy;32-90 F |  |  | 24-0134947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1989218 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | TRANSFORMER | 222321851299 | 20241113 | 1742 | 20241113 | 1842 | 2624341 | 60 | Transformer only | 3rd Party | Vehicle | 1 | 60 | 39.0752 | -121.1842 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0135301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1989471 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30353 | 20241114 | 631 | 20241114 | 818 | 2624644 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1498 | 39.1214 | -121.0293 | No | Overcast-Fog;32-90 F |  |  | 24-0135372 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1989539 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | FUSE | 30587 | 20241114 | 916 | 20241114 | 1018 | 2624882 | 62 | Distribution Circuit | Company Initiated | Improper Construction | 1 | 62 | 38.9781 | -121.1075 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0135424 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989663 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | SWITCH | 687818 | 20241115 | 151 | 20241115 | 1258 | 2625524 | 667 | Distribution Circuit | 3rd Party | Vehicle | 1209 | 37901 | 38.7627 | -120.5818 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0135752 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989852 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJ'S 1 SPAN SS OF CGC 222988545682 | 20241115 | 914 | 20241115 | 1312 | 2625821 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 952 | 38.9155 | -120.9503 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0135830 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989961 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 77546 | 20241115 | 1847 | 20241116 | 1128 | 2626421 | 1001 | Distribution Circuit | 3rd Party | Vehicle | 429 | 73024 | 38.5709 | -120.7329 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0136124 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1990141 | 0 | EPSS Ckt | N | 2024 | C GRD
SIERRA | PLACER | PENRYN-1107 | 152561107 | TRANSFORMER | 222474141295 | 20241115 | 2153 | 20241115 | 2345 | 2626464 | 112 | Transformer only | 3rd Party | Vehicle | 1 | 112 | 38.7978 | -121.1327 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1990155 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7851 | 20241115 | 2335 | 20241116 | 153 | 2626481 | 138 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 12420 | 39.2048 | -121.0925 | No | Clear;32-90 F |  |  | 24-0136144 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1990159 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-2106 | 152582106 | TRANSFORMER | T10741 | 20241116 | 509 | 20241116 | 1340 | 2626524 | 511 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 4088 | 38.7995 | -121.2115 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0136156 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990174 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 8655 | 20241116 | 630 | 20241116 | 914 | 2626771 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1312 | 38.7907 | -121.1639 | No | Clear;32-90 F |  |  | 24-0136189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1990243 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | SWITCH | 34961 | 20241116 | 1114 | 20241116 | 1812 | 2626969 | 418 | Distribution Circuit | 3rd Party | Vehicle | 269 | 80605 | 38.7964 | -121.1425 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136201 | OH | Sus | 35598180 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990275 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5165 | 20241117 | 1005 | 20241117 | 1140 | 2627397 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1045 | 39.0448 | -121.1718 | No | Overcast;32-90 F | Insulator | Broken | 24-0136305 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990368 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20267 | 20241117 | 2236 | 20241117 | 2346 | 2627700 | 70 | Distribution Circuit | 3rd Party | Vehicle | 3 | 210 | 38.5943 | -120.8471 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0136371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1990435 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | FUSE | 7817 | 20241118 | 634 | 20241118 | 814 | 2627830 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 9000 | 39.1527 | -121.1348 | No | Fog;32-90 F |  |  | 24-0136403 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1990483 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 2 SP S/SIDE OF CGC# 223014056380 | 20241118 | 815 | 20241118 | 1200 | 2628214 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 676 | 24772 | 39.2103 | -120.939 | No | Clear;32-90 F | Jumper | Burned Open | 24-0136512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1990642 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222766055054 | 20241118 | 1107 | 20241120 | 30 | 2628246 | 2243 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2243 | 39.1741 | -121.0254 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0137326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991085 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 31627 | 20241118 | 1155 | 20241118 | 1448 | 2628279 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1730 | 38.9244 | -121.377 | No | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0136560 | OH | Sus | 46390933 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990659 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20241118 | 1504 | 20241118 | 1529 | 2628492 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 3075 | 38.8326 | -120.8175 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0136710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990713 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20241119 | 632 | 20241119 | 750 | 2628798 | 78 | Distribution Circuit | Animal | Squirrel | 43 | 3354 | 38.748 | -121.4698 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0136870 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1990784 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 183495 | 20241119 | 832 | 20241119 | 1257 | 2628939 | 265 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 89 | 23585 | 38.6733 | -120.8368 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0136919 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990838 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OJS 1 SPAN LD SIDE OF CGC 221832346925 | 20241119 | 937 | 20241119 | 1254 | 2629115 | 197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 197 | 38.9531 | -121.3569 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0136977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1990964 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | JUMPER | OJ 1 SPAN SS OF CGC 221701342995 | 20241119 | 1432 | 20241119 | 1522 | 2629490 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 250 | 38.846 | -121.4032 | No | Overcast;32-90 F | Conductor- Overhead | Deteriorated | 24-0137233 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991060 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | JUMPER | OJ AT CGC 223088558560 | 20241119 | 2108 | 20241120 | 219 | 2629878 | 311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 13995 | 39.2688 | -120.9103 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 24-0137390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991130 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | RECLOSER | 556218 | 20241119 | 2326 | 20241120 | 1247 | 2629939 | 801 | Distribution Circuit | 3rd Party | Vehicle | 649 | 114214 | 38.6342 | -120.9454 | No | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0137404 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | Yes | No | 1991143 | 0 | EPSS Ckt | N | 2024 | ABC
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | 3 SPANS N/O TX CGC 223441037065 | 20241120 | 830 | 20241120 | 1009 | 2630327 | 99 | Distribution Circuit | Environmental/External | Flood/Erosion | 4 | 396 | 38.679 | -120.7946 | No | Overcast;32-90 F | Other | Broken | 24-0137535 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991260 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | WIRE DOWN | 20241120 | 932 | 20241120 | 1333 | 2630560 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 871 | 786 | 39.1927 | -120.9669 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137622 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | Yes | 1991352 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7007 | 20241120 | 937 | 20241120 | 1756 | 2630484 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 4434 | 39.2127 | -120.9877 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137645 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991366 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 8327 | 20241120 | 1005 | 20241120 | 1049 | 2630536 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 2024 | 39.2447 | -121.07 | No | Overcast-Rain;32-90 F | Fuse | Arcing | 24-0137615 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991343 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 7023 | 20241120 | 1029 | 20241120 | 1813 | 2630540 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 31552 | 39.1271 | -121.0556 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137649 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991369 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | OTHER | WIRE DOWN 1 SS OF CGC 222864056049 | 20241120 | 1030 | 20241120 | 2145 | 2630799 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2940 | 39.202 | -120.99 | No | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0137688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | Yes | 1991392 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 31377 | 20241120 | 1059 | 20241120 | 1718 | 2630694 | 379 | Distribution Circuit | Company Initiated | Improper Construction | 38 | 14402 | 39.0323 | -121.0725 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Together | 24-0137733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991419 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 9509 | 20241120 | 1103 | 20241120 | 1336 | 2630699 | 153 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 5613 | 39.011 | -120.9956 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0137770 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991443 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 20241120 | 1105 | 20241120 | 1454 | 2630713 | 229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 9160 | 39.0098 | -120.8455 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0137759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991434 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222758955081 | 20241120 | 1137 | 20241120 | 1708 | 2630883 | 331 | Transformer only | Vegetation | Tree - fell into line | 1 | 331 | 39.1748 | -121.028 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0137741 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991423 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | OTHER | WIRE HANGING ON XARM AT 11675 DOG BAR RD | 20241120 | 1143 | 20241120 | 2121 | 2630869 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 982 | 81769 | 39.158 | -121.0401 | No | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken | 24-0137722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1991413 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 3675 | 20241120 | 1143 | 20241120 | 1353 | 2630868 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2048 | 39.0552 | -121.1498 | No | Partly Cloudy;32-90 F |  |  | 24-0137783 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991450 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | TRANSFORMER | 222773850977 | 20241120 | 1150 | 20241120 | 1804 | 2630921 | 374 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 374 | 39.0611 | -121.0232 | No | Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 24-0137842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991478 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33807 | 20241120 | 1224 | 20241120 | 1332 | 2630980 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 680 | 39.1998 | -120.9932 | No | Overcast-Rain;32-90 F |  |  | 24-0137808 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991461 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRANSFORMER | 222648149702 | 20241120 | 1320 | 20241120 | 1947 | 2631139 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1386 | 39.0279 | -121.0689 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0137881 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991505 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9997 | 20241120 | 1353 | 20241120 | 1447 | 2631259 | 54 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 5763 | 39.2563 | -120.9688 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0137873 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991502 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5811 | 20241120 | 1432 | 20241120 | 1920 | 2631373 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 16416 | 38.8819 | -120.8303 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991553 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | SWITCH | 5513 | 20241120 | 1434 | 20241120 | 1515 | 2631380 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 401 | 16441 | 38.6776 | -120.9432 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 24-0137690 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991493 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ'S 1 SPAN SS OF CGC 222847549078 | 20241120 | 1600 | 20241120 | 1701 | 2631547 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 305 | 39.0089 | -120.9987 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0137947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991546 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 7339 | 20241120 | 1624 | 20241120 | 1633 | 2631434 | 9 | Distribution Circuit | Animal | Squirrel | 1 | 12 | 39.0186 | -120.8773 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0137981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991561 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222631048590 | 20241120 | 1713 | 20241120 | 1814 | 2631667 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 38.9968 | -121.0753 | No | Partly Cloudy-Rain;32-90 F | Fuse | Broken | 24-0138038 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991599 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ 4 SPANS SS OF CGC 223443036455 | 20241120 | 1758 | 20241120 | 1807 | 2631723 | 9 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9 | 38.6622 | -120.7925 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0138030 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991594 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1104 | 152691104 | OCB | 1104/2 | 20241120 | 1919 | 20241120 | 2021 | 2631833 | 62 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3636 | 225432 | 39.0444 | -121.0911 | No | Overcast-Rain;32-90 F | Insulator | Burned/flashed | 24-0138057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991609 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6429 | 20241120 | 2051 | 20241120 | 2241 | 2631926 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1430 | 39.2069 | -120.8114 | No | Overcast-Rain;32-90 F |  |  | 24-0138108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991653 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 8343 | 20241121 | 350 | 20241121 | 1047 | 2632206 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 12510 | 39.2242 | -121.1949 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0138174 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991717 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20241121 | 737 | 20241121 | 908 | 2632337 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 455 | 38.8986 | -120.8986 | No | Overcast-Rain;32-90 F |  |  | 24-0138263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991756 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1101 | 152061101 | JUMPER | OJS 1 SPAN SS OF 5969 | 20241121 | 946 | 20241121 | 1420 | 2632524 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2192 | 38.7848 | -121.2197 | No | Overcast-Rain;32-90 F | Pole-Wood | Deteriorated | 24-0138306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991785 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 12989 | 20241121 | 1036 | 20241121 | 1129 | 2632574 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 1802 | 38.7478 | -120.8205 | No | Overcast-Drizzle;32-90 F | Woodpin | Broken | 24-0138327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991802 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 8191 | 20241121 | 1424 | 20241121 | 1448 | 2632989 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 1272 | 39.2059 | -121.0385 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0138538 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991895 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 33123 | 20241121 | 1733 | 20241121 | 1821 | 2633227 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 672 | 39.2557 | -121.0274 | No | Overcast-Rain;32-90 F | Insulator | Failed/Faulted | 24-0138640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991931 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18747 | 20241121 | 1800 | 20241121 | 2041 | 2633237 | 161 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 58 | 9338 | 38.5601 | -120.8471 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0138653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991935 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | T280922 | 20241121 | 1807 | 20241122 | 1024 | 2633252 | 977 | Distribution Circuit | Equipment Failure/Involved | Underground | 8 | 2614 | 38.8878 | -120.9875 | No | Overcast;32-90 F | Transformer (UG) | Failed/Faulted | 24-0138685 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991948 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2426 | 20241122 | 1059 | 20241122 | 1136 | 2634339 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2115 | 78255 | 39.2042 | -121.2005 | No | Overcast-Heavy Rain;32-90 F |  |  | 24-0138952 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | No | No | 1992138 | 0 | EPSS Ckt | N | 2024 | A-B-C
SIERRA | PLACER | PENRYN-1105 | 152561105 | TRANSFORMER | 222363143318 | 20241122 | 1550 | 20241122 | 1604 | 2634956 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 98 | 38.853 | -121.1712 | No | Partly Cloudy-Heavy Rain;32-90 F | Connector or Splice (OH) | Burned/flashed | 24-0139170 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992222 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223522638310 | 20241122 | 1730 | 20241122 | 2054 | 2635151 | 204 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 204 | 38.7127 | -120.7665 | No | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0139291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1992302 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 3065 | 20241122 | 1806 | 20241122 | 2000 | 2635190 | 114 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 2394 | 39.2546 | -121.0124 | No | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 24-0139252 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992271 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3911 | 20241122 | 1808 | 20241123 | 1313 | 2635438 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5725 | 39.3625 | -121.1126 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1992298 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | OTHER | PRI NEUT ON GRD | 20241122 | 1825 | 20241123 | 1126 | 2635413 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 1645 | 62479 | 39.2578 | -121.2074 | No | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139277 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | Yes | No | 1992290 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222072556100 | 20241122 | 1826 | 20241123 | 1109 | 2635220 | 1003 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1118 | 39.2045 | -121.2699 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139330 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992337 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 32679 | 20241122 | 1839 | 20241123 | 953 | 2635257 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5484 | 39.2849 | -121.0599 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139289 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1992299 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 3971 | 20241122 | 1901 | 20241122 | 2054 | 2635367 | 113 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 2373 | 39.3164 | -120.9742 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0139310 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992318 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7065 | 20241122 | 2023 | 20241122 | 2100 | 2635425 | 37 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 1924 | 39.1869 | -120.9556 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0139306 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992314 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20241122 | 2120 | 20241123 | 1218 | 2635545 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 899 | 73573 | 39.2082 | -121.2033 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0139318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | Yes | No | 1992325 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 290705 | 20241122 | 2127 | 20241122 | 2337 | 2635560 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 18400 | 38.687 | -120.8138 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0139337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992344 | 0 | EPSS Ckt | N | 2024 | BC
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11425 | 20241122 | 2146 | 20241123 | 113 | 2635582 | 207 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 2070 | 38.6859 | -120.6469 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0139365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992371 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21149 | 20241122 | 2154 | 20241123 | 1420 | 2635721 | 986 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 11832 | 38.6069 | -120.7093 | No | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1992377 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 8597 | 20241122 | 2157 | 20241123 | 815 | 2635608 | 618 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 31 | 19158 | 38.8189 | -121.1641 | No | Clear;32-90 F |  |  | 24-0139341 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992349 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13739 | 20241122 | 2201 | 20241123 | 401 | 2635581 | 360 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 16560 | 38.6002 | -120.6709 | No | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0139390 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992396 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20241122 | 2213 | 20241123 | 1340 | 2635575 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10197 | 38.6945 | -120.6389 | No | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0139345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992353 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224015340022 | 20241122 | 2223 | 20241123 | 225 | 2635622 | 242 | Transformer only | Unknown Cause | Patrol - found nothing | 9 | 2178 | 38.7572 | -120.5923 | No | Overcast-Drizzle;32-90 F |  |  | 24-0139380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1992386 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 7955 | 20241122 | 2226 | 20241123 | 102 | 2635624 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 2652 | 39.1037 | -121.0819 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992368 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 224221335881 | 20241122 | 2229 | 20241123 | 355 | 2635635 | 326 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 326 | 38.6432 | -120.5224 | No | Clear;32-90 F |  |  | 24-0139392 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1992399 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223651137866 | 20241123 | 645 | 20241123 | 817 | 2635887 | 92 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 92 | 38.6995 | -120.7219 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Failed/Faulted | 24-0139436 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992443 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 6851 | 20241123 | 646 | 20241123 | 1221 | 2635888 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2345 | 38.8972 | -121.2451 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139447 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1992455 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 20241123 | 906 | 20241123 | 1028 | 2635948 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1640 | 38.8528 | -120.789 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992463 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | RECLOSER | 556218 | 20241123 | 1835 | 20241124 | 822 | 2636612 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 649 | 107362 | 38.6342 | -120.9454 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | Yes | No | 1992570 | 0 | EPSS Ckt | N | 2024 | A-B-C TIME OC
SIERRA | PLACER | BELL-1109 | 152701109 | RECLOSER | 724884 | 20241123 | 2056 | 20241124 | 1340 | 2636716 | 1004 | Distribution Circuit | 3rd Party | Vehicle | 370 | 127713 | 38.9512 | -121.0773 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0139625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Multi-Fault | 0 | No | Yes | No | 1992582 | 0 | EPSS Ckt | N | 2024 | B- C -SGF
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 30255 | 20241124 | 806 | 20241124 | 1037 | 2636869 | 151 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4530 | 39.2698 | -121.1136 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0139672 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1992629 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | ECHO SUMMIT SUB | 15803 | OTHER | ECHO SUMMIT | 20241124 | 1150 | 20241124 | 1217 | 2637015 | 27 | Distribution Circuit | 3rd Party | Other | 309 | 8343 | 0 | 0 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0139704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1992647 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222853162904 | 20241124 | 1152 | 20241124 | 1720 | 2637013 | 328 | Transformer only | 3rd Party | Other | 1 | 328 | 39.3897 | -120.9918 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0139728 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992664 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33223 | 20241124 | 1158 | 20241124 | 1252 | 2637021 | 54 | Distribution Circuit | Animal | Squirrel | 7 | 378 | 39.1208 | -120.953 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0139714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992653 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 481660 | 20241124 | 1309 | 20241124 | 1433 | 2637044 | 84 | Distribution Circuit | 3rd Party | Other | 40 | 3360 | 38.8107 | -120.0318 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0139704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1992658 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 166282 | 20241124 | 1627 | 20241124 | 2000 | 2637147 | 213 | Distribution Circuit | 3rd Party | Vehicle | 330 | 51075 | 39.068 | -121.0335 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Burned/flashed | 24-0139754 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1992680 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 6623 | 20241125 | 254 | 20241125 | 504 | 2637290 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 1820 | 38.6876 | -120.638 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0139808 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992705 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222329656501 | 20241125 | 1259 | 20241125 | 1650 | 2637756 | 231 | Transformer only | Animal | Bird found | 2 | 462 | 39.2154 | -121.1786 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 24-0140038 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992795 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 9465 | 20241126 | 18 | 20241126 | 757 | 2638156 | 459 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 4131 | 38.9175 | -121.2469 | No | Overcast-Fog;32-90 F |  |  | 24-0140285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992908 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15355 | 20241126 | 650 | 20241126 | 810 | 2638267 | 80 | Distribution Circuit | Animal | Bird found | 2 | 160 | 38.9847 | -121.3617 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0140287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992912 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18819 | 20241126 | 1033 | 20241126 | 1155 | 2638587 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 4592 | 38.7042 | -120.8417 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0140475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1993008 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DEL MAR-1103 | 152581103 | TRANSFORMER | 222304541278 | 20241127 | 729 | 20241127 | 859 | 2639140 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 90 | 38.7964 | -121.1925 | No | Clear;32-90 F |  |  | 24-0140829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | None | 0 | No | No | No | 1993126 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 4763 | 20241127 | 945 | 20241127 | 1403 | 2639268 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 7998 | 39.0194 | -121.0298 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0140913 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1993157 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | JUMPER | BURNED OPEN JUMPERS | 20241127 | 2308 | 20241128 | 446 | 2639721 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 12844 | 39.2125 | -121.1785 | No | Clear;32-90 F | Jumper | Burned Open | 24-0141177 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1993222 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | FUSE | 5727 | 20241128 | 255 | 20241128 | 1415 | 2639740 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 4856 | 39.0189 | -121.0519 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1993226 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | RECLOSER | 1020 | 20241128 | 512 | 20241128 | 1054 | 2639752 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 486 | 64594 | 39.2471 | -121.0378 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0141183 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1993228 | 0 | EPSS Ckt | N | 2024 | SGF
SIERRA | EL DORADO | PLACERVILLE-1111 | 153081111 | FUSE | 10479 | 20241130 | 1140 | 20241130 | 1202 | 2640582 | 22 | Distribution Circuit | Animal | Squirrel | 2 | 44 | 38.7223 | -120.8283 | No | Clear;32-90 F | Fuse | Burned Open | 24-0141397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1993411 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18477 | 20241130 | 1547 | 20241130 | 2319 | 2640810 | 452 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2712 | 38.7133 | -120.7118 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0141435 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | Yes | No | 1993430 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5777 | 20241130 | 1737 | 20241130 | 1845 | 2640851 | 68 | Distribution Circuit | Animal | Bird found | 2 | 136 | 39.0269 | -121.0979 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0141445 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1993433 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | TRANSFORMER | 222794547909 | 20241201 | 219 | 20241201 | 937 | 2640936 | 438 | Transformer only | Vegetation | Tree - fell into line | 1 | 438 | 38.978 | -121.0181 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 24-0141473 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1993452 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1107 | 152561107 | FUSE | 30383 | 20241201 | 1015 | 20241201 | 1143 | 2641004 | 88 | Distribution Circuit | Animal | Squirrel | 25 | 2200 | 38.8331 | -121.1214 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Burned/flashed | 24-0141506 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1993476 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 35369 | 20241202 | 1455 | 20241202 | 1715 | 2642149 | 91 | Distribution Circuit | Animal | Squirrel | 208 | 18928 | 39.238 | -120.9727 | No | Clear;32-90 F | Fuse | Burned Open | 24-0141901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1993802 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 81390 | 20241203 | 102 | 20241203 | 2047 | 2642407 | 1185 | Distribution Circuit | Equipment Failure/Involved | Underground | 333 | 261790 | 38.8008 | -120.9078 | No | Clear;32-90 F | Pothead/Riser Termination | Broken | 24-0141977 | UG | Sus | 46403203 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1993835 | 0 | EPSS Ckt | N | 2024 | A- GRD
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223689332093 | 20241203 | 1518 | 20241203 | 1618 | 2643042 | 60 | Transformer only | Animal | Squirrel | 1 | 60 | 38.5404 | -120.7112 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0142274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1994144 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222200557035 | 20241203 | 1604 | 20241204 | 245 | 2643190 | 641 | Transformer only | Equipment Failure/Involved | Underground | 1 | 641 | 39.23 | -121.2248 | No | Clear;32-90 F | Secondary | Broken | 24-0142349 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1994193 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7217 | 20241205 | 1202 | 20241205 | 1215 | 2644616 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 35 | 38.9994 | -121.4043 | No | Clear;32-90 F |  |  | 24-0142914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1994823 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1435 | 20241205 | 1355 | 20241205 | 1550 | 2645177 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2300 | 38.7507 | -120.7582 | No | Clear;32-90 F |  |  | 24-0143046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1994867 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20227 | 20241205 | 1544 | 20241205 | 1659 | 2645301 | 75 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1875 | 38.5771 | -120.8556 | No | Clear;32-90 F |  |  | 24-0143111 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1994890 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | TRANSFORMER | 222262357990 | 20241205 | 1620 | 20241206 | 1330 | 2645324 | 1270 | Transformer only | Vegetation | Tree - fell into line | 1 | 1270 | 39.2557 | -121.2017 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0143128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1994900 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | SWITCH | 610307 | 20241205 | 1630 | 20241205 | 1804 | 2645331 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 7896 | 39.2992 | -121.0399 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994884 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | JUMPER | 2 SPANS SS OF CGC 222841049960 | 20241205 | 1701 | 20241205 | 2110 | 2645335 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 498 | 39.0341 | -121.0023 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143101 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994885 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224028940280 | 20241208 | 946 | 20241208 | 1456 | 2646897 | 310 | Transformer only | Animal | Squirrel | 6 | 1860 | 38.7641 | -120.5885 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143706 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995479 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 30721 | 20241208 | 1158 | 20241208 | 1210 | 2646932 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 4 | 48 | 38.9502 | -121.0889 | No | Clear;32-90 F |  |  | 24-0143709 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995482 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222845057115 | 20241208 | 1209 | 20241208 | 2228 | 2646949 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1238 | 39.2304 | -120.9971 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0143724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995498 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224014039341 | 20241209 | 1254 | 20241209 | 1501 | 2647689 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 127 | 38.737 | -120.5938 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0143942 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995790 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 7339 | 20241209 | 1635 | 20241209 | 1828 | 2647976 | 113 | Distribution Circuit | Animal | Squirrel | 1 | 151 | 39.0186 | -120.8773 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0144027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995850 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 891 | 20241210 | 933 | 20241210 | 1433 | 2648585 | 300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1200 | 39.553 | -120.859 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0143889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996067 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1102 | 153701102 | OTHER | T7687 TWD T7686 | 20241210 | 1253 | 20241210 | 1356 | 2648920 | 63 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 1008 | 38.8812 | -121.3058 | No | Clear;32-90 F | Transformer (UG) | Leaking | 24-0144192 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996208 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJS @ FLYING BELLS 1 N/O CGC 222818056464 | 20241210 | 1319 | 20241210 | 1700 | 2648939 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2873 | 39.2129 | -121.0065 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0144226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996217 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20241210 | 1452 | 20241211 | 12 | 2649018 | 560 | Distribution Circuit | 3rd Party | Vehicle | 22 | 12320 | 39.1527 | -121.0381 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0144253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996233 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6187 | 20241210 | 1500 | 20241210 | 1603 | 2649043 | 63 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 144 | 9072 | 39.0605 | -120.984 | No | Partly Cloudy;32-90 F |  |  | 24-0144269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996243 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 7315 | 20241211 | 845 | 20241211 | 1038 | 2649451 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1469 | 38.9277 | -121.3578 | No | Fog;32-90 F |  |  | 24-0144380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996523 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 20241211 | 1739 | 20241211 | 1808 | 2650166 | 29 | Distribution Circuit | Company Initiated | Return Circuit Normal | 156 | 4524 | 39.3638 | -120.7923 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131574 | OH | Sus | 35578012 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996625 | 0 | Non-EPSS | N | 2024 | NONE
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 531679 | 20241211 | 1812 | 20241211 | 2102 | 2650174 | 170 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 11050 | 39.2363 | -121.0044 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0144487 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996626 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 6981 | 20241211 | 1850 | 20241211 | 2046 | 2650201 | 116 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 1508 | 38.9721 | -121.0436 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0144491 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996631 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1451 | 20241212 | 412 | 20241212 | 655 | 2650409 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 7498 | 38.7595 | -120.7202 | No | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 24-0144544 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996688 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2019 | 20241212 | 621 | 20241212 | 1012 | 2650440 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 5313 | 38.5874 | -120.6609 | No | Overcast-Heavy Rain;32-90 F | Insulator | Broken | 24-0144555 | OH | Sus | 46415887 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996705 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2104 | 153132104 | TRANSFORMER | 222274157030 | 20241212 | 740 | 20241212 | 823 | 2650493 | 43 | Transformer only | Animal | Squirrel | 4 | 172 | 39.2304 | -121.1982 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) |  | 24-0144568 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1996730 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20241212 | 752 | 20241212 | 1024 | 2650498 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 5320 | 38.6658 | -120.7503 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0144604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996843 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | TRANSFORMER | T1547 | 20241212 | 904 | 20241212 | 1000 | 2650636 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 112 | 38.6385 | -121.025 | No | Overcast-Fog-Rain;32-90 F | Customer Equipment | Broken | 24-0144584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1996769 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | FUSE | 8089 | 20241212 | 1219 | 20241212 | 1344 | 2650932 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 1955 | 38.9194 | -121.112 | No | Overcast;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0144655 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996894 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1103 | 152461103 | TRANSFORMER | 222539545825 | 20241212 | 1404 | 20241212 | 1954 | 2651033 | 350 | Transformer only | Animal | Squirrel | 2 | 700 | 38.9212 | -121.1084 | No | Partly Cloudy-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 24-0144680 | OH | Sus | 31719963 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1996922 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1101 | 152031101 | FUSE | 9001 | 20241213 | 944 | 20241213 | 1000 | 2651687 | 16 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 32 | 39.2003 | -121.0628 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0144815 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997117 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | TRANSFORMER | T1547 | 20241213 | 1003 | 20241213 | 1024 | 2651721 | 21 | Transformer only | Equipment Failure/Involved | Underground | 2 | 42 | 38.6385 | -121.025 | No | Overcast-Fog-Drizzle;32-90 F | Secondary | Broken | 24-0144816 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997121 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 54974 | 20241213 | 1022 | 20241213 | 2134 | 2651702 | 672 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 89 | 59808 | 38.6581 | -120.9846 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Burned/flashed | 24-0144820 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997127 | 0 | EPSS Ckt | N | 2024 | N/A
SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6389 | 20241213 | 1104 | 20241213 | 1114 | 2651826 | 10 | Distribution Circuit | Company Initiated | Improper Construction | 6 | 60 | 39.1984 | -120.8338 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0138212 | OH | Sus | 35367335 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997146 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 19742 | 20241213 | 2221 | 20241213 | 2348 | 2652409 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 759 | 66033 | 38.731 | -120.8097 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0144977 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1997281 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 30445 | 20241213 | 2303 | 20241213 | 2324 | 2652440 | 21 | Distribution Circuit | Vegetation | Tree - branch fell on line | 326 | 6846 | 38.9916 | -120.8639 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0144982 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997286 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | JUMPER | OPEN JUMPER @ R99957 | 20241213 | 2314 | 20241214 | 1135 | 2652529 | 741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1161 | 167086 | 38.9983 | -121.4043 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken | 24-0144986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | No | No | 1997291 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 223015658931 | 20241213 | 2316 | 20241214 | 1249 | 2652550 | 813 | Transformer only | Environmental/External | Water | 1 | 813 | 39.2795 | -120.936 | No | Partly Cloudy-Heavy Rain;32-90 F | Transformer | Failed/Faulted | 24-0145136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997441 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | OCB | 1103/2 | 20241213 | 2318 | 20241213 | 2325 | 2652583 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1509 | 10563 | 39.2093 | -121.0615 | No | Overcast-Heavy Rain;32-90 F |  |  | 24-0144990 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997294 | 0 | EPSS Ckt | N | 2024 | B C TIME
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | TRANSFORMER | 223301537185 | 20241213 | 2330 | 20241214 | 1305 | 2652613 | 815 | Transformer only | Vegetation | Tree - fell into line | 2 | 1630 | 38.682 | -120.8441 | No | Strong Winds-Rain-Partly Cloudy;32-90 F | Transformer | Broken- wire on ground | 24-0145020 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1997325 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4839 | 20241213 | 2348 | 20241214 | 1250 | 2653826 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2346 | 39.2188 | -120.9729 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0145150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997456 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | OTHER | WIRE DOWN 1 SPAN SW/OF CGC 221502040623 | 20241213 | 2349 | 20241214 | 1149 | 2653730 | 720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 219 | 14812 | 38.7807 | -121.4742 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1997451 | 1 | Non-EPSS | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | FUSE | 6527 | 20241213 | 2351 | 20241214 | 800 | 2652648 | 489 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 80685 | 39.2401 | -121.1879 | No | Partly Cloudy-Heavy Rain;32-90 F |  |  | 24-0145027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997332 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2102 | 153132102 | JUMPER | OJS 1 SPAN SS/OF CGC 222187557645 | 20241213 | 2352 | 20241214 | 1125 | 2652595 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3465 | 39.2496 | -121.2268 | No | Overcast-Heavy Rain;32-90 F | Secondary | Broken- wire on ground | 24-0145063 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997367 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 28457 | 20241213 | 2359 | 20241214 | 1300 | 2652658 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5467 | 38.9022 | -120.8622 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145061 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1997365 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 9123 | 20241214 | 14 | 20241214 | 502 | 2652690 | 288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 3744 | 39.2845 | -121.0567 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997382 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | RECLOSER | 2784 | 20241214 | 18 | 20241214 | 1533 | 2652706 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 1366 | 195958 | 39.2591 | -121.0188 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145014 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Three Phase Fault | 0 | No | Yes | No | 1997319 | 0 | EPSS Ckt | N | 2024 | A B C GRD TIME OC
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20241214 | 26 | 20241214 | 407 | 2652730 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 17901 | 38.6542 | -121.0356 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145067 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997371 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 19742 | 20241214 | 33 | 20241214 | 117 | 2652735 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 759 | 33396 | 38.731 | -120.8097 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F | Recloser | Failed/Faulted | 24-0145031 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1997336 | 0 | EPSS Ckt | N | 2024 | NO TGTS
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5825 | 20241214 | 37 | 20241214 | 1326 | 2652746 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5383 | 38.8507 | -120.8542 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1997353 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRIP-SAVER | 7559 | 20241214 | 38 | 20241214 | 236 | 2652747 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 8142 | 39.0202 | -121.0625 | Yes | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997337 | 0 | EPSS Ckt | N | 2024 | B C
SIERRA | NEVADA | NARROWS-2102 | 153132102 | RECLOSER | 960916 | 20241214 | 47 | 20241214 | 1612 | 2652784 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 897 | 186031 | 39.2538 | -121.1981 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | Yes | No | 1997331 | 0 | EPSS Ckt | N | 2024 | A B C GRD TIME
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | RECLOSER | 51484 | 20241214 | 202 | 20241214 | 1803 | 2652870 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 990 | 339382 | 39.1909 | -120.9998 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145044 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1997349 | 0 | EPSS Ckt | N | 2024 | A B GRD
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20241214 | 340 | 20241214 | 617 | 2652929 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 6751 | 38.748 | -121.4698 | Yes | Partly Cloudy-Rain;32-90 F |  |  | 24-0145095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997400 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | WISE-1102 | 152271102 | FUSE | 9447 | 20241214 | 445 | 20241214 | 1401 | 2652959 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7228 | 38.9273 | -121.1662 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145106 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1997412 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20241214 | 655 | 20241214 | 1123 | 2653919 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 21708 | 38.6542 | -121.0356 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0145287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997597 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | TRIP-SAVER | 3907 | 20241214 | 728 | 20241214 | 1951 | 2654378 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 105506 | 39.2223 | -121.0816 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145252 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1997562 | 0 | EPSS Ckt | N | 2024 | #1 OF 2 BLOWN
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12121 | 20241214 | 729 | 20241214 | 918 | 2654387 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1308 | 38.6376 | -120.6493 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997680 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1161 | 20241214 | 734 | 20241214 | 1131 | 2654463 | 237 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 184 | 43608 | 38.6752 | -120.7521 | Yes | Clear;32-90 F |  |  | 24-0145494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997817 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 37071 | 20241214 | 734 | 20241214 | 1011 | 2654548 | 157 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 6123 | 38.7934 | -121.0413 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145421 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997743 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1593 | 20241214 | 740 | 20241214 | 1006 | 2654565 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 6563 | 38.619 | -120.9296 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997718 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5775 | 20241214 | 758 | 20241214 | 1119 | 2654730 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 51 | 10251 | 39.0212 | -121.1001 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997857 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 3675 | 20241214 | 758 | 20241214 | 1638 | 2654714 | 520 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 8320 | 39.0552 | -121.1498 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998260 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | TRIP-SAVER | 7559 | 20241214 | 800 | 20241214 | 1755 | 2654860 | 595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 35493 | 39.0202 | -121.0625 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0145309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997622 | 0 | EPSS Ckt | N | 2024 | NONE
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | RECLOSER | 861610 | 20241214 | 803 | 20241215 | 1637 | 2654750 | 1954 | Distribution Circuit | Vegetation | Tree - fell into line | 1218 | 120718 | 39.0467 | -121.0715 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145237 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1997547 | 0 | EPSS Ckt | N | 2024 | A C GRD TIME OC
SIERRA | EL DORADO | PLACERVILLE-1109 | 153081109 | FUSE | 24007 | 20241214 | 807 | 20241214 | 1824 | 2655213 | 617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1234 | 38.7312 | -120.7795 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Fuse | Burned Open | 24-0145992 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998333 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | TRANSFORMER | 222485746447 | 20241214 | 808 | 20241214 | 1630 | 2654788 | 502 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 1506 | 38.9383 | -121.1274 | Yes | Partly Cloudy-Heavy Rain;32-90 F |  |  | 24-0145933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1998263 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20241214 | 808 | 20241214 | 935 | 2654776 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 3741 | 38.748 | -121.4698 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997732 | 0 | Non-EPSS | N | 2024
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 32621 | 20241214 | 811 | 20241214 | 1241 | 2654916 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1842 | 49610 | 39.2311 | -121.0586 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Cutout- fuse holder | Broken | 24-0145587 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997910 | 1 | EPSS Ckt | N | 2024
SIERRA | NEVADA | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2110 | 20241214 | 812 | 20241215 | 1232 | 2654907 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 1508 | 522949 | 39.2017 | -121.0784 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Three Phase Fault | 0 | No | Yes | No | 1997564 | 0 | EPSS Ckt | N | 2024 | A+B+C
SIERRA | PLACER | LINCOLN-1105 | 153701105 | OCB | 1105/2 | 20241214 | 815 | 20241214 | 1017 | 2654958 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1908 | 184672 | 38.9006 | -121.2943 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0145269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997578 | 0 | Non-EPSS | N | 2024 | A & C
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20241214 | 820 | 20241214 | 1542 | 2655015 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 1239 | 117978 | 39.2408 | -121.0301 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | Yes | No | 1997591 | 0 | EPSS Ckt | N | 2024 | A+B+SGF
SIERRA | PLACER | LINCOLN-1104 | 153701104 | RECLOSER | 685276 | 20241214 | 824 | 20241214 | 1106 | 2655123 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 38718 | 38.9848 | -121.2917 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Insulator | Broken | 24-0145307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997620 | 0 | EPSS Ckt | N | 2024 | B+C
SIERRA | PLACER | ROCKLIN-1102 | 152061102 | TRANSFORMER | 222159540519 | 20241214 | 826 | 20241214 | 1805 | 2655103 | 579 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 12107 | 38.7767 | -121.2436 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0145626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997951 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 20709 | 20241214 | 828 | 20241214 | 1213 | 2655132 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 18900 | 38.684 | -120.8255 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145528 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997852 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9351 | 20241214 | 828 | 20241214 | 1724 | 2655156 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2680 | 38.8963 | -120.8911 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145638 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | Yes | No | 1997963 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 18773 | 20241214 | 829 | 20241214 | 1012 | 2655147 | 103 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 14008 | 38.6472 | -120.9436 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Three Phase Fault | 0 | No | No | No | 1997779 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223394241627 | 20241214 | 857 | 20241215 | 1700 | 2656223 | 1923 | Transformer only | Vegetation | Tree - fell into line | 1 | 1923 | 38.8034 | -120.8064 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998341 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223407041627 | 20241214 | 857 | 20241214 | 1830 | 2658314 | 573 | Transformer only | Vegetation | Tree - fell into line | 1 | 573 | 38.8034 | -120.8056 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Fuse | Normal | 24-0146005 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998344 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20241214 | 902 | 20241214 | 2059 | 2656035 | 717 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 21068 | 38.6196 | -120.7647 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1997816 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20241214 | 912 | 20241215 | 935 | 2656368 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 103873 | 38.6926 | -120.765 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998276 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | FUSE | 1553 | 20241214 | 925 | 20241214 | 1332 | 2656416 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 14573 | 38.7447 | -120.8192 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0145737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998068 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224068039843 | 20241214 | 934 | 20241214 | 1326 | 2656497 | 232 | Transformer only | Vegetation | Tree - fell into line | 6 | 1392 | 38.7517 | -120.5739 | Yes | Overcast-Rain-Strong Winds;32-90 F | Service conductor | Normal | 24-0145742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998074 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2103 | 153612103 | FUSE | 18887 | 20241214 | 954 | 20241214 | 1833 | 2656888 | 519 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 22836 | 38.5556 | -120.9916 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0146003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998342 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | CATLETT-1102 | 153761102 | FUSE | 7945 | 20241214 | 1006 | 20241214 | 1300 | 2657060 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 7482 | 38.748 | -121.4698 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0145712 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998041 | 0 | Non-EPSS | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 222908439292 | 20241214 | 1024 | 20241215 | 1633 | 2659848 | 1809 | Transformer only | Vegetation | Tree - fell into line | 1 | 1809 | 38.7411 | -120.9815 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0146040 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998379 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20241214 | 1025 | 20241214 | 1828 | 2657539 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 54815 | 38.7121 | -120.9501 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145471 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | Yes | No | 1997794 | 0 | EPSS Ckt | N | 2024 | B- C & GRD
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 30067 | 20241214 | 1117 | 20241214 | 1309 | 2658232 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3024 | 38.8459 | -121.1004 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0145689 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998016 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20535 | 20241214 | 1129 | 20241216 | 947 | 2659360 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 4870 | 2070129 | 38.7338 | -120.6035 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145756 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998089 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1507 | 20241214 | 1136 | 20241214 | 1645 | 2658419 | 309 | Distribution Circuit | 3rd Party | Other | 26 | 3894 | 38.7412 | -120.7227 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998057 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1513 | 20241214 | 1138 | 20241215 | 1545 | 2658420 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11004 | 38.7424 | -120.6941 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145927 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998258 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32315 | 20241214 | 1140 | 20241215 | 1440 | 2658510 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4860 | 38.9096 | -120.8354 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146075 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998417 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 20165 | 20241214 | 1147 | 20241215 | 1225 | 2658508 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 81845 | 38.6987 | -120.8505 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998123 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 117452 | 20241214 | 1148 | 20241215 | 154 | 2658543 | 846 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 44838 | 38.8428 | -121.029 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145636 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997961 | 0 | EPSS Ckt | N | 2024 | A B
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20241214 | 1150 | 20241215 | 1657 | 2658598 | 1747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 665 | 885406 | 38.9128 | -120.82 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145613 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997938 | 0 | EPSS Ckt | N | 2024 | A+B
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9325 | 20241214 | 1151 | 20241215 | 1900 | 2659790 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1869 | 38.9287 | -120.7607 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0145841 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1998175 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1107 | 152691107 | JUMPER | WIRE DOWN 3P SS FROM CGC#222724949384 | 20241214 | 1153 | 20241215 | 1216 | 2659630 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3432 | 39.0191 | -121.0433 | Yes | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145781 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | Yes | Yes | 1998112 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9991 | 20241214 | 1155 | 20241214 | 2328 | 2658564 | 693 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 13860 | 38.9124 | -120.8292 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0146128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998477 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 15341 | 20241214 | 1155 | 20241214 | 1548 | 2659734 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 622 | 38.9263 | -121.4059 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145893 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998226 | 1 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 22367 | 20241214 | 1157 | 20241214 | 1810 | 2658363 | 373 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 6714 | 38.6699 | -120.8964 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145710 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998039 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6919 | 20241214 | 1158 | 20241215 | 1108 | 2658593 | 1390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 48650 | 38.8593 | -120.833 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146226 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998582 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20241214 | 1159 | 20241214 | 1348 | 2658626 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 883 | 96247 | 39.2609 | -120.9817 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1997948 | 0 | EPSS Ckt | N | 2024 | A-B
SIERRA | PLACER | HALSEY-1102 | 152241102 | FUSE | 9509 | 20241214 | 1201 | 20241215 | 1110 | 2659637 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 905 | 113816 | 39.011 | -120.9956 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145787 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998119 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1103 | 152571103 | FUSE | 5959 | 20241214 | 1201 | 20241214 | 1306 | 2658642 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 2860 | 38.7432 | -121.1638 | Yes | Overcast-Fog-Strong Winds;32-90 F |  |  | 24-0145702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998029 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | JUMPER | WIRE DOWN @ CGC#223394349585 | 20241214 | 1205 | 20241214 | 1645 | 2660003 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 840 | 39.022 | -120.8064 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | Yes | No | 1998232 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20241214 | 1206 | 20241214 | 1701 | 2658692 | 295 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 79 | 23305 | 38.7309 | -120.8421 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F |  |  | 24-0145937 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998266 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1109 | 152691109 | FUSE | 5775 | 20241214 | 1206 | 20241215 | 1003 | 2658658 | 1317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 67167 | 39.0212 | -121.1001 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0145881 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998215 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACER-1104 | 152461104 | FUSE | 39927 | 20241214 | 1206 | 20241214 | 1507 | 2658671 | 181 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 7602 | 38.9027 | -121.0753 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Service conductor | Broken | 24-0145814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998147 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11537 | 20241214 | 1207 | 20241215 | 1033 | 2658677 | 1346 | Distribution Circuit | Vegetation | Tree - bark fell into line | 21 | 28266 | 38.6682 | -120.9386 | Yes | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998167 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 20867 | 20241214 | 1209 | 20241215 | 1323 | 2658698 | 1514 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 26061 | 38.7197 | -120.5828 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998213 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10321 | 20241214 | 1210 | 20241214 | 1718 | 2658736 | 308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 27720 | 38.8032 | -120.9307 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0145951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998283 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20241214 | 1211 | 20241214 | 1447 | 2658792 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 25896 | 38.7712 | -120.9325 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0145825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998158 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6917 | 20241214 | 1213 | 20241214 | 2336 | 2658822 | 683 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 42346 | 38.8721 | -120.8333 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0146125 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998473 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1361 | 20241214 | 1214 | 20241215 | 1330 | 2659714 | 1516 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34868 | 38.5813 | -120.5699 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145816 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998149 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20241214 | 1215 | 20241214 | 1759 | 2658779 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1720 | 38.8986 | -120.8986 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998106 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223109353943 | 20241214 | 1217 | 20241215 | 1053 | 2659159 | 1356 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2712 | 39.1428 | -120.9048 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Service conductor | Normal | 24-0146254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998629 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20241214 | 1218 | 20241215 | 1132 | 2658814 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 79458 | 38.9142 | -120.9386 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145979 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998318 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1110 | 153081110 | TRANSFORMER | 223204839847 | 20241214 | 1218 | 20241214 | 2033 | 2658754 | 495 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 495 | 38.7555 | -120.8775 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Fuse | Failed/Faulted | 24-0146073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998415 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20241214 | 1242 | 20241215 | 1235 | 2659062 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 644 | 115674 | 39.0317 | -121.0046 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken | 24-0145761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | No | No | 1998094 | 0 | EPSS Ckt | N | 2024 | A+B+C+SGF
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7721 | 20241214 | 1308 | 20241214 | 1736 | 2659189 | 268 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 3 | 894 | 39.0138 | -121.327 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0145974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998312 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | HORSESHOE-1101 | 152571101 | TRANSFORMER | 222392239633 | 20241214 | 1337 | 20241214 | 1637 | 2658417 | 180 | Transformer only | Vegetation | Tree - fell into line | 4 | 720 | 38.7517 | -121.162 | Yes | Strong Winds-Overcast-Fog;32-90 F | Transformer | Broken- wire on ground | 24-0145786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998118 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 914599 | 20241214 | 1352 | 20241215 | 1426 | 2659574 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8844 | 39.0084 | -120.8974 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998314 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224004240528 | 20241214 | 1545 | 20241215 | 936 | 2660013 | 1071 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2142 | 38.7708 | -120.5964 | Yes | Overcast-Fog-Rain;32-90 F | Fuse | Normal | 24-0146209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998558 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 20241214 | 1558 | 20241214 | 2031 | 2660010 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2184 | 38.9807 | -120.9404 | Yes | Partly Cloudy-Fog;32-90 F |  |  | 24-0146071 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998413 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13739 | 20241214 | 2107 | 20241215 | 139 | 2660714 | 272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 12512 | 38.6002 | -120.6709 | Yes | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Normal | 24-0146145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998494 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 9991 | 20241214 | 2346 | 20241215 | 1349 | 2660778 | 843 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 16860 | 38.9124 | -120.8292 | Yes | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0146137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998486 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1110 | 152691110 | TRANSFORMER | 222808851105 | 20241215 | 140 | 20241215 | 1319 | 2660805 | 699 | Transformer only | Vegetation | Tree - fell into line | 1 | 699 | 39.0654 | -121.0115 | No | Partly Cloudy-Fog;32-90 F | Transformer | Broken- wire on ground | 24-0146193 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998542 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OTHER | CAR POLE | 20241215 | 920 | 20241215 | 1832 | 2661175 | 552 | Distribution Circuit | 3rd Party | Vehicle | 58 | 21304 | 38.7469 | -120.5598 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0146261 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | No | No | 1998637 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 300879 | 20241215 | 921 | 20241215 | 1348 | 2661178 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 801 | 38.6409 | -120.5109 | No | Clear;32-90 F |  |  | 24-0146329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998698 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SPAULDING-1101 | 152251101 | JUMPER | WIRE DOW @ CGC#223748559505 | 20241215 | 1110 | 20241215 | 1739 | 2661424 | 371 | Distribution Circuit | Environmental/External | Ice or snow | 61 | 5076 | 39.2933 | -120.6764 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146260 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | Yes | No | 1998636 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 5711 | 20241215 | 1354 | 20241215 | 1450 | 2661669 | 56 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 560 | 38.9831 | -121.0247 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0146325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1998695 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 4403 | 20241215 | 1956 | 20241216 | 218 | 2662118 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3820 | 39.2247 | -121.1988 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0146461 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998826 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1107 | 152701107 | FUSE | 51349 | 20241216 | 750 | 20241216 | 1044 | 2662384 | 174 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 228 | 38.9403 | -121.1077 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 24-0146513 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998885 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6377 | 20241216 | 811 | 20241216 | 857 | 2662440 | 46 | Distribution Circuit | Company Initiated | Improper Construction | 89 | 4111 | 39.2023 | -120.8368 | No | Overcast-Fog-Rain;32-90 F | Fuse | Normal | 24-0146507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998881 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | OCB | 1102/2 | 20241216 | 906 | 20241216 | 1233 | 2662595 | 178 | Distribution Circuit | Company Initiated | Other Circuits | 2450 | 246983 | 39.1155 | -120.954 | No | Overcast-Rain;32-90 F | Transformer (OH) | Normal | 24-0146507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | No | No | 1998899 | 0 | EPSS Ckt | N | 2024 | GRD SGF TOC
SIERRA | NEVADA | NARROWS-2105 | 153132105 | RECLOSER | 2216 | 20241216 | 951 | 20241216 | 1802 | 2662724 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 1568 | 138482 | 39.1999 | -121.1727 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 24-0146532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | No | No | 1998918 | 0 | EPSS Ckt | N | 2024 | B C GRD
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 32993 | 20241216 | 951 | 20241216 | 1542 | 2662878 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 30186 | 39.2528 | -121.1149 | No | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146566 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998952 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20241216 | 1030 | 20241216 | 1128 | 2662809 | 58 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 3422 | 39.1894 | -120.9612 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0146558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998943 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | FUSE | 3011 | 20241216 | 1035 | 20241216 | 1608 | 2662680 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 999 | 39.2609 | -121.0054 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998947 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 24237 | 20241216 | 1119 | 20241216 | 1207 | 2662909 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 48 | 38.7098 | -120.9193 | No | Overcast-Rain;32-90 F |  |  | 24-0146595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998975 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 222927254007 | 20241216 | 1444 | 20241216 | 1725 | 2663170 | 161 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 483 | 39.145 | -120.9693 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Deteriorated | 24-0146646 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999029 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1593 | 20241217 | 656 | 20241217 | 911 | 2663801 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 135 | 16117 | 38.619 | -120.9296 | No | Partly Cloudy-Fog;32-90 F | Fuse | Failed/Faulted | 24-0146738 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1999135 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223607236658 | 20241217 | 841 | 20241217 | 1434 | 2664234 | 353 | Transformer only | Animal | Squirrel | 1 | 353 | 38.6662 | -120.737 | No | Clear;32-90 F | Transformer (OH) |  | 24-0146825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999325 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | SUMMIT-1101 | 152591101 | TRANSFORMER | 224591160685 | 20241217 | 1024 | 20241217 | 1529 | 2664088 | 305 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 610 | 39.3216 | -120.3782 | No | Partly Cloudy;32-90 F |  |  | 24-0146784 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1999274 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223303841219 | 20241217 | 1027 | 20241217 | 1233 | 2664094 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 126 | 38.7914 | -120.842 | No | Clear;32-90 F | Service conductor | Broken | 24-0146795 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999287 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 3389 | 20241217 | 1059 | 20241217 | 2259 | 2664593 | 720 | Distribution Circuit | Equipment Failure/Involved | Underground | 100 | 56154 | 38.9384 | -121.0861 | No | Partly Cloudy;32-90 F | Transformer (UG) | Broken | 24-0146829 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1999360 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224032740135 | 20241217 | 1956 | 20241218 | 327 | 2664583 | 451 | Transformer only | Equipment Failure/Involved | Overhead | 20 | 9020 | 38.76 | -120.5867 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999375 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | DIAMOND SPRINGS-1103 | 152261103 | TRANSFORMER | MTR#1007648999 | 20241219 | 209 | 20241219 | 930 | 2665631 | 441 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 441 | 38.7339 | -120.845 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999728 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | ROCKLIN-1103 | 152061103 | FUSE | 34871 | 20241219 | 712 | 20241219 | 1407 | 2665654 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 5719 | 38.7844 | -121.2544 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147090 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1999789 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | SWITCH | 923421 | 20241220 | 812 | 20241220 | 1450 | 2666448 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 796 | 39.0931 | -120.9509 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0146797 | OH | Sus | 35605709 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1999969 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | CLARKSVILLE-2105 | 153612105 | FUSE | 19105 | 20241220 | 2104 | 20241221 | 144 | 2667108 | 280 | Distribution Circuit | Equipment Failure/Involved | Underground | 86 | 24080 | 38.6585 | -121.0115 | No | Partly Cloudy;32-90 F | Elbow | Burned/flashed | 24-0147275 | UG | Sus | 46423373 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2000186 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | SWITCH | 1455 | 20241222 | 2334 | 20241223 | 432 | 2667891 | 298 | Distribution Circuit | 3rd Party | Vehicle | 200 | 59600 | 38.9735 | -121.0931 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken | 24-0147419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 2000415 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222363556430 | 20241223 | 342 | 20241223 | 835 | 2667978 | 293 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 879 | 39.2133 | -121.1668 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 24-0147440 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2000424 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1103 | 152561103 | FUSE | 30067 | 20241224 | 426 | 20241224 | 614 | 2668790 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2916 | 38.8459 | -121.1004 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0147558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000611 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLEASANT GROVE-2110 | 152442110 | RECLOSER | 6128 | 20241224 | 1223 | 20241224 | 1253 | 2669233 | 30 | Distribution Circuit | 3rd Party | Vehicle | 147 | 4410 | 38.8246 | -121.3507 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 24-0147645 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2000701 | 0 | Non-EPSS | N | 2024 | NA
SIERRA | PLACER | HALSEY-1101 | 152241101 | FUSE | 8483 | 20241224 | 1729 | 20241225 | 1205 | 2669421 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 14618 | 39.0185 | -121.0227 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147696 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 2000756 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 222915734624 | 20241224 | 1905 | 20241224 | 2244 | 2669468 | 219 | Transformer only | Environmental/External | Lightning | 1 | 219 | 38.6114 | -120.9816 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 24-0147694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000754 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER | 222914034645 | 20241224 | 1924 | 20241224 | 2331 | 2669469 | 247 | Transformer only | Environmental/External | Lightning | 2 | 494 | 38.6117 | -120.9825 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 24-0147695 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000755 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 18653 | 20241225 | 1045 | 20241225 | 1300 | 2669611 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1620 | 38.7375 | -120.7101 | No | Clear;32-90 F |  |  | 24-0147719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000780 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | FUSE | 7765 | 20241225 | 1120 | 20241225 | 1444 | 2669633 | 204 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 4803 | 39.2018 | -121.1976 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2000788 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 74084 | 20241226 | 735 | 20241226 | 907 | 2669880 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 15548 | 38.7191 | -120.7692 | No | Overcast-Drizzle;32-90 F |  |  | 24-0147781 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000841 | 0 | EPSS Ckt | N | 2024 | A-C
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 16687 | 20241226 | 1242 | 20241226 | 1347 | 2670120 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 130 | 38.9174 | -121.2796 | No | Overcast;32-90 F |  |  | 24-0147813 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000910 | 0 | EPSS Ckt | N | 2024
SIERRA | EL DORADO | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22331 | 20241227 | 125 | 20241227 | 716 | 2670410 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 8212 | 38.6538 | -120.9298 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147879 | OH | Sus | 46438617 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 2000975 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | RECLOSER | 382858 | 20241227 | 328 | 20241227 | 1129 | 2670453 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 12506 | 39.0571 | -121.0877 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0147882 | OH | Sus | 46438618 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2000978 | 0 | EPSS Ckt | N | 2024 | B
SIERRA | PLACER | LINCOLN-1101 | 153701101 | TRANSFORMER | 222297845238 | 20241227 | 357 | 20241227 | 1806 | 2670478 | 849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3203 | 38.906 | -121.1935 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 24-0147911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001032 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | WHEATLAND-1104 | 152811104 | FUSE | 7267 | 20241227 | 404 | 20241227 | 1239 | 2670479 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 5665 | 38.9973 | -121.3769 | No | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0147903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 2001010 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | NARROWS-2105 | 153132105 | TRANSFORMER | 222295455741 | 20241227 | 919 | 20241227 | 1435 | 2670652 | 316 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 632 | 39.1945 | -121.191 | No | Overcast-Fog;32-90 F | Transformer | Broken | 24-0147923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001047 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 34029 | 20241227 | 1841 | 20241227 | 2246 | 2671021 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 245 | 39.0516 | -121.0839 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0147980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001111 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | TRANSFORMER | 222300553324 | 20241227 | 2002 | 20241228 | 1110 | 2671079 | 908 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 1 | 908 | 39.1277 | -121.1895 | No | Overcast-Fog;32-90 F | Service conductor | Broken | 24-0147988 | OH | Sus | 31721046 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001120 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1104 | 153701104 | FUSE | 15257 | 20241228 | 135 | 20241228 | 835 | 2671142 | 420 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 5880 | 38.9265 | -121.2597 | No | Overcast;32-90 F |  |  | 24-0148016 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001149 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | LINCOLN-1101 | 153701101 | FUSE | 4631 | 20241228 | 918 | 20241228 | 1507 | 2671238 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1047 | 38.8863 | -121.2093 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148024 | OH | Sus | 35607669 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001160 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 4415 | 20241228 | 1225 | 20241229 | 1418 | 2671427 | 1553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 23295 | 39.6681 | -120.6253 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 2001196 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PENRYN-1105 | 152561105 | RECLOSER | 50550 | 20241228 | 1821 | 20241228 | 2244 | 2671512 | 263 | Distribution Circuit | 3rd Party | Vehicle | 272 | 26561 | 38.8511 | -121.1794 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0148064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 2001205 | 0 | EPSS Ckt | N | 2024 | C SGF
SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 31957 | 20241229 | 941 | 20241229 | 949 | 2671658 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 24 | 39.0191 | -120.8237 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 24-0148104 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001250 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | TRANSFORMER | 222849348824 | 20241229 | 1033 | 20241229 | 1428 | 2671763 | 235 | Transformer only | Vegetation | Tree - fell into line | 3 | 705 | 39.0033 | -120.9983 | No | Overcast-Fog-Drizzle;32-90 F | Service conductor | Broken- wire on ground | 24-0148135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001284 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | HALSEY-1102 | 152241102 | SWITCH | 9539 | 20241229 | 1051 | 20241229 | 1151 | 2671761 | 60 | Distribution Circuit | Vegetation | Other ground vegetation | 192 | 11520 | 39.0032 | -120.9953 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0148115 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001262 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 183068 | 20241229 | 1523 | 20241231 | 1815 | 2671888 | 3052 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 239732 | 39.569 | -120.6271 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0148141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 2001290 | 0 | EPSS Ckt | N | 2024 | SGF INST OC
SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | RECLOSER | 669489 | 20241229 | 1715 | 20241229 | 2120 | 2671957 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2084 | 252018 | 38.73 | -120.5695 | No | Overcast-Fog-Rain;32-90 F | Switch (OH) | Normal | 24-0148154 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001304 | 1 | EPSS Ckt | N | 2024 | SGF
SIERRA | NEVADA | BRUNSWICK-1110 | 152481110 | FUSE | 7823 | 20241230 | 655 | 20241230 | 900 | 2672218 | 125 | Distribution Circuit | Animal | Bird found | 52 | 6500 | 39.1453 | -121.126 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148187 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001358 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | HIGGINS-1103 | 152691103 | FUSE | 4729 | 20241230 | 1002 | 20241230 | 1127 | 2672410 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 3315 | 39.0824 | -121.1414 | No | Clear;32-90 F |  |  | 24-0148208 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001444 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | TRANSFORMER | 222708547185 | 20241230 | 1947 | 20241231 | 45 | 2672794 | 298 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 596 | 38.9582 | -121.0486 | No | Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148247 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001497 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20241231 | 840 | 20241231 | 1133 | 2673024 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 9861 | 38.9142 | -120.9386 | No | Clear;32-90 F |  |  | 24-0148296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001588 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | DRUM-1101 | 152321101 | TRANSFORMER | 223626658165 | 20241231 | 848 | 20241231 | 1032 | 2673033 | 104 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 104 | 39.2586 | -120.7214 | No | Clear;32-90 F |  |  | 24-0148292 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 2001584 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5823 | 20241231 | 1558 | 20241231 | 1605 | 2673394 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 21 | 38.8508 | -120.8577 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0148320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001617 | 1 | EPSS Ckt | N | 2024
SIERRA | PLACER | EAST NICOLAUS-1103 | 152151103 | FUSE | 7883 | 20241231 | 1618 | 20241231 | 2001 | 2673406 | 223 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 669 | 38.8972 | -121.415 | No | Clear;32-90 F |  |  | 24-0148338 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001635 | 0 | Non-EPSS | N | 2024
SIERRA | PLACER | BELL-1109 | 152701109 | FUSE | 5783 | 20241231 | 1659 | 20241231 | 2103 | 2673381 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 12112 | 38.9562 | -121.0712 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0148323 | OH | Sus | 46443214 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001620 | 0 | EPSS Ckt | N | 2024
SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9889 | 20241231 | 1743 | 20241231 | 1759 | 2673470 | 16 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 32 | 39.2991 | -120.9693 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0148328 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2001624 | 0 | EPSS Ckt | N | 2024
SIERRA | PLACER | BELL-1108 | 152701108 | RECLOSER | 80680 | 20241231 | 2015 | 20250101 | 557 | 2673506 | 582 | Distribution Circuit | 3rd Party | Vehicle | 146 | 74652 | 38.9639 | -121.105 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0148339 | OH | Sus | 31721173 | NORTH VALLEY AND SIERRA | DEC | Multi-Fault | 0 | No | Yes | No | 2001636 | 0 | EPSS Ckt | N | 2024 | A+C+GRD
SONOMA | SANTA ROSA | COTATI 1105 | 42271105 | FUSE | 2881 | 20230101 | 23 | 20230101 | 440 | 1907606 | 257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 12079 | 38.3435 | -122.7574 | No | Clear;32-90 F |  |  | 23-0004281 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1794876 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | SWITCH | 746290 | 20230101 | 753 | 20230101 | 910 | 1907943 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 81 | 6237 | 38.3535 | -122.6425 | No | Clear;32-90 F |  |  | 23-0004306 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | No | No | 1794902 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1103 | 42151103 | FUSE | 4507 | 20230101 | 1115 | 20230101 | 1611 | 1908326 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7400 | 38.4252 | -122.7347 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0004386 | OH | Sus | 31634160 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1794981 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 13255 | 20230102 | 1110 | 20230102 | 1222 | 1909890 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 72 | 38.372 | -122.6238 | No | Clear;32-90F |  |  | 23-0004736 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1795342 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | FORT ROSS 1121 | 42851121 | RECLOSER | 560 | 20230102 | 1712 | 20230103 | 1838 | 1910406 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 47306 | 38.5561 | -123.3034 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004827 | OH | Sus | 45615940 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1795430 | 0 | EPSS Ckt | N | 2023 | AB
SONOMA | SANTA ROSA | MONTE RIO 1111 | 42811111 | FUSE | 17609 | 20230102 | 1858 | 20230102 | 1927 | 1910486 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 406 | 38.4508 | -123.1213 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0004852 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1795456 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO 1102 | 42571102 | FUSE | 1955 | 20230102 | 1952 | 20230103 | 346 | 1910568 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 13184 | 38.3883 | -122.9713 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004869 | OH | Sus | 31634147 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795472 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL 1101 | 42091101 | JUMPER | WIRE DOWN @ 7280 GIOVANETTI | 20230102 | 2246 | 20230103 | 1044 | 1910996 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3594 | 38.4636 | -122.9209 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004967 | OH | Sus | 45615386 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1795568 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 3795 | 20230103 | 59 | 20230103 | 1047 | 1910853 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 21168 | 38.3962 | -122.6248 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004947 | OH | Sus | 45615368 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1795554 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR 1102 | 43071102 | TRANSFORMER | 218555524110 | 20230103 | 1153 | 20230103 | 1237 | 1911449 | 44 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 132 | 38.3275 | -122.5045 | No | Clear;32-90F | Fuse | Normal | 23-0005102 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1795663 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE 1102 | 42821102 | FUSE | 12905 | 20230103 | 1242 | 20230103 | 1746 | 1911519 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11241 | 38.7762 | -122.9308 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005190 | OH | Sus | 45615957 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1795708 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN 1111 | 42751111 | TRANSFORMER | 217554534056 | 20230103 | 2053 | 20230104 | 1235 | 1912096 | 942 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 2826 | 38.5994 | -122.8565 | No | Clear;32-90 F | Transformer | Broken | 23-0005435 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1795916 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA 1105 | 42721105 | FUSE | 17971 | 20230104 | 134 | 20230104 | 236 | 1912168 | 62 | Distribution Circuit | 3rd Party | Vehicle | 4 | 248 | 38.2719 | -122.429 | Yes | Clear;32-90F | Fuse | Normal | 23-0005497 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1795979 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA 1104 | 42721104 | FUSE | 12407 | 20230104 | 500 | 20230104 | 1646 | 1912232 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21886 | 38.3032 | -122.5518 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005559 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796021 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 7385 | 20230104 | 554 | 20230104 | 821 | 1912326 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5733 | 38.4829 | -123.1468 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0005575 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796034 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4537 | 20230104 | 631 | 20230110 | 1700 | 1912953 | 9269 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 92690 | 38.5247 | -123.2647 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005674 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | No | No | 1796097 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 11011 | 20230104 | 724 | 20230111 | 1334 | 1912447 | 10450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 73150 | 38.5448 | -123.2925 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0013612 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1803074 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20230104 | 752 | 20230113 | 1710 | 1912567 | 13518 | Distribution Circuit | Vegetation | Tree - fell into line | 446 | 3972255 | 38.5561 | -123.3034 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0005579 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796039 | 0 | EPSS Ckt | N | 2023 | A- GRD
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4613 | 20230104 | 752 | 20230112 | 1517 | 1913825 | 11965 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11965 | 38.5616 | -123.3114 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005918 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796281 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ SS OF 216391631660 | 20230104 | 753 | 20230109 | 1745 | 1913867 | 7792 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7792 | 38.5278 | -123.2635 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0005931 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1796291 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRANSFORMER | 216394431593 | 20230104 | 758 | 20230111 | 652 | 1938939 | 10014 | Transformer only | Vegetation | Tree - fell into line | 1 | 10014 | 38.5272 | -123.2618 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0011444 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1801203 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 116 | 20230104 | 810 | 20230104 | 901 | 1912621 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 384 | 19584 | 38.4736 | -122.8977 | Yes | Clear;32-90F |  |  | 23-0005592 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796046 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4271 | 20230104 | 811 | 20230110 | 1621 | 1913037 | 9130 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 127820 | 38.5392 | -123.2764 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005694 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796109 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 2699 | 20230104 | 812 | 20230111 | 1334 | 1913110 | 10402 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 353668 | 38.5431 | -123.2894 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005712 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1796124 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI 1102 | 42271102 | RECLOSER | 464 | 20230104 | 859 | 20230104 | 1424 | 1912851 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 5315 | 377617 | 38.3002 | -122.7115 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005652 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796081 | 0 | EPSS Ckt | N | 2023 | B INST
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 7935 | 20230104 | 921 | 20230104 | 1103 | 1912957 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1970 | 38.3699 | -122.6237 | Yes | Clear;32-90F |  |  | 23-0005775 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796175 | 1 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 116 | 20230104 | 955 | 20230104 | 1015 | 1913088 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 7540 | 38.4736 | -122.8977 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005709 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1796122 | 0 | EPSS Ckt | N | 2023 | N/A
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | JUMPER | OJ'S 6/LD SIDE OF 6485 | 20230104 | 955 | 20230104 | 1846 | 1913185 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3717 | 38.4675 | -122.9145 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005709 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1796147 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20230104 | 1021 | 20230104 | 1603 | 1913190 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 22572 | 38.4728 | -123.0474 | Yes | Clear;32-90F |  |  | 23-0006019 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796363 | 0 | EPSS Ckt | N | 2023 | A & B
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230104 | 1030 | 20230104 | 1130 | 1913242 | 60 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 103 | 6180 | 38.826 | -123.0003 | Yes | Clear;32-90F |  |  | 23-0005803 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796201 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 15575 | 20230104 | 1123 | 20230104 | 1925 | 1913271 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 4372 | 38.7803 | -122.9666 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005823 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796218 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-1105 | 43301105 | FUSE | 7799 | 20230104 | 1123 | 20230104 | 1130 | 1913333 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 14 | 38.4524 | -122.7838 | Yes | Clear;32-90F |  |  | 23-0005813 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796209 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ 2 SS CGC 216298333783 | 20230104 | 1150 | 20230113 | 1409 | 1944686 | 13099 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 13099 | 38.5863 | -123.2974 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0012240 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1802001 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ 216336633269 | 20230104 | 1150 | 20230112 | 1750 | 1944699 | 11880 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 23760 | 38.5725 | -123.2786 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0012247 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1802007 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20230104 | 1201 | 20230113 | 1444 | 1923881 | 13123 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 131230 | 38.5896 | -123.3033 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007954 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798089 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON 1101 | 42561101 | FUSE | 11131 | 20230104 | 1225 | 20230104 | 1917 | 1913760 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 14008 | 38.5106 | -122.7782 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005967 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1796317 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20230104 | 1255 | 20230114 | 1232 | 1945455 | 14377 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 215272 | 38.536 | -123.1403 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012565 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802246 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 18831 | 20230104 | 1314 | 20230106 | 1952 | 1914020 | 3278 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 95062 | 38.3997 | -122.6212 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006117 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796439 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 2239 | 20230104 | 1325 | 20230107 | 1947 | 1922978 | 4702 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23510 | 38.3448 | -123.0243 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0007656 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797854 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1703 | 20230104 | 1331 | 20230109 | 1838 | 1914741 | 7507 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 420392 | 38.4835 | -123.0538 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006116 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796438 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4555 | 20230104 | 1337 | 20230110 | 1325 | 1923873 | 8628 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17256 | 38.5639 | -123.2711 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007947 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798084 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217173430860 | 20230104 | 1337 | 20230105 | 1526 | 1914116 | 1549 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1549 | 38.5094 | -122.9884 | Yes | Clear;32-90 F | Transformer | Broken | 23-0006158 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796477 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 7935 | 20230104 | 1340 | 20230104 | 1402 | 1914138 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 1276 | 38.3699 | -122.6237 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0005999 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796342 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONROE-1105 | 43301105 | FUSE | 7799 | 20230104 | 1345 | 20230104 | 1902 | 1913775 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 634 | 38.4524 | -122.7838 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006015 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796357 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20230104 | 1403 | 20230112 | 1725 | 1914096 | 11722 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1026 | 6351858 | 38.4714 | -123.0471 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006032 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796371 | 0 | EPSS Ckt | N | 2023 | A/B GRD
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | SWITCH | 6901 | 20230104 | 1403 | 20230109 | 1855 | 1925209 | 7492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 104876 | 38.4958 | -123.0687 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0008456 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798395 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 56225 | 20230104 | 1403 | 20230112 | 1100 | 1926814 | 11337 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 419469 | 38.485 | -123.0591 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008832 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798694 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20230104 | 1403 | 20230110 | 1426 | 1926817 | 8663 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 311868 | 38.4982 | -123.0729 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008836 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798696 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20230104 | 1403 | 20230111 | 1052 | 1926825 | 9889 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 108779 | 38.4983 | -123.0731 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008840 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798699 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 7697 | 20230104 | 1403 | 20230113 | 1315 | 1934112 | 12912 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 64560 | 38.5157 | -123.0649 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010333 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1800182 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 3895 | 20230104 | 1403 | 20230112 | 1555 | 1939025 | 11632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 139584 | 38.5158 | -123.0795 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011467 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1801225 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 1059 | 20230104 | 1403 | 20230112 | 1732 | 1944937 | 11729 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 504347 | 38.527 | -123.0876 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0012352 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1802092 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 2301 | 20230104 | 1403 | 20230113 | 1900 | 1946086 | 13257 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 251883 | 38.5286 | -123.0954 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012856 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1802437 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 16229 | 20230104 | 1403 | 20230111 | 1627 | 1948422 | 10224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 30672 | 38.5259 | -123.0899 | Yes | Clear;32-90F | Pole-Wood | Normal | 23-0013779 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1803174 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 1047 | 20230104 | 1403 | 20230113 | 1752 | 1948862 | 13189 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 232987 | 38.5318 | -123.0876 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013921 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1803279 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | JUMPER | OJ TWD CGC 216799231576 | 20230104 | 1403 | 20230114 | 1632 | 1952504 | 14549 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14549 | 38.5316 | -123.0906 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015538 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1804384 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 13567 | 20230104 | 1419 | 20230111 | 1755 | 1925129 | 10296 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 82368 | 38.5444 | -123.2282 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008424 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798381 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ 4 SS OF 6259 | 20230104 | 1419 | 20230112 | 1950 | 1933777 | 11851 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 59255 | 38.5036 | -123.1903 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0010215 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800066 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 13539 | 20230104 | 1419 | 20230111 | 1640 | 1933799 | 10221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 10221 | 38.5544 | -123.2566 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010228 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800078 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 7237 | 20230104 | 1419 | 20230114 | 1317 | 1934438 | 14338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 100366 | 38.5615 | -123.2692 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010420 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1800266 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ'S 4 SPANS SS OF CGC 216701331037 | 20230104 | 1419 | 20230116 | 1445 | 1945732 | 17306 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 17306 | 38.5167 | -123.1577 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012677 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1802323 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20230104 | 1424 | 20230113 | 1346 | 1928088 | 12922 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 503958 | 38.5579 | -123.0951 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009128 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798956 | 0 | EPSS Ckt | N | 2023 | N/A
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4509 | 20230104 | 1424 | 20230108 | 1949 | 1928217 | 6085 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 127785 | 38.526 | -123.2105 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009205 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799034 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRIP-SAVER | 6917 | 20230104 | 1431 | 20230107 | 1212 | 1914524 | 4181 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 321937 | 38.3875 | -122.9724 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006170 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796487 | 0 | EPSS Ckt | N | 2023 | AB
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 2957 | 20230104 | 1438 | 20230113 | 1346 | 1951543 | 12908 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 180712 | 38.5857 | -123.1195 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015152 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1804200 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE 1101 | 42891101 | FUSE | 5531 | 20230104 | 1444 | 20230104 | 1547 | 1914572 | 63 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 1093 | 38.6773 | -123.0625 | Yes | Clear;32-90 F |  |  | 23-0006135 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796456 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 2707 | 20230104 | 1445 | 20230113 | 1407 | 1951966 | 12922 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 25844 | 38.5866 | -123.1183 | Yes | Clear;32-90 F |  |  | 23-0015354 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1804280 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO 1113 | 42811113 | RECLOSER | 532 | 20230104 | 1456 | 20230112 | 1509 | 1914654 | 11434 | Distribution Circuit | Vegetation | Tree - fell into line | 3566 | 6554131 | 38.4949 | -123.0108 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006094 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796420 | 0 | EPSS Ckt | N | 2023 | B & C
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | FUSE | 16745 | 20230104 | 1500 | 20230104 | 1658 | 1914583 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 118 | 38.3797 | -122.5679 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0006075 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1796404 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 5687 | 20230104 | 1511 | 20230106 | 2100 | 1922288 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19374 | 38.4072 | -122.932 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007452 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797686 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 13247 | 20230104 | 1525 | 20230108 | 1747 | 1914789 | 5902 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 41314 | 38.3734 | -122.6389 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0006288 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796593 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | OTHER | WIRE DOWN AT 3840 MUNIZ RANCH | 20230104 | 1529 | 20230111 | 1756 | 1915218 | 10227 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 395109 | 38.4987 | -123.1375 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006358 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1796657 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO 1101 | 42571101 | RECLOSER | 322 | 20230104 | 1530 | 20230110 | 1535 | 1914842 | 8541 | Distribution Circuit | Vegetation | Tree - fell into line | 1309 | 4341320 | 38.3871 | -122.89 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006130 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796451 | 0 | EPSS Ckt | N | 2023 | A B GRD
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 1241 | 20230104 | 1530 | 20230108 | 1345 | 1922796 | 5655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 125956 | 38.3523 | -122.8719 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007590 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797800 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 15609 | 20230104 | 1534 | 20230109 | 1320 | 1916985 | 7066 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 692468 | 38.5128 | -122.9981 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006422 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1796720 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 15559 | 20230104 | 1535 | 20230108 | 1850 | 1927491 | 5955 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11910 | 38.3513 | -122.9804 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008989 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798819 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 12637 | 20230104 | 1538 | 20230106 | 1236 | 1916887 | 2698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 99826 | 38.5018 | -123.0047 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006412 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796710 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 547 | 20230104 | 1546 | 20230108 | 1700 | 1932999 | 5834 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 1149298 | 38.4252 | -122.9584 | Yes | Clear;32-90 F | Service conductor | Broken | 23-0009983 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799831 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | RECLOSER | 140 | 20230104 | 1555 | 20230110 | 1812 | 1914975 | 8777 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 1255111 | 38.4669 | -123.0161 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006189 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796503 | 0 | EPSS Ckt | N | 2023 | A/C
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20230104 | 1557 | 20230112 | 812 | 1915989 | 11055 | Distribution Circuit | Vegetation | Tree - fell into line | 1209 | 4490916 | 38.4031 | -122.9214 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006331 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796629 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | JUMPER | OJ'S 2 LOAD SIDE OF 318 ON HARD TAP | 20230104 | 1557 | 20230106 | 1750 | 1923367 | 2993 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8979 | 38.4039 | -122.9492 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007778 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1797946 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1955 | 20230104 | 1557 | 20230108 | 1932 | 1924503 | 5975 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 969156 | 38.3883 | -122.9713 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006331 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798252 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 10135 | 20230104 | 1557 | 20230109 | 1050 | 1934917 | 6893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 41358 | 38.3391 | -122.9183 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Normal | 23-0006331 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800448 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2443 | 20230104 | 1600 | 20230106 | 1157 | 1915042 | 2637 | Distribution Circuit | Vegetation | Tree - bark fell into line | 6 | 15830 | 38.1938 | -122.9112 | Yes | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0008233 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798289 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6245 | 20230104 | 1607 | 20230107 | 1117 | 1915064 | 4030 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 100750 | 38.4444 | -122.9019 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Together | 23-0007794 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797960 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | OTHER | WIRE DOWN 8 SP LS/OF 12717 | 20230104 | 1610 | 20230110 | 1635 | 1934496 | 8665 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39770 | 38.4704 | -123.0533 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010436 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1800280 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRANSFORMER | 217102929220 | 20230104 | 1611 | 20230108 | 1918 | 1915152 | 5947 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 59470 | 38.4643 | -123.0127 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0009995 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799840 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI 1103 | 42271103 | FUSE | 2423 | 20230104 | 1612 | 20230105 | 1758 | 1915132 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17006 | 38.2648 | -122.838 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006250 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796555 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO 1112 | 42811112 | RECLOSER | 212 | 20230104 | 1616 | 20230108 | 1014 | 1915193 | 5356 | Distribution Circuit | Vegetation | Tree - fell into line | 722 | 775642 | 38.4752 | -123.0022 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006205 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796515 | 0 | EPSS Ckt | N | 2023 | A/B
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 4837 | 20230104 | 1616 | 20230107 | 2128 | 1923929 | 4632 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 240864 | 38.4803 | -122.9967 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008006 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798138 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 3869 | 20230104 | 1617 | 20230109 | 614 | 1919665 | 6597 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 158328 | 38.4789 | -123.0504 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006817 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797119 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230104 | 1623 | 20230104 | 1723 | 1915468 | 60 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 103 | 6180 | 38.826 | -123.0003 | Yes | Clear;32-90F |  |  | 23-0006290 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796595 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20230104 | 1625 | 20230113 | 1608 | 1915251 | 12943 | Distribution Circuit | 3rd Party | Other | 26 | 294674 | 38.6773 | -123.0625 | Yes | Clear;32-90 F | Conductor- Overhead | Contaminated | 23-0006211 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796518 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1039 | 20230104 | 1635 | 20230109 | 1430 | 1923137 | 7075 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 955125 | 38.5034 | -122.9973 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0007690 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797877 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 8165 | 20230104 | 1635 | 20230106 | 1720 | 1915140 | 2925 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 114075 | 38.4988 | -123.0189 | Yes | Clear;32-90 F |  |  | 23-0008524 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798452 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | RECLOSER | 166 | 20230104 | 1637 | 20230104 | 1721 | 1915459 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 909 | 39996 | 38.7164 | -122.921 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0006239 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796544 | 0 | EPSS Ckt | N | 2023 | A/B 51 TIME
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5659 | 20230104 | 1653 | 20230108 | 1840 | 1915679 | 5867 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76271 | 38.3833 | -122.8919 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007940 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798078 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1347 | 20230104 | 1656 | 20230105 | 1732 | 1922830 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 48708 | 38.5128 | -122.9964 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007595 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1797804 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE 1101 | 43471101 | FUSE | 6963 | 20230104 | 1656 | 20230105 | 1753 | 1915539 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 50514 | 38.3469 | -122.6122 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006638 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796939 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 15491 | 20230104 | 1658 | 20230108 | 1119 | 1932989 | 5421 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 37947 | 38.4311 | -122.9653 | Yes | Clear;32-90F |  |  | 23-0009977 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799825 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 15405 | 20230104 | 1658 | 20230108 | 1630 | 1932992 | 5716 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 102888 | 38.4274 | -122.9598 | Yes | Clear;32-90 F |  |  | 23-0009978 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799827 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 1293 | 20230104 | 1658 | 20230108 | 1130 | 1932995 | 5432 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 59752 | 38.4258 | -122.9588 | Yes | Clear;32-90F |  |  | 23-0009982 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799830 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 551 | 20230104 | 1658 | 20230108 | 1410 | 1933003 | 5592 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 50328 | 38.4246 | -122.9568 | Yes | Clear;32-90F |  |  | 23-0009985 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799832 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 589 | 20230104 | 1658 | 20230108 | 1136 | 1933005 | 5438 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 157702 | 38.4241 | -122.9564 | Yes | Clear;32-90 F |  |  | 23-0009986 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799833 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 1797 | 20230104 | 1658 | 20230108 | 1141 | 1933010 | 5443 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 97974 | 38.4203 | -122.9524 | Yes | Clear;32-90F |  |  | 23-0009988 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799834 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 7317 | 20230104 | 1659 | 20230109 | 1650 | 1932879 | 7191 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 194157 | 38.3942 | -122.9218 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009930 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1799781 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 4663 | 20230104 | 1659 | 20230108 | 1934 | 1917559 | 5915 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 47320 | 38.4984 | -122.9935 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006470 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1796767 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20230104 | 1702 | 20230108 | 1225 | 1933047 | 5483 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 422191 | 38.422 | -122.954 | Yes | Clear;32-90 F |  |  | 23-0009996 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1799841 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | PETALUMA C 1108 | 42631108 | RECLOSER | 233646 | 20230104 | 1703 | 20230107 | 2150 | 1915642 | 3971 | Distribution Circuit | Vegetation | Tree - fell into line | 451 | 593449 | 38.2416 | -122.679 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006269 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796574 | 0 | EPSS Ckt | N | 2023 | A & GRD
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 3377 | 20230104 | 1706 | 20230104 | 2007 | s1796727 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 18824 | 38.3451 | -122.6667 | Yes | Clear;32-90 F |  |  | 23-0006429 |  | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796727 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3055 | 20230104 | 1706 | 20230106 | 2120 | 1922782 | 3134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3134 | 38.4069 | -122.9279 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007585 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1797795 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 15403 | 20230104 | 1706 | 20230106 | 2122 | 1925376 | 3134 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 56412 | 38.4076 | -122.928 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008504 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798433 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20230104 | 1706 | 20230109 | 1712 | 1921839 | 7206 | Distribution Circuit | Company Initiated | Other Circuits | 66 | 475596 | 38.4728 | -123.0474 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0007301 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1797564 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 12011 | 20230104 | 1708 | 20230109 | 1212 | 1934798 | 6904 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 110464 | 38.3736 | -122.9185 | Yes | Clear;32-90 F |  |  | 23-0010524 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1800374 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3443 | 20230104 | 1709 | 20230106 | 1327 | 1922018 | 2658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15948 | 38.275 | -122.8 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007343 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1797603 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3053 | 20230104 | 1709 | 20230108 | 1452 | 1923027 | 5623 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 601661 | 38.4189 | -122.9303 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007665 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797862 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3259 | 20230104 | 1712 | 20230107 | 1630 | 1923517 | 4278 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 136896 | 38.4002 | -122.954 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007828 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797992 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 4899 | 20230104 | 1713 | 20230108 | 1240 | 1922773 | 5487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 71331 | 38.4083 | -122.9372 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007581 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797792 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | RECLOSER | 213984 | 20230104 | 1715 | 20230106 | 1327 | 1915769 | 2652 | Distribution Circuit | Equipment Failure/Involved | Overhead | 923 | 907300 | 38.2983 | -122.8208 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006345 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796643 | 0 | EPSS Ckt | N | 2023 | C- GRD
SONOMA | SANTA ROSA | SALMON CREEK 1101 | 43161101 | RECLOSER | 37368 | 20230104 | 1715 | 20230107 | 1825 | 1916073 | 4262 | Distribution Circuit | Vegetation | Tree - fell into line | 485 | 1608945 | 38.3809 | -123.079 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0006337 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796635 | 0 | EPSS Ckt | N | 2023 | C- GRD
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 5209 | 20230104 | 1717 | 20230109 | 1545 | 1923143 | 7108 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7108 | 38.2806 | -122.9474 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007694 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797881 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7705 | 20230104 | 1717 | 20230108 | 1917 | 1916124 | 5880 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 52920 | 38.3169 | -122.7498 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010298 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1800147 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | RECLOSER | 173590 | 20230104 | 1717 | 20230105 | 1227 | 1915823 | 1150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 102 | 117300 | 38.5114 | -122.7173 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0007391 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797639 | 0 | EPSS Ckt | N | 2023 | A
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6877 | 20230104 | 1718 | 20230109 | 1816 | 1915780 | 7258 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 226927 | 38.3942 | -122.9138 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007972 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798104 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 982462 | 20230104 | 1721 | 20230107 | 1007 | 1915913 | 3886 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 143782 | 38.4048 | -122.8963 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008063 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798189 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6991 | 20230104 | 1722 | 20230108 | 1258 | 1920261 | 5496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 192 | 100668 | 38.412 | -122.8811 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006919 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1797219 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRIP-SAVER | 3281 | 20230104 | 1723 | 20230106 | 1920 | 1915971 | 2997 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 344655 | 38.3636 | -122.8354 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006499 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796798 | 0 | EPSS Ckt | N | 2023 | NA
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5831 | 20230104 | 1724 | 20230108 | 1250 | 1926723 | 5486 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 38402 | 38.3723 | -122.8717 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008817 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798676 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7803 | 20230104 | 1725 | 20230107 | 1958 | 1926380 | 4473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 353367 | 38.3441 | -122.8499 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008727 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798611 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 69159 | 20230104 | 1725 | 20230107 | 1510 | 1916617 | 4185 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25110 | 38.4648 | -122.8895 | Yes | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0007571 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797782 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 1747 | 20230104 | 1726 | 20230105 | 1533 | 1916007 | 1327 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 66350 | 38.4119 | -122.856 | Yes | Clear;32-90 F |  |  | 23-0007596 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797805 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A 1111 | 42151111 | RECLOSER | 99050 | 20230104 | 1726 | 20230104 | 2243 | 1916084 | 317 | Distribution Circuit | 3rd Party | Other | 1087 | 224933 | 38.4323 | -122.7043 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006321 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796621 | 0 | EPSS Ckt | N | 2023 | B-C GRD
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 3133 | 20230104 | 1727 | 20230115 | 1527 | 1916044 | 15720 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31360 | 38.2742 | -122.9266 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007688 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1797875 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230104 | 1730 | 20230105 | 1834 | 1916279 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 72192 | 38.4756 | -122.9526 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007322 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797580 | 0 | EPSS Ckt | N | 2023 | AC
SONOMA | SANTA ROSA | MOLINO 1104 | 42571104 | RECLOSER | 468882 | 20230104 | 1730 | 20230104 | 1958 | 1916150 | 148 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 3425 | 365769 | 38.4061 | -122.8266 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006328 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796626 | 0 | EPSS Ckt | N | 2023 | A & GRD
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 7547 | 20230104 | 1731 | 20230110 | 1545 | 1924911 | 8534 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 25602 | 38.4148 | -122.9717 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008338 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798344 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217764525075 | 20230104 | 1732 | 20230105 | 1129 | 1921481 | 1077 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3231 | 38.3524 | -122.7809 | Yes | Clear;32-90 F | Secondary | Broken | 23-0007177 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797459 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN 1112 | 42751112 | RECLOSER | 24918 | 20230104 | 1732 | 20230106 | 1345 | 1916170 | 2447 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 161139 | 38.5911 | -122.9201 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006340 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796638 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 781 | 20230104 | 1732 | 20230108 | 1544 | 1927379 | 5652 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 56520 | 38.6025 | -123.0037 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008966 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1798798 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20230104 | 1732 | 20230108 | 2035 | 1927405 | 5943 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 213948 | 38.5969 | -122.9892 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0008970 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | Yes | 1798803 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 11927 | 20230104 | 1733 | 20230108 | 1402 | 1916148 | 5549 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 49941 | 38.4158 | -122.8702 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006593 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1796894 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN 1113 | 42751113 | FUSE | 838937 | 20230104 | 1735 | 20230107 | 1802 | 1920781 | 4347 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 247779 | 38.5918 | -122.9619 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007016 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797319 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3203 | 20230104 | 1737 | 20230105 | 1641 | 1916192 | 1384 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 35984 | 38.4422 | -122.8843 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0007682 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797872 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | T6769 | 20230104 | 1738 | 20230110 | 2006 | 1926279 | 8788 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22502 | 38.3943 | -122.9459 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0008713 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798597 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217806124596 | 20230104 | 1739 | 20230107 | 1706 | 1916218 | 4287 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 25722 | 38.3393 | -122.7661 | Yes | Clear;32-90 F | Transformer | Broken | 23-0008895 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798747 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR 1103 | 43071103 | RECLOSER | 416 | 20230104 | 1745 | 20230109 | 2226 | 1916333 | 7481 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 194506 | 38.4361 | -122.5779 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006357 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796656 | 0 | EPSS Ckt | N | 2023 | B/GRD
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230104 | 1750 | 20230104 | 1843 | 1916340 | 53 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 103 | 5459 | 38.826 | -123.0003 | Yes | Clear;32-90 F |  |  | 23-0006415 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796713 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 481459 | 20230104 | 1754 | 20230109 | 1523 | 1915532 | 7049 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 28196 | 38.4101 | -122.5735 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0006406 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1796704 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217823324177 | 20230104 | 1756 | 20230105 | 1915 | 1916447 | 1519 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 3038 | 38.3281 | -122.7599 | Yes | Clear;32-90 F |  |  | 23-0007870 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798034 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 755 | 20230104 | 1757 | 20230105 | 1004 | 1916500 | 967 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 23208 | 38.3524 | -122.7655 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007237 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797508 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON 1103 | 43321103 | FUSE | 2225 | 20230104 | 1805 | 20230105 | 1043 | 1916633 | 995 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 91540 | 38.5247 | -122.6543 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007295 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797557 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | OTHER | WIRE DOWN @ 7389 LD SIDE | 20230104 | 1825 | 20230108 | 1702 | 1916869 | 5677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 113540 | 38.5126 | -122.9338 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007574 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797785 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A 1104 | 42151104 | FUSE | 346749 | 20230104 | 1845 | 20230105 | 832 | 1917164 | 827 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 52403 | 38.4599 | -122.7033 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0007092 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797386 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA 1103 | 43491103 | TRANSFORMER | T2838 | 20230104 | 1846 | 20230107 | 1612 | 1917193 | 4166 | Transformer only | Equipment Failure/Involved | Underground | 24 | 99984 | 38.2614 | -122.6358 | Yes | Clear;32-90 F | Secondary | Burned Open | 23-0007553 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797768 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217454728465 | 20230104 | 1846 | 20230107 | 935 | 1917186 | 3769 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 11307 | 38.4445 | -122.8901 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0008134 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798225 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20230104 | 1846 | 20230107 | 1510 | 1917176 | 4104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 94392 | 38.4634 | -123.0122 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006509 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796807 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1181 | 20230104 | 1849 | 20230108 | 1908 | 1917215 | 5779 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 505665 | 38.4027 | -122.9163 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0007936 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798072 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | FUSE | 2558 | 20230104 | 1849 | 20230104 | 2221 | 1917214 | 212 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 269 | 57028 | 38.2483 | -122.6244 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0006713 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797015 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 6589 | 20230104 | 1850 | 20230108 | 1946 | 1915621 | 5816 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34880 | 38.2953 | -122.7501 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006453 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796751 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON 1104 | 43321104 | OCB | 1104/2 | 20230104 | 1854 | 20230105 | 32 | 1917314 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4020 | 665256 | 38.4901 | -122.6661 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006501 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796800 | 0 | EPSS Ckt | N | 2023 | A- GRD
SONOMA | SANTA ROSA | FULTON 1104 | 42561104 | FUSE | 9223 | 20230104 | 1916 | 20230105 | 920 | 1917530 | 844 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 40512 | 38.5131 | -122.7699 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0007144 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797430 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | JUMPER | WIRE DOWN 4 SPANS LD SIDE OF 374323 | 20230104 | 1918 | 20230105 | 1710 | 1917545 | 1312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 62976 | 38.3252 | -122.9325 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006852 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1797156 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20230104 | 1918 | 20230105 | 1345 | 1917612 | 1107 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 63 | 69407 | 38.3901 | -122.8853 | Yes | Clear;32-90 F |  |  | 23-0007505 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797723 | 1 | EPSS Ckt | N | 2023 | A
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 8019 | 20230104 | 1919 | 20230105 | 954 | 1918498 | 875 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 418 | 365750 | 38.3478 | -122.7778 | Yes | Clear;32-90 F |  |  | 23-0007185 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797465 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 3647 | 20230104 | 1922 | 20230105 | 1419 | 1917591 | 1137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 27302 | 38.4676 | -122.689 | Yes | Clear;32-90 F |  |  | 23-0007565 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797777 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20230104 | 1932 | 20230105 | 918 | 1917717 | 826 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 7434 | 38.4671 | -122.909 | Yes | Clear;32-90 F |  |  | 23-0005709 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1796789 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRIP-SAVER | 8459 | 20230104 | 1937 | 20230105 | 1121 | 1917759 | 944 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 73632 | 38.3395 | -122.8023 | Yes | Clear;32-90 F |  |  | 23-0007317 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797577 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | RECLOSER | 480 | 20230104 | 1937 | 20230104 | 2241 | s1833821 | 184 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 39008 | 38.7001 | -122.9516 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0006239 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1833821 | 0 | EPSS Ckt | N | 2023 | A/B
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 15385 | 20230104 | 1939 | 20230105 | 1844 | 1917774 | 1385 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 31855 | 38.4202 | -122.888 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F |  |  | 23-0007847 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798009 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | OCB | 1103/2 | 20230104 | 1943 | 20230105 | 1814 | 1915540 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 1427 | 1428200 | 38.3098 | -122.7316 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006514 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1796811 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 217804022105 | 20230104 | 1943 | 20230108 | 2057 | 1920396 | 5834 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 11668 | 38.2712 | -122.7661 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0007430 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797671 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 18569 | 20230104 | 1947 | 20230107 | 947 | 1917821 | 3720 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 22320 | 38.3785 | -122.8775 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008653 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798545 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1793 | 20230104 | 1947 | 20230108 | 1916 | 1917841 | 5729 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 91661 | 38.421 | -122.8998 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008017 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798150 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 671411 | 20230104 | 1947 | 20230107 | 1055 | 1924037 | 3788 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 161876 | 38.4149 | -122.8997 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008045 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798176 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230104 | 1951 | 20230105 | 809 | 1917931 | 738 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 76752 | 38.826 | -123.0003 | Yes | Clear;32-90 F |  |  | 23-0006578 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796875 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5731 | 20230104 | 1951 | 20230107 | 1513 | 1923982 | 4042 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 315276 | 38.3777 | -122.8342 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008024 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798156 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20230104 | 1951 | 20230107 | 1743 | 1915904 | 4192 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 58688 | 38.3653 | -123.0706 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007661 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797858 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3157 | 20230104 | 1956 | 20230107 | 1058 | 1918268 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18910 | 38.3369 | -122.844 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006938 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797239 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20230104 | 1958 | 20230105 | 1513 | 1917847 | 1155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 6933 | 38.509 | -122.8869 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007541 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797756 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 13821 | 20230104 | 2000 | 20230111 | 1448 | 1917949 | 9768 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 60432 | 38.4756 | -123.0192 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011108 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800919 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL 1102 | 42091102 | RECLOSER | 503294 | 20230104 | 2007 | 20230105 | 1144 | 1918083 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 181 | 169597 | 38.502 | -122.9359 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0007222 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797496 | 0 | EPSS Ckt | N | 2023 | A & C
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2371 | 20230104 | 2010 | 20230108 | 1456 | 1918054 | 5446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 32676 | 38.5423 | -122.8717 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007504 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797722 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 116 | 20230104 | 2010 | 20230108 | 1707 | 1918077 | 5577 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 389759 | 38.4736 | -122.8977 | Yes | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006565 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796863 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO 1103 | 42571103 | FUSE | 6943 | 20230104 | 2022 | 20230105 | 1918 | 1918160 | 1376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 20640 | 38.4636 | -122.8628 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007258 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797526 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 786457 | 20230104 | 2024 | 20230105 | 1245 | 1918192 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 45126 | 38.4017 | -122.8257 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007419 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797662 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | TRANSFORMER | 217587628082 | 20230104 | 2027 | 20230110 | 1431 | 1918223 | 8284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 49704 | 38.4344 | -122.8434 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0010947 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800785 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7777 | 20230104 | 2028 | 20230107 | 1700 | 1926356 | 4112 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 131584 | 38.3374 | -122.8432 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008726 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798610 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | TRANSFORMER | 218207926559 | 20230104 | 2033 | 20230109 | 1934 | 1918342 | 7141 | Transformer only | Equipment Failure/Involved | Electrical Overload | 5 | 35705 | 38.394 | -122.6266 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010850 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800701 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | OTHER | WIRE DOWN 5 SPANS LD SIDE FUCO 16231 | 20230104 | 2040 | 20230107 | 1804 | 1918330 | 4164 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 84513 | 38.5013 | -122.9237 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007445 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1797682 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | RECLOSER | 468882 | 20230104 | 2042 | 20230104 | 2304 | 1918408 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 3056 | 265185 | 38.4061 | -122.8266 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006328 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796892 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 15549 | 20230104 | 2042 | 20230105 | 954 | 1921493 | 792 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 41 | 32472 | 38.3881 | -122.813 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007182 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797463 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217817624929 | 20230104 | 2046 | 20230109 | 1907 | 1918444 | 7101 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 85212 | 38.3486 | -122.7621 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010384 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800232 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 2569 | 20230104 | 2046 | 20230105 | 925 | 1919641 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 214820 | 38.3644 | -122.8222 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006813 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797115 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE 1102 | 43181102 | FUSE | 13653 | 20230104 | 2048 | 20230105 | 1445 | 1918473 | 1077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 7539 | 38.3772 | -122.7543 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007568 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797779 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE 1102 | 42891102 | FUSE | 858093 | 20230104 | 2049 | 20230105 | 937 | 1918760 | 768 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 20 | 15360 | 38.6478 | -122.8503 | Yes | Clear;32-90 F |  |  | 23-0007167 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797454 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 55433 | 20230104 | 2052 | 20230105 | 1106 | 1921487 | 854 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 4270 | 38.3546 | -122.7783 | Yes | Clear;32-90 F |  |  | 23-0007179 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797460 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 6965 | 20230104 | 2052 | 20230105 | 1128 | 1918512 | 876 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 32412 | 38.3561 | -122.7677 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007242 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797513 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 7285 | 20230104 | 2055 | 20230108 | 2039 | 1919652 | 5744 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 74672 | 38.3647 | -122.821 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006816 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797118 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C 1109 | 42631109 | FUSE | 5785 | 20230104 | 2057 | 20230105 | 1054 | 1918571 | 837 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 25110 | 38.2245 | -122.6337 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007259 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797527 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 3279 | 20230104 | 2059 | 20230105 | 1531 | 1921169 | 1112 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 21128 | 38.3629 | -122.8288 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007078 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797372 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20230104 | 2102 | 20230105 | 1859 | 1918637 | 1317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 164624 | 38.2617 | -122.7157 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006626 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1796926 | 0 | EPSS Ckt | N | 2023 | A &B & GRD
SONOMA | SANTA ROSA | COTATI 1104 | 42271104 | FUSE | 817 | 20230104 | 2103 | 20230108 | 1511 | 1918628 | 5408 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 106600 | 38.322 | -122.71 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Service conductor | Broken- wire on ground | 23-0007083 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797376 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-1105 | 43301105 | FUSE | 7799 | 20230104 | 2110 | 20230111 | 1554 | 1918680 | 9764 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 19528 | 38.4524 | -122.7838 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008501 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798429 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 15445 | 20230104 | 2125 | 20230108 | 1634 | 1918805 | 5469 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 76566 | 38.4632 | -122.9407 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008469 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798404 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | TRANSFORMER | 218166820543 | 20230104 | 2146 | 20230109 | 1204 | 1919067 | 6618 | Transformer only | Equipment Failure/Involved | Fire- pole | 4 | 26472 | 38.2289 | -122.6392 | Yes | Clear;32-90 F | Transformer | Broken | 23-0007314 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797574 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1104 | 42271104 | FUSE | 2790 | 20230104 | 2220 | 20230107 | 2157 | 1919363 | 3664 | Distribution Circuit | Equipment Failure/Involved | Underground | 178 | 136266 | 38.327 | -122.7066 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Transformer (UG) | Broken | 23-0007100 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797394 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | FUSE | 4350 | 20230104 | 2249 | 20230105 | 1649 | 1919548 | 1080 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 56 | 60480 | 38.2392 | -122.6222 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 23-0007700 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797886 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | JUMPER | OJ SS 3273 | 20230104 | 2316 | 20230106 | 1326 | 1922591 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 1029 | 404411 | 38.3723 | -122.8063 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007532 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1797747 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A 1108 | 42151108 | TRANSFORMER | 217958928039 | 20230104 | 2346 | 20230105 | 1937 | 1918090 | 1191 | Transformer only | Equipment Failure/Involved | Overhead | 26 | 30966 | 38.4342 | -122.7137 | Yes | Clear;32-90 F | Transformer | Broken | 23-0006868 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797170 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1110 | 42151110 | TRANSFORMER | 218083228424 | 20230105 | 58 | 20230105 | 1710 | 2026761 | 972 | Transformer only | Vegetation | Tree - fell into line | 17 | 16524 | 38.4451 | -122.6703 | Yes | Overcast-Heavy Rain;32-90 F | Service conductor | Broken- wire on ground | 23-0041740 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1822942 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 2499 | 20230105 | 118 | 20230105 | 225 | 1920201 | 67 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 7638 | 38.3904 | -122.821 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0006941 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797242 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | TRANSFORMER | MTR#1007760555 | 20230105 | 438 | 20230107 | 1257 | 1920588 | 3379 | Transformer only | Vegetation | Tree - fell into line | 4 | 13516 | 38.3889 | -122.5506 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0007345 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797605 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1105 | 42631105 | FUSE | 13113 | 20230105 | 523 | 20230106 | 1253 | 1920651 | 1890 | Distribution Circuit | Equipment Failure/Involved | Underground | 111 | 195670 | 38.2389 | -122.6294 | Yes | Overcast-Fog-Rain;32-90 F | Elbow | Failed/Faulted | 23-0007372 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797623 | 1 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | OTHER | WIRE DOWN 1 SPAN SS OF CGC 217393326785 | 20230105 | 615 | 20230107 | 1947 | 1923901 | 3692 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14848 | 38.3984 | -122.9132 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007975 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798107 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 12727 | 20230105 | 648 | 20230109 | 1828 | 1920779 | 6460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 45220 | 38.6792 | -122.9401 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007210 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797485 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3249 | 20230105 | 700 | 20230105 | 2143 | 1920806 | 883 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 3532 | 38.3357 | -122.8021 | Yes | Clear;32-90 F |  |  | 23-0007981 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798112 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 4701 | 20230105 | 711 | 20230105 | 1453 | 1921809 | 462 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 924 | 38.2151 | -122.6252 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0007580 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797791 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | JUMPER | WIRE DOWN TWD CGC 217363023450 | 20230105 | 759 | 20230109 | 1801 | 1923416 | 6362 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12949 | 38.3071 | -122.9206 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007799 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1797964 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 439 | 20230105 | 831 | 20230107 | 1356 | 1921192 | 3205 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 48075 | 38.463 | -123.0122 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008809 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798667 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 45223 | 20230105 | 841 | 20230106 | 1216 | 1921241 | 1655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4965 | 38.3389 | -122.7778 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008177 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798257 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217892823574 | 20230105 | 930 | 20230108 | 1534 | 1921240 | 4684 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 28104 | 38.3115 | -122.735 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0007180 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1797461 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | TRANSFORMER | 218133420574 | 20230105 | 943 | 20230109 | 1542 | 1921498 | 6119 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 61190 | 38.2297 | -122.6509 | Yes | Overcast-Fog-Rain;32-90 F | Transformer | Failed/Faulted | 23-0007613 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797820 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 6493 | 20230105 | 1012 | 20230108 | 2043 | 1921639 | 4951 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5859 | 38.5209 | -122.9581 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007743 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797921 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | JUMPER | DOWN WIRE 2 SPAN LD SIDE 6379 | 20230105 | 1237 | 20230108 | 1508 | 1922504 | 4471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 49181 | 38.4664 | -123.0155 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007503 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1797721 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | RECLOSER | 48000 | 20230105 | 1334 | 20230107 | 2141 | 1922498 | 3367 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 52486 | 38.2262 | -122.6131 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0007500 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797717 | 0 | EPSS Ckt | N | 2023 | A & B
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 597 | 20230105 | 1334 | 20230107 | 2141 | 1923633 | 3367 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 24283 | 38.1855 | -122.5997 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007859 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1798023 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 867183 | 20230105 | 1454 | 20230105 | 1705 | 1922947 | 131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 3144 | 38.4111 | -122.9499 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007758 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1797931 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 13907 | 20230105 | 1456 | 20230109 | 1205 | 1922851 | 5589 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 184437 | 38.4946 | -123.0156 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008582 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798501 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217109230382 | 20230105 | 1501 | 20230106 | 1653 | 1922864 | 1552 | Transformer only | Equipment Failure/Involved | Overhead | 43 | 66736 | 38.4963 | -123.0108 | Yes | Heavy Rain-Clear;32-90 F | Secondary | Broken | 23-0011255 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801041 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230105 | 1512 | 20230106 | 1537 | 1922936 | 1465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 164080 | 38.5018 | -123.0238 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008460 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798397 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2107 | 43182107 | FUSE | 11687 | 20230105 | 1517 | 20230106 | 946 | s1798236 | 1109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 1109 | 38.3638 | -122.7133 | Yes | Clear;32-90 F |  |  | 23-0008146 |  | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798236 | 1 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20230105 | 1537 | 20230107 | 1520 | 1922997 | 2863 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 25767 | 38.4782 | -122.9384 | Yes | Clear;32-90 F |  |  | 23-0008860 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798720 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 2335 | 20230105 | 1615 | 20230109 | 1234 | 1923174 | 5539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 1046871 | 38.5207 | -122.9807 | Yes | Clear;32-90 F | Insulator | Broken | 23-0007783 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1797951 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 1687 | 20230105 | 1806 | 20230108 | 1752 | 1924441 | 4306 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 55978 | 38.3341 | -122.9774 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008526 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1798454 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2437 | 20230105 | 1841 | 20230106 | 1617 | 1923582 | 1296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 15552 | 38.2431 | -122.8861 | Yes | Clear;32-90 F |  |  | 23-0008165 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798251 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 7677 | 20230105 | 1844 | 20230106 | 955 | 1923588 | 911 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 9110 | 38.3884 | -122.5505 | Yes | Clear;32-90 F |  |  | 23-0007989 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798120 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2425 | 20230105 | 1901 | 20230106 | 1018 | 1923742 | 917 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 22925 | 38.2724 | -122.861 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0008123 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798220 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313087164478 | 20230105 | 1912 | 20230106 | 1203 | 1923699 | 1011 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4044 | 38.2464 | -122.9085 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0008260 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798304 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 867183 | 20230105 | 1930 | 20230105 | 2200 | 1923744 | 150 | Distribution Circuit | Vegetation | Tree - grew into line | 24 | 3600 | 38.4111 | -122.9499 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0007882 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798043 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2555 | 20230105 | 1937 | 20230106 | 1306 | 1923753 | 1049 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 7343 | 38.2439 | -122.882 | Yes | Clear;32-90 F |  |  | 23-0008294 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798321 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | TRANSFORMER | 313082764491 | 20230105 | 2001 | 20230106 | 1953 | 1924746 | 1432 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2864 | 38.2468 | -122.91 | Yes | Clear;32-90 F | Fuse | Burned Open | 23-0008257 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798302 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 4571 | 20230105 | 2006 | 20230110 | 1305 | 1923801 | 6779 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 13558 | 38.1682 | -122.8939 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008364 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798359 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6727 | 20230105 | 2015 | 20230108 | 1830 | 1923857 | 4215 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 59010 | 38.4389 | -122.8658 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007941 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798079 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 937000 | 20230105 | 2025 | 20230109 | 940 | 1923286 | 5115 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 122760 | 38.4887 | -123.017 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008685 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798567 | 0 | EPSS Ckt | N | 2023 | B
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 9138 | 20230105 | 2039 | 20230106 | 1125 | 1923859 | 886 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 22322 | 38.7995 | -123.0253 | Yes | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0008030 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798161 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 12027 | 20230106 | 830 | 20230108 | 1703 | 1924277 | 3393 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30537 | 38.4 | -122.9581 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008351 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798352 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313179065441 | 20230106 | 840 | 20230106 | 1620 | 1924289 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 460 | 38.2726 | -122.8771 | No | Clear;32-90 F | Connector or Splice (OH) | Deteriorated | 23-0008497 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798425 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | TRANSFORMER | T3399 | 20230106 | 1009 | 20230108 | 1307 | 1924500 | 3058 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 3058 | 38.2989 | -123.005 | No | Clear;32-90F |  |  | 23-0010130 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799978 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | RECLOSER | 87402 | 20230106 | 1036 | 20230108 | 1341 | 1924563 | 3065 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 95015 | 38.1632 | -122.8903 | No | Clear;32-90 F | Woodpin | Broken | 23-0008184 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798261 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 3419 | 20230106 | 1421 | 20230107 | 1025 | 1925072 | 1204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1204 | 38.2594 | -122.8593 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008705 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798588 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 3649 | 20230106 | 1424 | 20230106 | 2021 | 1925076 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 26418 | 38.4646 | -122.6947 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008570 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798489 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217599626757 | 20230106 | 1949 | 20230110 | 1845 | 1927786 | 5696 | Transformer only | Vegetation | Tree - fell into line | 3 | 17088 | 38.3982 | -122.8389 | No | Clear;32-90 F | Transformer | Normal | 23-0009031 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798858 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1102 | 42151102 | TRANSFORMER | T4248 | 20230106 | 2202 | 20230107 | 1119 | 1925794 | 797 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1594 | 38.4184 | -122.7547 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008745 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798626 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 9138 | 20230107 | 416 | 20230107 | 1613 | s1798637 | 430 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 27749 | 38.7995 | -123.0253 | Yes | Clear;32-90 F | Conductor- Underground | Broken | 23-0008761 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798637 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE 1101 | 42821101 | FUSE | 7295 | 20230107 | 557 | 20230107 | 1025 | 1925973 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 9112 | 38.8631 | -123.0866 | Yes | Clear;32-90 F |  |  | 23-0008715 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798598 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRANSFORMER | 217303529685 | 20230107 | 644 | 20230110 | 1242 | 1926045 | 4678 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 9356 | 38.4779 | -122.9429 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010260 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800108 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 17371 | 20230107 | 852 | 20230110 | 1124 | 1926182 | 4472 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8559 | 38.7684 | -122.9805 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009019 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798846 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217577525204 | 20230107 | 1001 | 20230108 | 1512 | 1926294 | 1751 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 7004 | 38.3559 | -122.8457 | Yes | Clear;32-90 F | Connector or Splice (OH) | Contaminated | 23-0010237 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800086 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6247 | 20230107 | 1009 | 20230107 | 1734 | 1926307 | 445 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 2225 | 38.4441 | -122.8923 | Yes | Clear;32-90 F |  |  | 23-0008950 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798786 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | JUMPER | 441 | 20230107 | 1211 | 20230107 | 1248 | 1926237 | 37 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 2553 | 38.3635 | -122.8218 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008703 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1798586 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | JUMPER | WIRE DOWN | 20230107 | 1301 | 20230109 | 1631 | 1934080 | 3090 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32030 | 38.375 | -123.0036 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010323 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1800172 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | TRANSFORMER | 217011924252 | 20230107 | 1330 | 20230108 | 1837 | 1926703 | 1747 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 12229 | 38.3277 | -123.0426 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0008985 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798814 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 2959 | 20230107 | 1452 | 20230107 | 1720 | 1926898 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 7844 | 38.7134 | -122.9762 | Yes | Clear;32-90 F |  |  | 23-0008919 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798762 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 3377 | 20230107 | 1500 | 20230107 | 2035 | 1926913 | 335 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 34840 | 38.3451 | -122.6667 | Yes | Clear;32-90 F |  |  | 23-0008893 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798745 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1995 | 20230107 | 1639 | 20230112 | 1700 | 1927207 | 7221 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 64989 | 38.5326 | -123.0037 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0008932 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1798771 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 7945 | 20230107 | 1648 | 20230110 | 1424 | 1927416 | 4176 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20880 | 38.3652 | -122.6643 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008973 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1798805 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | JUMPER | WIRE DOWN @ CGC# 218199430883 | 20230107 | 1711 | 20230109 | 1710 | 1927478 | 2879 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48254 | 38.5134 | -122.6305 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0008987 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798816 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1104 | 43181104 | TRANSFORMER | 217895626593 | 20230107 | 1713 | 20230109 | 1023 | 1927249 | 2470 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 9880 | 38.3945 | -122.7355 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0009276 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799107 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | OCB | 2101/2 | 20230107 | 1718 | 20230107 | 2001 | 1927303 | 163 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1154 | 159962 | 38.3787 | -122.7123 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0008951 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | No | No | 1798787 | 0 | Non-EPSS | N | 2023 | A-B-C
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 441501 | 20230107 | 1718 | 20230111 | 1247 | 1927583 | 5489 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 27445 | 38.3757 | -122.7019 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 23-0009006 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798834 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217809024770 | 20230107 | 1722 | 20230108 | 1021 | 1927378 | 1019 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2038 | 38.3442 | -122.7651 | Yes | Clear;32-90F | Secondary | Normal | 23-0010010 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799855 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A 1107 | 42151107 | TRANSFORMER | 218037528266 | 20230107 | 1730 | 20230109 | 1827 | 1927321 | 2937 | Transformer only | Equipment Failure/Involved | Electrical Overload | 16 | 46992 | 38.4406 | -122.6862 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0009083 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1798912 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 6965 | 20230107 | 1738 | 20230107 | 2108 | 1927357 | 210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 5183 | 38.3561 | -122.7677 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0009042 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798869 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217207526255 | 20230107 | 1738 | 20230109 | 918 | 1927360 | 2380 | Transformer only | Equipment Failure/Involved | Fire- pole | 1 | 2380 | 38.3829 | -122.9757 | Yes | Clear;32-90 F | Transformer | Broken | 23-0010482 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800331 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON 1105 | 42561105 | RECLOSER | 142 | 20230107 | 1758 | 20230107 | 1921 | 1927364 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 18011 | 38.483 | -122.8191 | Yes | Clear;32-90 F | Connector or Splice (OH) | Burned/flashed | 23-0009039 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1798866 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217529726130 | 20230107 | 1815 | 20230110 | 1354 | 1927504 | 4059 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 12177 | 38.3809 | -122.8628 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0009917 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799769 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE 2103 | 43182103 | FUSE | 9841 | 20230107 | 1914 | 20230110 | 1550 | 1927797 | 4116 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16464 | 38.3794 | -122.6904 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010423 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800269 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | TRANSFORMER | 217673429046 | 20230107 | 1915 | 20230109 | 1215 | 1927930 | 2460 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 14760 | 38.4612 | -122.8138 | Yes | Clear;32-90 F | Transformer | Broken | 23-0009129 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798957 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | TRANSFORMER | 217191825085 | 20230107 | 1942 | 20230108 | 1910 | 1927929 | 1408 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 1408 | 38.3513 | -122.9804 | Yes | Clear;32-90F |  |  | 23-0010059 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799902 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 12909 | 20230107 | 2040 | 20230107 | 2214 | 1928025 | 94 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 6486 | 38.387 | -122.8351 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0009177 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799005 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 7295 | 20230107 | 2132 | 20230108 | 849 | 1928113 | 677 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 23018 | 38.8631 | -123.0866 | Yes | Clear;32-90F |  |  | 23-0009897 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799746 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20230107 | 2235 | 20230109 | 1824 | 1928421 | 2629 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23661 | 38.509 | -122.8869 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009759 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1799595 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | TRANSFORMER | 217148940080 | 20230107 | 2255 | 20230110 | 1505 | 1931132 | 3850 | Transformer only | Environmental/External | Lightning | 1 | 3850 | 38.7621 | -123.0023 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0010108 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799956 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 661 | 20230107 | 2258 | 20230108 | 1006 | 1928907 | 668 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 4008 | 38.2708 | -122.7083 | Yes | Clear;32-90F |  |  | 23-0009974 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799822 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230107 | 2301 | 20230108 | 745 | 1931106 | 524 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 147 | 71997 | 38.826 | -123.0003 | Yes | Clear;32-90 F |  |  | 23-0009531 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799363 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1105 | 42151105 | INTERRUPTER | 10253 | 20230107 | 2301 | 20230108 | 842 | 1928637 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 957 | 556017 | 38.4351 | -122.7201 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0009876 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799727 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 1979 | 20230107 | 2305 | 20230110 | 1746 | 1928699 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 111077 | 38.4905 | -122.8939 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009945 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1799795 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | WINDSOR 1102 | 43501102 | RECLOSER | 596 | 20230107 | 2308 | 20230108 | 749 | 1928804 | 521 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 610 | 317810 | 38.5473 | -122.8179 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0009871 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799722 | 0 | EPSS Ckt | N | 2023 | A & B
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1547 | 20230107 | 2314 | 20230108 | 818 | 1932571 | 544 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 49 | 10786 | 38.4351 | -122.8818 | Yes | Clear;32-90F |  |  | 23-0009874 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799725 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3259 | 20230107 | 2315 | 20230110 | 1347 | 1928952 | 3752 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 120064 | 38.4002 | -122.954 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010095 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799942 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | RECLOSER | 464 | 20230107 | 2317 | 20230108 | 37 | 1929015 | 80 | Distribution Circuit | Environmental/External | Lightning | 5317 | 425360 | 38.3002 | -122.7115 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole - Tower- steel | Burned/flashed | 23-0009371 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799204 | 0 | EPSS Ckt | N | 2023 | B C
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20230107 | 2317 | 20230108 | 1146 | 1928980 | 749 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 6741 | 38.4782 | -122.9384 | Yes | Clear;32-90F |  |  | 23-0010086 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799932 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | RECLOSER | 167726 | 20230107 | 2324 | 20230107 | 2339 | 1929353 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 130 | 1950 | 38.2838 | -122.7101 | Yes | Clear;32-90F |  |  | 23-0009399 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799232 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | FUSE | 14703 | 20230108 | 14 | 20230109 | 1208 | 1930636 | 2154 | Distribution Circuit | Equipment Failure/Involved | Underground | 70 | 93726 | 38.4681 | -122.6444 | Yes | Overcast-Rain;32-90 F | Elbow | Broken | 23-0009968 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799817 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | TRANSFORMER | 100000057262 | 20230108 | 45 | 20230109 | 1505 | 1931201 | 2300 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2300 | 38.3143 | -122.6848 | Yes | Clear;32-90 F | Transformer | Broken | 23-0011204 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801004 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1111 | 42751111 | RECLOSER | 424 | 20230108 | 346 | 20230108 | 1919 | 1932132 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 104496 | 38.5712 | -122.8415 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009797 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1799636 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217459927593 | 20230108 | 407 | 20230111 | 1528 | 1932428 | 5001 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 5001 | 38.4203 | -122.8885 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0010345 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800194 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 2719 | 20230108 | 439 | 20230108 | 1535 | 1932189 | 656 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 7001 | 38.2027 | -122.7812 | Yes | Clear;32-90F | Insulator | Broken | 23-0010045 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799890 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 18267 | 20230108 | 446 | 20230108 | 1211 | 1932195 | 445 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 8900 | 38.4156 | -122.5116 | Yes | Clear;32-90F |  |  | 23-0010087 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799933 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR 1101 | 43071101 | FUSE | 3075 | 20230108 | 459 | 20230108 | 1646 | 1932204 | 707 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 10605 | 38.3861 | -122.4872 | Yes | Clear;32-90 F |  |  | 23-0010335 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800184 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 463297 | 20230108 | 710 | 20230108 | 950 | 1932471 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5440 | 38.3496 | -122.7888 | Yes | Clear;32-90F |  |  | 23-0009972 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799820 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | FUSE | 5891 | 20230108 | 802 | 20230108 | 1253 | 1931726 | 291 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 3783 | 38.4828 | -122.8254 | Yes | Clear;32-90 F |  |  | 23-0010134 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799982 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRANSFORMER | 217106529029 | 20230108 | 941 | 20230110 | 1718 | 1932971 | 3337 | Transformer only | Vegetation | Tree - fell into line | 7 | 23359 | 38.4591 | -123.0114 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011967 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801747 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3055 | 20230108 | 1137 | 20230108 | 1759 | 1933354 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7258 | 38.4069 | -122.9279 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0010077 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1799922 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 1595 | 20230108 | 1155 | 20230109 | 1814 | 1933538 | 1819 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9095 | 38.477 | -122.9332 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010140 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1799989 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 8089 | 20230108 | 1236 | 20230108 | 1309 | 1933517 | 33 | Distribution Circuit | Equipment Failure/Involved | Underground | 3 | 110 | 38.3099 | -123.0123 | Yes | Clear;32-90 F | Transformer (UG) | Broken | 23-0010133 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799981 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313098764592 | 20230108 | 1319 | 20230110 | 631 | 1927917 | 2472 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4944 | 38.2496 | -122.9045 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0010174 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800025 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 55433 | 20230108 | 1324 | 20230108 | 1502 | 1932618 | 98 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 490 | 38.3546 | -122.7783 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010245 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800096 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 2619 | 20230108 | 1327 | 20230110 | 1707 | 1933652 | 3100 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 9300 | 38.1732 | -122.6724 | Yes | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0010431 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800276 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | JUMPER | OJ'S FEEDING MTR 1010197229 | 20230108 | 1424 | 20230108 | 1659 | 1933767 | 155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 310 | 38.4032 | -122.879 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0010211 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1800062 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRANSFORMER | 217311930131 | 20230108 | 1546 | 20230111 | 1640 | 1933989 | 4374 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4374 | 38.4907 | -122.9429 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0011202 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801001 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3249 | 20230108 | 1600 | 20230108 | 1645 | 1934124 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 180 | 38.3357 | -122.8021 | Yes | Clear;32-90 F |  |  | 23-0010338 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800187 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 1967 | 20230108 | 1805 | 20230108 | 1947 | 1934343 | 102 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 80 | 8160 | 38.4261 | -122.963 | Yes | Clear;32-90 F |  |  | 23-0010453 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800299 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217349927153 | 20230108 | 1824 | 20230110 | 1108 | 1934386 | 2444 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 2444 | 38.4079 | -122.9261 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0010416 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800263 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1525 | 20230108 | 1845 | 20230109 | 2012 | 1934489 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 83985 | 38.4106 | -122.9828 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010621 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1800477 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 15407 | 20230108 | 1854 | 20230109 | 1139 | 1934474 | 1005 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 4020 | 38.4111 | -122.9549 | Yes | Clear;32-90 F |  |  | 23-0011130 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800939 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2485 | 20230108 | 1921 | 20230108 | 2027 | 1934582 | 66 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 92 | 6072 | 38.6502 | -122.869 | Yes | Clear;32-90 F |  |  | 23-0010479 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800327 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5787 | 20230108 | 1955 | 20230109 | 1813 | 1934632 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17394 | 38.3755 | -122.9051 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010486 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1800336 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217394226553 | 20230108 | 2013 | 20230109 | 1746 | 1934721 | 1293 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 5172 | 38.3926 | -122.9115 | Yes | Clear;32-90 F | Transformer | Broken | 23-0011397 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801163 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217412926275 | 20230108 | 2049 | 20230111 | 1041 | 1934774 | 3712 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3712 | 38.3858 | -122.9041 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0011501 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801258 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 661 | 20230109 | 49 | 20230109 | 843 | 1935165 | 474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 2844 | 38.2708 | -122.7083 | Yes | Clear;32-90F |  |  | 23-0010915 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800759 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | OTHER | 4 SPAN LD SIDE OF HARD TAP | 20230109 | 107 | 20230111 | 1205 | 1938075 | 3538 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24106 | 38.4667 | -122.919 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011169 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1800973 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 671411 | 20230109 | 111 | 20230109 | 1045 | 1935163 | 574 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 10906 | 38.4149 | -122.8997 | Yes | Clear;32-90F |  |  | 23-0011054 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800876 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 1351 | 20230109 | 146 | 20230110 | 1522 | 1935192 | 2256 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 78960 | 38.279 | -122.4371 | Yes | Overcast-Heavy Rain;32-90 F | Fuse | Broken | 23-0010974 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800814 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 819757 | 20230109 | 323 | 20230111 | 1303 | 1935430 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 183380 | 38.4721 | -123.0032 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010767 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1800632 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1104 | 42721104 | TRANSFORMER | 218612522901 | 20230109 | 422 | 20230111 | 1300 | 1935586 | 3398 | Transformer only | Vegetation | Tree - fell into line | 3 | 10194 | 38.2944 | -122.4845 | Yes | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0011100 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800912 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE 1105 | 43371105 | FUSE | 8325 | 20230109 | 423 | 20230109 | 822 | 1935587 | 239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 446 | 90202 | 38.2566 | -122.6193 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Fuse | Broken | 23-0010792 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800654 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20230109 | 433 | 20230110 | 1656 | 1935627 | 2183 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 96052 | 38.5078 | -122.9896 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010916 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800760 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217798624104 | 20230109 | 438 | 20230110 | 1741 | 1935646 | 2223 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4446 | 38.3259 | -122.7685 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0010990 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1800826 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRANSFORMER | 217464030016 | 20230109 | 836 | 20230110 | 1605 | 1937046 | 1889 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 7556 | 38.4873 | -122.8871 | Yes | Clear;32-90 F | Transformer | Broken | 23-0012164 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801931 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | RECLOSER | 332 | 20230109 | 922 | 20230109 | 932 | 1935494 | 10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 941 | 9410 | 38.509 | -122.9241 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010952 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1800791 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 937000 | 20230109 | 943 | 20230109 | 1513 | 1937608 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7920 | 38.4887 | -123.017 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0008685 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800861 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 1261 | 20230109 | 1100 | 20230109 | 1612 | s1800896 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 3744 | 38.4241 | -122.554 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0011081 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1800896 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 10135 | 20230109 | 1110 | 20230109 | 2220 | 1937780 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4020 | 38.3391 | -122.9183 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0011682 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | No | No | 1801445 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20230109 | 1140 | 20230110 | 1718 | 1937961 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 28448 | 38.4634 | -123.0122 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011162 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800964 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 781629 | 20230109 | 1154 | 20230109 | 1841 | 1939291 | 407 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1221 | 38.3747 | -122.9078 | Yes | Clear;32-90 F |  |  | 23-0011531 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1801290 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 15455 | 20230109 | 1246 | 20230111 | 1600 | 1938139 | 3074 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15370 | 38.4761 | -122.952 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0011247 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1801035 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3249 | 20230109 | 1429 | 20230109 | 1440 | 1938455 | 11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 33 | 38.3357 | -122.8021 | Yes | Clear;32-90 F |  |  | 23-0011314 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1801090 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRANSFORMER | 216444332454 | 20230109 | 1434 | 20230112 | 1205 | 1938470 | 4171 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 4171 | 38.551 | -123.2447 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 23-0014406 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803709 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 2733 | 20230109 | 1456 | 20230110 | 1816 | 1938536 | 1640 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 59040 | 38.231 | -122.6648 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011376 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1801144 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 9391 | 20230109 | 1537 | 20230109 | 1622 | 1938690 | 45 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 360 | 38.5005 | -123.0053 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0011390 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1801156 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | TRANSFORMER | 217295037859 | 20230109 | 1606 | 20230111 | 1339 | 1938766 | 2733 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 8199 | 38.7039 | -122.947 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0011491 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801249 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | TRANSFORMER | 218531727340 | 20230109 | 1609 | 20230111 | 1418 | 1938772 | 2769 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2769 | 38.4171 | -122.5154 | Yes | Clear;32-90 F | Transformer | Broken | 23-0013459 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802972 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 14289 | 20230109 | 1705 | 20230111 | 1357 | 1939092 | 2692 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5384 | 38.3943 | -122.5319 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011488 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801246 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20230109 | 1754 | 20230109 | 1902 | s1801346 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1301 | 88468 | 38.3443 | -122.5144 | Yes | Clear;32-90 F |  |  | 23-0011582 |  | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801346 | 0 | EPSS Ckt | N | 2023 | A & GRD
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 17613 | 20230109 | 1809 | 20230111 | 1756 | 1939192 | 2867 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 43005 | 38.4506 | -123.1155 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011540 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1801301 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217500928547 | 20230109 | 1909 | 20230111 | 1200 | 1938409 | 2451 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 4902 | 38.4473 | -122.8735 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0011552 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801315 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | JUMPER | 2 BURNED OPEN JUMPERS | 20230109 | 2224 | 20230111 | 1136 | 1939806 | 2232 | Distribution Circuit | Vegetation | Tree - fell into line | 1301 | 34868 | 38.3297 | -122.504 | Yes | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011702 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1801462 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217299129084 | 20230109 | 2301 | 20230117 | 133 | 1939632 | 10232 | Transformer only | Vegetation | Tree - fell into line | 1 | 10232 | 38.4616 | -122.9446 | Yes | Clear;32-90 F | Service conductor | Broken | 23-0011689 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1801451 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | RECLOSER | SO-ND104846 | 20230110 | 153 | 20230111 | 1518 | 1939998 | 2245 | Distribution Circuit | Vegetation | Tree - fell into line | 1845 | 2156495 | 38.3433 | -123.0445 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0011729 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | No | No | 1801489 | 0 | EPSS Ckt | N | 2023 | A B C GRD
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230110 | 204 | 20230110 | 809 | 1939979 | 365 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 104 | 37960 | 38.826 | -123.0003 | Yes | Clear;32-90 F |  |  | 23-0012021 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1801803 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20230110 | 204 | 20230111 | 1235 | 1940156 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 223642 | 38.4637 | -123.0083 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011757 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1801518 | 0 | EPSS Ckt | N | 2023 | B & C
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 2093 | 20230110 | 359 | 20230110 | 1010 | 1941419 | 371 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 65 | 24003 | 38.3497 | -122.7793 | Yes | Clear;32-90F |  |  | 23-0012165 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801932 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | FUSE | 4350 | 20230110 | 520 | 20230110 | 922 | 1942651 | 242 | Distribution Circuit | 3rd Party | Other | 56 | 13552 | 38.2392 | -122.6222 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012071 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801848 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3249 | 20230110 | 524 | 20230111 | 1047 | 1942823 | 1763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7052 | 38.3357 | -122.8021 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0013393 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802928 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | OCB | 1106/2 | 20230110 | 547 | 20230110 | 1357 | 1942827 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 3409 | 362206 | 38.4374 | -122.7128 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0011942 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1801718 | 0 | Non-EPSS | N | 2023 | B & C INST
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 293941 | 20230110 | 549 | 20230110 | 1235 | 1942845 | 406 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 4060 | 38.5105 | -123.0679 | Yes | Clear;32-90F |  |  | 23-0012364 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802099 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 7389 | 20230110 | 608 | 20230112 | 1535 | 1942930 | 3447 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 68940 | 38.5126 | -122.9338 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0012327 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802074 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217706026382 | 20230110 | 618 | 20230110 | 1321 | 1943015 | 423 | Transformer only | Vegetation | Tree - branch fell on line | 9 | 3807 | 38.3881 | -122.8016 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0012503 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802201 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230110 | 734 | 20230110 | 1352 | 1943375 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 18144 | 38.4756 | -122.9526 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012526 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802222 | 0 | EPSS Ckt | N | 2023 | A & C
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 2561 | 20230110 | 738 | 20230111 | 1405 | 1943359 | 1824 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38304 | 38.4113 | -122.9652 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012151 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801919 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | RECLOSER | 861496 | 20230110 | 816 | 20230113 | 1631 | 1943550 | 4815 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 32180 | 38.358 | -122.5256 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012037 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801819 | 0 | EPSS Ckt | N | 2023 | C
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20230110 | 833 | 20230110 | 1604 | 1943811 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 48411 | 38.4984 | -122.9914 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012060 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1801840 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | TRANSFORMER | 218361130702 | 20230110 | 850 | 20230111 | 1313 | 1943933 | 1703 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 5109 | 38.5084 | -122.5753 | Yes | Clear;32-90 F | Transformer | Broken | 23-0012577 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802255 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 6537 | 20230110 | 901 | 20230110 | 1505 | 1943996 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2548 | 38.7623 | -122.9945 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0012083 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1801857 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217160927732 | 20230110 | 911 | 20230110 | 1743 | 1944068 | 512 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 512 | 38.4238 | -122.9923 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012439 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802155 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | FUSE | 5891 | 20230110 | 919 | 20230110 | 1125 | 1944106 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1093 | 38.4828 | -122.8254 | Yes | Clear;32-90F |  |  | 23-0012229 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1801993 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1313 | 20230110 | 1001 | 20230110 | 1055 | 1944355 | 54 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 5940 | 38.504 | -122.9884 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012218 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1801980 | 0 | EPSS Ckt | N | 2023 | NA
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | SWITCH | 2861 | 20230110 | 1002 | 20230110 | 1124 | 1944384 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 328 | 38.764 | -122.9793 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012084 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1801940 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216946230263 | 20230110 | 1117 | 20230111 | 827 | 1944779 | 1270 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 6350 | 38.4925 | -123.0679 | Yes | Clear;32-90 F |  |  | 23-0012278 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1802036 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 933981 | 20230110 | 1136 | 20230110 | 1432 | 1944840 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 176 | 38.2226 | -122.6337 | Yes | Clear;32-90F |  |  | 23-0012569 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802249 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA 1107 | 42721107 | FUSE | 11567 | 20230110 | 1140 | 20230111 | 1058 | 1944101 | 1398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1398 | 38.2077 | -122.4524 | Yes | Clear;32-90F | Jumper | Broken | 23-0012335 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1802080 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | TRANSFORMER | 218589724174 | 20230110 | 1155 | 20230112 | 1043 | 1944920 | 2808 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 28080 | 38.3293 | -122.493 | Yes | Partly Cloudy-Rain;32-90 F | Transformer | Broken | 23-0014377 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803693 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON 1102 | 42561102 | FUSE | 975301 | 20230110 | 1327 | 20230110 | 1847 | 1945246 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 15040 | 38.6133 | -122.7678 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012479 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1802182 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | TRANSFORMER | 217934028328 | 20230110 | 1432 | 20230110 | 1504 | 1945514 | 32 | Transformer only | Unknown Cause | Patrol - found nothing | 11 | 352 | 38.4421 | -122.7225 | Yes | Clear;32-90F |  |  | 23-0012639 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1802301 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 17799 | 20230110 | 1505 | 20230111 | 1535 | 1945711 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4410 | 38.403 | -122.9444 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012703 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1802342 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4555 | 20230110 | 1535 | 20230111 | 1545 | 1945763 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2900 | 38.5639 | -123.2711 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012696 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1802335 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 3865 | 20230110 | 1606 | 20230110 | 1635 | 1945833 | 29 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 174 | 38.4712 | -123.0472 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012746 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1802360 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2349 | 20230110 | 1712 | 20230110 | 1921 | 1946069 | 129 | Distribution Circuit | Environmental/External | Lightning | 24 | 3096 | 38.6287 | -122.8829 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0012948 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802514 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2347 | 20230110 | 1717 | 20230110 | 2326 | 1946090 | 369 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 3690 | 38.6277 | -122.8793 | Yes | Clear;32-90F |  |  | 23-0013193 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802748 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217308826814 | 20230110 | 1803 | 20230111 | 1135 | 1946227 | 1052 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1052 | 38.3983 | -122.9401 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013056 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802611 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230110 | 1814 | 20230110 | 1933 | 1946272 | 79 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 103 | 8137 | 38.826 | -123.0003 | Yes | Clear;32-90F |  |  | 23-0012954 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1802521 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2349 | 20230110 | 1952 | 20230111 | 1623 | 1946423 | 1231 | Distribution Circuit | Environmental/External | Lightning | 24 | 29544 | 38.6287 | -122.8829 | Yes | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0013534 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1803023 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE 1101 | 43371101 | TRANSFORMER | 314143562000 | 20230110 | 2249 | 20230111 | 332 | 1946711 | 283 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 283 | 38.1854 | -122.5389 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0013343 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1802895 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | TRANSFORMER | 217478035055 | 20230111 | 1032 | 20230111 | 1844 | 1947338 | 492 | Transformer only | Environmental/External | Lightning | 3 | 1476 | 38.6266 | -122.883 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0013509 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803009 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 769 | 20230111 | 1134 | 20230111 | 2110 | 1947762 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16128 | 38.5962 | -122.9148 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013708 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1803119 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 913 | 20230111 | 1500 | 20230112 | 1505 | 1948456 | 1445 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4335 | 38.5168 | -122.8908 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013786 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1803182 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217234727142 | 20230111 | 1524 | 20230111 | 1611 | 1948474 | 47 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 188 | 38.4069 | -122.965 | No | Clear;32-90 F |  |  | 23-0013821 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1803205 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 2913 | 20230111 | 1820 | 20230111 | 1852 | 1948698 | 32 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 192 | 38.7033 | -122.9205 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013936 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1803290 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRANSFORMER | 217122829321 | 20230111 | 1823 | 20230112 | 1430 | 1948904 | 1207 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 10863 | 38.4672 | -123.0061 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0013986 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803337 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A 1110 | 42151110 | TRANSFORMER | T1024 | 20230111 | 1940 | 20230111 | 2214 | 1949002 | 154 | Transformer only | Equipment Failure/Involved | Underground | 13 | 2002 | 38.4366 | -122.6622 | No | Clear;32-90 F | Service conductor | Broken | 23-0014090 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803436 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | FUSE | 333 | 20230112 | 804 | 20230112 | 900 | 1949513 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 60 | 3360 | 38.4663 | -122.8161 | No | Clear;32-90F |  |  | 23-0014292 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1803629 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | JUMPER | OJ'S SS OF CGC 217245340677 | 20230112 | 946 | 20230112 | 1145 | 1949730 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 476 | 38.7816 | -122.9646 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0014339 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1803657 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE-1105 | 43371105 | TRANSFORMER | T0306 | 20230112 | 955 | 20230112 | 1054 | 1949752 | 59 | Transformer only | Unknown Cause | Patrol - found nothing | 18 | 1062 | 38.2451 | -122.6115 | No | Clear;32-90 F |  |  | 23-0014398 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1803704 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 477 | 20230112 | 1015 | 20230112 | 1116 | 1949785 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 286 | 17446 | 38.4926 | -123.008 | No | Clear;32-90 F |  |  | 23-0014385 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1803698 | 0 | EPSS Ckt | N | 2023 | POS 2 AND 3
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 4509 | 20230112 | 1158 | 20230112 | 1950 | 1950032 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 9912 | 38.526 | -123.2105 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014480 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1803756 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 13075 | 20230112 | 1205 | 20230112 | 1420 | 1950055 | 135 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 135 | 38.549 | -123.2446 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014485 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1803757 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRANSFORMER | 216444132376 | 20230112 | 1225 | 20230112 | 1650 | 1950096 | 265 | Transformer only | Vegetation | Tree - fell into line | 1 | 265 | 38.5488 | -123.2445 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0014535 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803778 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 2989 | 20230112 | 1452 | 20230113 | 1816 | 1950403 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6576 | 38.5326 | -123.1351 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014764 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1803888 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | SWITCH | 6967 | 20230112 | 1454 | 20230112 | 1815 | 1950405 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 12663 | 38.8424 | -122.9906 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0014640 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1803813 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217260831960 | 20230112 | 1515 | 20230113 | 1831 | 1950447 | 1636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 25696 | 38.5402 | -122.9577 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0015205 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804227 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON 1102 | 43321102 | TRANSFORMER | 218091929874 | 20230113 | 439 | 20230113 | 1501 | 1951270 | 622 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1244 | 38.4849 | -122.6678 | No | Clear;32-90 F | Transformer | Broken | 23-0015062 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804167 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 374323 | 20230113 | 734 | 20230113 | 854 | 1951345 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 48 | 3840 | 38.3249 | -122.9279 | No | Clear;32-90F |  |  | 23-0015104 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804179 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230113 | 840 | 20230113 | 1154 | 1951433 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 20176 | 38.826 | -123.0003 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0015099 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1804177 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRANSFORMER | 217132429400 | 20230113 | 920 | 20230113 | 1102 | 1951494 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 12 | 1224 | 38.4696 | -123.0026 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0015131 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1804192 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ'S LINE & BUS 1 POLSE S/OF FUCO 18673 | 20230113 | 952 | 20230113 | 1236 | 1951610 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 164 | 38.5968 | -123.3025 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015168 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | Yes | No | 1804210 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 366758 | 20230113 | 1047 | 20230113 | 1726 | 1951716 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 13566 | 38.4586 | -122.9351 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015221 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804232 | 0 | EPSS Ckt | N | 2023 | C
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2349 | 20230113 | 1133 | 20230113 | 1810 | 1951802 | 397 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 4968 | 38.6287 | -122.8829 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0015261 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1804245 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | RECLOSER | 350 | 20230113 | 1142 | 20230113 | 1706 | 1951820 | 324 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 25635 | 38.6707 | -122.8117 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0015272 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804251 | 0 | EPSS Ckt | N | 2023 | C/GRD
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 2733 | 20230113 | 1232 | 20230113 | 1323 | 1951904 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 1836 | 38.231 | -122.6648 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0015356 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804281 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1110 | 42151110 | TRANSFORMER | 218032028214 | 20230113 | 1315 | 20230113 | 1937 | 1951915 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 382 | 38.4393 | -122.6883 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0015388 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804296 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217771024740 | 20230113 | 1550 | 20230114 | 605 | 1952098 | 855 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 5985 | 38.3434 | -122.7785 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0015493 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804351 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | TRANSFORMER | 218388527449 | 20230113 | 1629 | 20230113 | 1745 | 1952314 | 76 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 76 | 38.4191 | -122.5634 | No | Clear;32-90 F |  |  | 23-0015515 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1804364 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20230113 | 1742 | 20230114 | 1250 | 1952440 | 1148 | Distribution Circuit | 3rd Party | Vehicle | 12 | 13776 | 38.5498 | -122.6679 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0015514 | OH | Sus | 0 | NORTH COAST | JAN | Three Phase Fault | 0 | No | No | No | 1804363 | 0 | EPSS Ckt | N | 2023 | A-B-C & INST
SONOMA | SANTA ROSA | LAKEVILLE-1105 | 43371105 | FUSE | 5019 | 20230113 | 1948 | 20230114 | 1219 | 1952551 | 991 | Distribution Circuit | Equipment Failure/Involved | Underground | 150 | 34202 | 38.2461 | -122.6112 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (UG) | Failed/Faulted | 23-0015549 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804391 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-1106 | 43301106 | FUSE | 9079 | 20230113 | 2153 | 20230114 | 1438 | 1952610 | 1005 | Distribution Circuit | 3rd Party | Vehicle | 392 | 295960 | 38.4624 | -122.7302 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0015625 | UG | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804509 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | INTERRUPTER | 647666 | 20230113 | 2327 | 20230114 | 208 | 1952658 | 161 | Distribution Circuit | Equipment Failure/Involved | Underground | 613 | 88317 | 38.3352 | -122.6869 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Underground | Deteriorated | 23-0015726 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804569 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2911 | 20230114 | 224 | 20230114 | 427 | 1952722 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 2337 | 38.6453 | -122.9187 | Yes | Clear;32-90F |  |  | 23-0015830 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804674 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 41392 | 20230114 | 641 | 20230114 | 1837 | 1952844 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 512 | 120314 | 38.4457 | -122.868 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0015851 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1804694 | 0 | EPSS Ckt | N | 2023 | A- GRD
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20230114 | 646 | 20230115 | 1333 | s1808661 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 1823 | 423587 | 38.4031 | -122.9214 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0015851 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808661 | 0 | EPSS Ckt | N | 2023 | A- GRD
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 3455 | 20230114 | 654 | 20230114 | 944 | 1952913 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 30 | 5100 | 38.4436 | -123.0631 | Yes | Clear;32-90F |  |  | 23-0016008 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804825 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 12637 | 20230114 | 657 | 20230114 | 1057 | 1952907 | 240 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 8880 | 38.5018 | -123.0047 | Yes | Clear;32-90F |  |  | 23-0016074 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804877 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 2113 | 20230114 | 732 | 20230114 | 828 | 1953034 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 92 | 3535 | 38.3837 | -122.6868 | Yes | Clear;32-90F |  |  | 23-0015892 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804727 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONROE 2107 | 43302107 | FUSE | 9075 | 20230114 | 755 | 20230114 | 1601 | 1953140 | 486 | Distribution Circuit | Equipment Failure/Involved | Underground | 269 | 122556 | 38.4655 | -122.7138 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0015926 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804759 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 15599 | 20230114 | 756 | 20230114 | 1125 | 1953001 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 5225 | 38.5123 | -122.9847 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016106 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804901 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230114 | 815 | 20230114 | 1117 | 1953196 | 182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 18746 | 38.826 | -123.0003 | Yes | Clear;32-90F | Connector or Splice (OH) | Deteriorated | 23-0015902 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1804734 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 9659 | 20230114 | 815 | 20230114 | 1438 | 1953344 | 383 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 9575 | 38.3844 | -122.4654 | Yes | Clear;32-90F |  |  | 23-0016261 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1805022 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3061 | 20230114 | 826 | 20230114 | 1005 | 1953282 | 99 | Distribution Circuit | Vegetation | Tree - branch fell on line | 147 | 14553 | 38.3582 | -122.7789 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016017 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804834 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6863 | 20230114 | 832 | 20230114 | 1702 | 1954748 | 510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 22950 | 38.4296 | -122.9328 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016313 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1805070 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | SWITCH | 7621 | 20230114 | 900 | 20230114 | 1601 | 1953553 | 421 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 168 | 70728 | 38.4778 | -122.9421 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015339 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1804799 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE-1101 | 43471101 | RECLOSER | 3476 | 20230114 | 900 | 20230114 | 1447 | 1953511 | 347 | Distribution Circuit | Equipment Failure/Involved | Underground | 2265 | 112032 | 38.3207 | -122.6669 | Yes | Clear;32-90F | Elbow | Failed/Faulted | 23-0015959 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804787 | 0 | EPSS Ckt | N | 2023 | C & GRD
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 1479 | 20230114 | 943 | 20230114 | 1147 | 1953703 | 124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1364 | 38.7638 | -122.8997 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016125 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804914 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | JUMPER | WIRE DOWN SS OF CGC 217376729268 | 20230114 | 1048 | 20230114 | 1650 | 1954369 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2534 | 38.4676 | -122.9173 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016194 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | No | 1804967 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | FUSE | 16619 | 20230114 | 1107 | 20230114 | 2112 | 1953484 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 14270 | 38.3681 | -122.5229 | Yes | Clear;32-90F | Fuse | Burned Open | 23-0016148 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804932 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 100000122903 | 20230114 | 1116 | 20230114 | 1235 | 1954112 | 79 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 158 | 38.5272 | -123.002 | Yes | Clear;32-90F | Transformer (OH) |  | 23-0016177 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1804954 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA-1103 | 43491103 | FUSE | 15139 | 20230114 | 1144 | 20230114 | 1230 | 1954183 | 46 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 5014 | 38.296 | -122.6668 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016149 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1804933 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1102 | 43181102 | TRANSFORMER | 217900525781 | 20230114 | 1304 | 20230114 | 1351 | 1954327 | 47 | Transformer only | Vegetation | Tree - branch fell on line | 7 | 329 | 38.3723 | -122.7333 | Yes | Clear;32-90F | Service conductor | Broken | 23-0016241 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1805001 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-2107 | 43302107 | SWITCH | 3894 | 20230114 | 1611 | 20230114 | 1619 | 1954769 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 6 | 48 | 38.4685 | -122.7069 | Yes | Clear;32-90F | Conductor- Underground | Normal | 23-0015926 | UG | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1805074 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | OCB | 1106/2 | 20230114 | 1611 | 20230114 | 1811 | 1954740 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3409 | 409080 | 38.4374 | -122.7128 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0016312 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1805068 | 0 | Non-EPSS | N | 2023 | PHASE
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20230114 | 1645 | 20230115 | 1507 | 1954800 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 1490 | 442048 | 38.4698 | -123.0145 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016325 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805082 | 0 | EPSS Ckt | N | 2023 | A GRD
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230114 | 1649 | 20230114 | 2131 | 1954809 | 282 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 18612 | 38.4735 | -123.023 | Yes | Clear;32-90F |  |  | 23-0016448 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1805200 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 250 | 20230114 | 1652 | 20230115 | 1208 | 1954819 | 1156 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 71672 | 38.4816 | -123.0113 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0016328 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | No | No | 1805086 | 0 | EPSS Ckt | N | 2023 | ABC GRD
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230115 | 342 | 20230115 | 1132 | 1955455 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 22110 | 38.4735 | -123.023 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016519 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1805277 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20230115 | 611 | 20230115 | 636 | 1955517 | 25 | Distribution Circuit | Vegetation | Tree - fell into line | 1863 | 46575 | 38.4637 | -123.0083 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016507 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1805287 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | OJ 7 N/ CGC 216-97533204 | 20230115 | 704 | 20230115 | 1415 | 1955730 | 431 | Distribution Circuit | Company Initiated | Return Circuit Normal | 2 | 862 | 38.5813 | -123.3342 | No | Clear;32-90F | Other | Normal | 23-0016536 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1805346 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20230115 | 730 | 20230115 | 1931 | 1955537 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 31724 | 38.5078 | -122.9896 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016533 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1805291 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | SWITCH | 9138SW | 20230115 | 740 | 20230115 | 904 | 1955563 | 84 | Distribution Circuit | Equipment Failure/Involved | Underground | 47 | 3948 | 38.7995 | -123.0254 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0016534 | UG | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1805299 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1101 | 42151101 | FUSE | 8233 | 20230115 | 1318 | 20230115 | 1405 | 1955978 | 47 | Distribution Circuit | Animal | Squirrel | 234 | 10998 | 38.4476 | -122.7085 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016696 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1805420 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | RECLOSER | 378 | 20230115 | 1922 | 20230116 | 1126 | 1956346 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 489 | 41728 | 38.4139 | -122.8269 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016784 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805480 | 0 | EPSS Ckt | N | 2023 | BC GRD
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | RECLOSER | 84088 | 20230115 | 2208 | 20230116 | 1041 | 1956421 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 77466 | 38.8138 | -123.0234 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016845 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805543 | 0 | EPSS Ckt | N | 2023 | GRD & SGF
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 579 | 20230116 | 10 | 20230116 | 1121 | 1956458 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 42944 | 38.6144 | -122.835 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016861 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805559 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 298 | 20230116 | 715 | 20230116 | 1547 | 1957169 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 64690 | 38.4726 | -122.9108 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016990 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | Yes | No | 1805695 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | BELLEVUE-2107 | 43182107 | JUMPER | OJ @ 7919 BEVERLY DR | 20230116 | 846 | 20230116 | 1046 | 1957250 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2400 | 38.3332 | -122.6957 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0017003 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1805707 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | TRANSFORMER | T0361 | 20230116 | 901 | 20230116 | 1139 | 1957419 | 158 | Transformer only | Equipment Failure/Involved | Underground | 16 | 2528 | 38.4755 | -122.6587 | Yes | Clear;32-90F | Connector or Splice (UG) | Deteriorated | 23-0017061 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1805759 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 3197 | 20230116 | 909 | 20230116 | 2107 | 1957445 | 718 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 4256 | 38.2458 | -122.6544 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0017081 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1805775 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE-1101 | 43371101 | FUSE | 6713 | 20230116 | 923 | 20230116 | 930 | 1957466 | 7 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 7 | 38.2223 | -122.5685 | Yes | Clear;32-90F |  |  | 23-0017065 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1805763 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | FUSE | 2961 | 20230116 | 1603 | 20230116 | 1700 | 1958503 | 57 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 228 | 38.5004 | -122.7902 | Yes | Clear;32-90F |  |  | 23-0017325 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1806002 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1111 | 42151111 | TRANSFORMER | 218081327857 | 20230116 | 2040 | 20230117 | 132 | 1958756 | 292 | Transformer only | Equipment Failure/Involved | Overhead | 18 | 5256 | 38.4295 | -122.671 | Yes | Clear;32-90 F | Transformer | Broken | 23-0017397 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1806068 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE-1105 | 43371105 | FUSE | 2624 | 20230116 | 2057 | 20230117 | 1339 | 1958883 | 821 | Distribution Circuit | Equipment Failure/Involved | Underground | 170 | 57973 | 38.239 | -122.608 | Yes | Clear;32-90F | Bushing | Failed/Faulted | 23-0017433 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1806102 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | RECLOSER | 294 | 20230117 | 159 | 20230117 | 424 | 1959025 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 27115 | 38.2349 | -122.4611 | No | Clear;32-90 F |  |  | 23-0017450 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1806118 | 0 | EPSS Ckt | N | 2023 | B PH
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | TRANSFORMER | 218735719701 | 20230117 | 948 | 20230117 | 1052 | 1959267 | 64 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 64 | 38.2066 | -122.441 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0017592 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1806189 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 3197 | 20230117 | 1044 | 20230117 | 1701 | 1959464 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2262 | 38.2458 | -122.6544 | No | Clear;32-90F | Pole-Wood | Broken | 23-0017584 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1806185 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216856031420 | 20230117 | 1207 | 20230117 | 1554 | 1959614 | 227 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 227 | 38.5246 | -123.0999 | No | Clear;32-90F |  |  | 23-0017836 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1806269 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 3471 | 20230117 | 1253 | 20230117 | 1431 | 1959675 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 588 | 38.2459 | -122.4379 | No | Clear;32-90F |  |  | 23-0017762 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1806242 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | TRANSFORMER | 217459538690 | 20230117 | 1315 | 20230117 | 1520 | 1959716 | 125 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 250 | 38.7253 | -122.8913 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0017752 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1806236 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 17797 | 20230118 | 1040 | 20230119 | 1157 | 1960952 | 1517 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1517 | 38.7939 | -123.1631 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0018332 | OH | Sus | 45644694 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1806570 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1111 | 42751111 | FUSE | 3149 | 20230118 | 1136 | 20230118 | 1222 | 1960892 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 121 | 5566 | 38.588 | -122.8489 | No | Clear;32-90F |  |  | 23-0018324 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1806565 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217182331385 | 20230118 | 2041 | 20230118 | 2104 | 1961521 | 23 | Transformer only | Vegetation | Tree - fell into line | 8 | 184 | 38.5238 | -122.9857 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0018623 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1806680 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | OTHER | 933786 | 20230119 | 327 | 20230119 | 1350 | 1961765 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17965 | 38.4881 | -122.9208 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0018655 | OH | Sus | 45644913 | NORTH COAST | JAN | Force Out | 0 | No | Yes | Yes | 1806720 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 2113 | 20230119 | 707 | 20230119 | 838 | 1961827 | 91 | Distribution Circuit | Animal | Bird found | 92 | 8372 | 38.3837 | -122.6868 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018696 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1806737 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 6843 | 20230119 | 719 | 20230119 | 820 | 1961841 | 61 | Distribution Circuit | Animal | Bird found | 20 | 1220 | 38.2871 | -122.4271 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0018690 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1806731 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | RECLOSER | 138 | 20230119 | 1354 | 20230119 | 2216 | 1962235 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 699 | 52117 | 38.2726 | -122.4372 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0018945 | OH | Sus | 45645649 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1806806 | 0 | EPSS Ckt | N | 2023 | AC GRD TIME
SONOMA | SANTA ROSA | SONOMA 1102 | 42721102 | FUSE | 13365 | 20230119 | 1534 | 20230119 | 1841 | 1962564 | 187 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 5984 | 38.3124 | -122.4802 | No | Clear;32-90F | Crossarm- Wood | Deteriorated | 23-0019002 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1806823 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | OTHER | 1108/2 | 20230120 | 700 | 20230120 | 1717 | 1962934 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5567 | 167719 | 38.2395 | -122.6368 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0019210 | OH | Sus | 45645838 | NORTH COAST | JAN | Open Circuit | 0 | No | Yes | Yes | 1806970 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 13983 | 20230120 | 726 | 20230120 | 923 | 1962974 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 106 | 12402 | 38.5338 | -123.131 | No | Clear;32-90F |  |  | 23-0019283 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807006 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 933981 | 20230120 | 820 | 20230120 | 1135 | 1963224 | 195 | Distribution Circuit | Animal | Bird found | 1 | 195 | 38.2226 | -122.6337 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0019372 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807045 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313213665387 | 20230120 | 846 | 20230120 | 1737 | 1962890 | 531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 738 | 38.272 | -122.8652 | No | Clear;32-90F | Pole-Wood | Broken | 23-0019331 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807030 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | TRANSFORMER | 217641028151 | 20230120 | 1950 | 20230121 | 42 | 1963655 | 292 | Transformer only | Equipment Failure/Involved | Electrical Overload | 7 | 2044 | 38.4366 | -122.8252 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019625 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807099 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 14893 | 20230121 | 955 | 20230121 | 1005 | 1963936 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 33 | 38.2714 | -122.6959 | No | Clear;32-90 F |  |  | 23-0019701 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807182 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 298 | 20230121 | 2235 | 20230122 | 1502 | 1964382 | 987 | Distribution Circuit | 3rd Party | Vehicle | 229 | 34318 | 38.4726 | -122.9108 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0019809 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807268 | 0 | EPSS Ckt | N | 2023 | AB
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | TRANSFORMER | 313418562395 | 20230122 | 505 | 20230122 | 1601 | 1964436 | 656 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1312 | 38.1919 | -122.7911 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0019835 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807289 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | SWITCH | 1007 | 20230122 | 1510 | 20230122 | 1541 | 1964907 | 31 | Distribution Circuit | 3rd Party | Vehicle | 49 | 1495 | 38.4859 | -122.9621 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0019809 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807344 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | RECLOSER | 904170 | 20230122 | 2144 | 20230122 | 2247 | 1965072 | 63 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 77 | 4851 | 38.6936 | -122.8331 | No | Clear;32-90 F |  |  | 23-0019959 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807392 | 0 | EPSS Ckt | N | 2023 | AB
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | FUSE | 6113 | 20230123 | 336 | 20230123 | 1311 | 1965271 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 29900 | 38.5382 | -122.6465 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0020034 | OH | Sus | 45647247 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1807447 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 231979 | 20230123 | 349 | 20230123 | 741 | 1965258 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 44370 | 38.4509 | -122.6945 | No | Clear;32-90 F | PT/CCVT | Broken | 23-0019990 | OH | Sus | 45647106 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807423 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1109 | 42151109 | TRANSFORMER | 217985728448 | 20230123 | 556 | 20230123 | 1603 | 1965327 | 607 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1214 | 38.4454 | -122.7044 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0020092 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807532 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1111 | 42751111 | FUSE | 2357 | 20230123 | 737 | 20230123 | 849 | 1965378 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1080 | 38.5913 | -122.8507 | No | Clear;32-90 F |  |  | 23-0020058 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807486 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6247 | 20230123 | 837 | 20230123 | 914 | 1965466 | 37 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 185 | 38.4441 | -122.8923 | No | Clear;32-90 F |  |  | 23-0020074 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807506 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | RECLOSER | 136 | 20230123 | 956 | 20230123 | 1434 | 1965650 | 278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 880 | 85757 | 38.3587 | -122.7693 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0020124 | OH | Sus | 45647380 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1807559 | 0 | EPSS Ckt | N | 2023 | B C GRD
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | JUMPER | LINE AND BUCK SS/OF FUSES 615 | 20230123 | 1233 | 20230123 | 1507 | 1965875 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 308 | 38.363 | -122.9802 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0020243 | OH | Sus | 45647465 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1807598 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | RECLOSER | 94084 | 20230123 | 1455 | 20230123 | 1515 | 1966062 | 0 | Distribution Circuit | Company Initiated | Return Circuit Normal | 252 | 0 | 38.381 | -122.8054 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0020124 | OH | Sus | 45647380 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1807625 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | RECLOSER | 274 | 20230123 | 1618 | 20230124 | 820 | 1966150 | 911 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 422 | 76387 | 38.6627 | -122.8694 | No | Clear;32-90 F |  |  | 23-0020423 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807636 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20230123 | 2113 | 20230123 | 2317 | 1966339 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 816 | 9684 | 38.4728 | -123.0474 | No | Clear;32-90F |  |  | 23-0020488 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807683 | 0 | EPSS Ckt | N | 2023 | AB
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20230124 | 415 | 20230124 | 614 | 1966417 | 119 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 7854 | 38.4728 | -123.0474 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020506 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1807703 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217634326279 | 20230124 | 1654 | 20230125 | 56 | 1967322 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1446 | 38.3852 | -122.8265 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020950 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1807936 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | RECLOSER | 552 | 20230124 | 1947 | 20230124 | 2027 | 1967404 | 40 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 32805 | 38.3652 | -122.6659 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0020962 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1807944 | 0 | Non-EPSS | N | 2023 | NONE
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 7465 | 20230125 | 1048 | 20230125 | 1320 | 1967881 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 608 | 38.166 | -122.8087 | No | Clear;32-90F |  |  | 23-0021287 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1808153 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | OCB | 1101/2 | 20230125 | 1111 | 20230125 | 1651 | 1967908 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1558 | 157472 | 38.4896 | -122.8942 | No | Partly Cloudy-Fog;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0021196 | OH | Sus | 31635566 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808127 | 0 | EPSS Ckt | N | 2023 | B GRD
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | TRANSFORMER | 217791021620 | 20230125 | 1248 | 20230125 | 1820 | 1968020 | 332 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 332 | 38.2578 | -122.7712 | No | Clear;32-90F | Jumper | Broken | 23-0021350 | OH | Sus | 45650104 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1808165 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 6009 | 20230125 | 1753 | 20230125 | 2024 | 1968303 | 151 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 755 | 38.5987 | -122.9113 | No | Clear;32-90F |  |  | 23-0021457 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1808199 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 3831 | 20230126 | 740 | 20230126 | 1114 | 1968693 | 214 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 2568 | 38.3707 | -122.5155 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021717 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1808402 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | WINDSOR 1103 | 43501103 | TRANSFORMER | 217598632897 | 20230126 | 958 | 20230126 | 1038 | 1968756 | 40 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 80 | 38.5668 | -122.8416 | No | Clear;32-90F |  |  | 23-0021713 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1808401 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216889631568 | 20230126 | 1155 | 20230126 | 1300 | 1968893 | 65 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 65 | 38.5311 | -123.0881 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0021826 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1808441 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE-1101 | 43471101 | TRANSFORMER | 218123524347 | 20230127 | 934 | 20230127 | 1215 | 1969671 | 161 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 161 | 38.3332 | -122.6555 | No | Clear;32-90F |  |  | 23-0022337 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1808674 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 14095 | 20230127 | 1414 | 20230127 | 2100 | 1970006 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 812 | 38.3449 | -123.0029 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022536 | OH | Sus | 45653110 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1808720 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1102 | 42561102 | TRANSFORMER | T8974 | 20230127 | 1629 | 20230127 | 2137 | 1970118 | 308 | Transformer only | Equipment Failure/Involved | Underground | 1 | 308 | 38.5517 | -122.7465 | No | Clear;32-90F | Fuse | Burned Open | 23-0022569 | UG | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1808747 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 83355 | 20230128 | 629 | 20230128 | 1345 | 1970263 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2180 | 38.3733 | -122.8326 | No | Clear;32-90F | Crossarm- Wood | Broken | 23-0022622 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1808817 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217510628392 | 20230128 | 1457 | 20230128 | 1540 | 1970596 | 43 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 258 | 38.443 | -122.8702 | No | Clear;32-90F |  |  | 23-0022653 | OH | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1808843 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1102 | 42721102 | FUSE | 16497 | 20230129 | 2306 | 20230130 | 734 | 1971275 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 24384 | 38.3165 | -122.4853 | No | Clear;32-90F | Conductor- Overhead | Broken | 23-0022792 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1808993 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | TRANSFORMER | 218679621973 | 20230130 | 103 | 20230130 | 1500 | 1971287 | 837 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1674 | 38.2691 | -122.4612 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0022797 | OH | Sus | 35423948 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1809000 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 2305 | 20230130 | 414 | 20230130 | 1801 | 1971885 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2876 | 38.5104 | -123.0963 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022968 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1809188 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216848530835 | 20230130 | 703 | 20230130 | 1812 | 1971478 | 669 | Transformer only | Vegetation | Tree - fell into line | 1 | 669 | 38.509 | -123.1013 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0022998 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1809204 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | JUMPER | DIG IN | 20230130 | 756 | 20230131 | 1246 | 1971414 | 1730 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 4 | 6920 | 38.384 | -123.0819 | No | Clear;32-90F | Conductor- Underground | Broken | 23-0022871 | UG | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | No | No | 1809140 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2547 | 20230130 | 948 | 20230130 | 1421 | 1971722 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1911 | 38.2527 | -122.839 | No | Clear;32-90F | Pole-Wood | Broken | 23-0022879 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1809149 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 17141 | 20230130 | 1218 | 20230130 | 1314 | 1971936 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 224 | 38.2526 | -122.3959 | No | Clear;32-90F |  |  | 23-0023021 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1809210 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | JUMPER | OPEN JUMPER @ 18271 | 20230131 | 1204 | 20230131 | 1502 | 1972950 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 178 | 38.2616 | -122.9572 | No | Clear;32-90F | Jumper | Broken | 23-0023484 | OH | Sus | 31636034 | NORTH COAST | JAN | Open Circuit | 0 | No | No | No | 1809493 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217587825293 | 20230201 | 107 | 20230201 | 628 | 1973362 | 321 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 963 | 38.358 | -122.8423 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0023731 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1809582 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 95187 | 20230201 | 1555 | 20230201 | 2147 | 1974221 | 352 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3168 | 38.4124 | -123.0965 | No | Clear;32-90 F | Insulator | Broken | 23-0024093 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1809812 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 15877 | 20230201 | 2133 | 20230202 | 312 | 1974397 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1356 | 38.3982 | -122.5127 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0024196 | OH | Sus | 31636116 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1809858 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA 1106 | 42721106 | RECLOSER | 376 | 20230202 | 844 | 20230202 | 938 | 1974580 | 54 | Distribution Circuit | Animal | Squirrel | 940 | 50760 | 38.2953 | -122.4677 | No | Fog;32-90 F | Cutout- fuse holder | Normal | 23-0024286 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1809947 | 0 | EPSS Ckt | N | 2023 | BC
SONOMA | SANTA ROSA | SONOMA-1106 | 42721106 | FUSE | 98967 | 20230202 | 1015 | 20230202 | 1028 | 1974729 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 27 | 356 | 38.3036 | -122.4747 | No | Clear;32-90 F |  |  | 23-0024338 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810016 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | TRANSFORMER | 218512124014 | 20230202 | 1045 | 20230202 | 1144 | 1974848 | 59 | Transformer only | Vegetation | Tree - palm frond fell into line | 1 | 59 | 38.3246 | -122.5195 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0024407 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810040 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1955 | 20230202 | 1822 | 20230202 | 2030 | 1975355 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 163 | 20864 | 38.3883 | -122.9713 | No | Clear;32-90 F |  |  | 23-0024661 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1810135 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217708925881 | 20230202 | 1910 | 20230203 | 252 | 1975377 | 462 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 2772 | 38.3741 | -122.8005 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0024681 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810151 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | JUMPER | OJ SS CGC 218135830538 | 20230203 | 1043 | 20230203 | 1215 | 1975747 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 92 | 38.5038 | -122.6498 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0024786 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1810255 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | TRANSFORMER | 217092341553 | 20230204 | 1050 | 20230204 | 1256 | 1976571 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 8 | 1008 | 38.8032 | -123.0212 | No | Clear;32-90 F | Fuse | Burned Open | 23-0025207 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810517 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | RECLOSER | 406 | 20230204 | 1826 | 20230205 | 143 | 1976846 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 526 | 34644 | 38.6211 | -122.8757 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025252 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810553 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 2203 | 20230204 | 1951 | 20230205 | 529 | 1976897 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3874 | 38.4055 | -122.8958 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025297 | OH | Sus | 45658837 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810599 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | FUSE | 4061 | 20230204 | 1955 | 20230204 | 2106 | 1976903 | 71 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 289 | 20519 | 38.4415 | -122.729 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0025273 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1810576 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | TRANSFORMER | 218026329217 | 20230204 | 2006 | 20230205 | 1205 | 1976917 | 959 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1918 | 38.4665 | -122.6906 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0025308 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810611 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 6749 | 20230204 | 2013 | 20230205 | 910 | 1976947 | 777 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 50505 | 38.5111 | -122.6907 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0025292 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1810594 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2105 | 43182105 | INTERRUPTER | 959792 | 20230205 | 624 | 20230205 | 923 | 1977305 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 179 | 38.3522 | -122.7063 | No | Clear;32-90 F |  |  | 23-0025355 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1810654 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 1343 | 20230205 | 704 | 20230205 | 1639 | 1977264 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 10440 | 38.2758 | -122.7662 | No | Clear;32-90 F | Other | Broken- wire on ground | 23-0025387 | OH | Sus | 45658909 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1810681 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2105 | 43182105 | FUSE | 3721 | 20230205 | 717 | 20230205 | 921 | 1977276 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 620 | 38.3526 | -122.7058 | No | Clear;32-90 F |  |  | 23-0025354 | OH | Sus | 0 | NORTH COAST | FEB | Multi-Fault | 0 | No | No | No | 1810653 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 3647 | 20230205 | 907 | 20230205 | 1205 | 1977336 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 6052 | 38.4676 | -122.689 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0025366 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1810661 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 8769 | 20230205 | 931 | 20230205 | 1006 | 1977352 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 420 | 38.5157 | -122.6796 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0025377 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1810672 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 6749 | 20230205 | 945 | 20230205 | 1006 | 1977364 | 21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 1071 | 38.5111 | -122.6907 | No | Overcast-Drizzle;32-90 F | Fuse | Arcing | 23-0025372 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1810667 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 2221 | 20230205 | 1509 | 20230205 | 1650 | 1977542 | 101 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 1954 | 38.5065 | -122.8825 | No | Clear;32-90 F |  |  | 23-0025435 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810722 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 551 | 20230206 | 532 | 20230206 | 1249 | 1977827 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3933 | 38.4246 | -122.9568 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025542 | OH | Sus | 31636316 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1810818 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE-1101 | 43471101 | FUSE | 9869 | 20230206 | 912 | 20230206 | 1032 | 1978054 | 80 | Distribution Circuit | Animal | Squirrel | 9 | 694 | 38.3289 | -122.6574 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0025653 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810968 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | TRANSFORMER | 218175825185 | 20230206 | 952 | 20230206 | 1700 | 1978122 | 428 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 856 | 38.3554 | -122.6369 | No | Clear;32-90 F | Other | Burned/flashed | 23-0025686 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1810984 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SONOMA-1106 | 42721106 | TRANSFORMER | 218660022868 | 20230206 | 1305 | 20230206 | 2307 | 1978380 | 602 | Transformer only | Equipment Failure/Involved | Substation | 2 | 1204 | 38.2936 | -122.468 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0025798 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811019 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | RECLOSER | 294 | 20230206 | 1323 | 20230207 | 327 | 1978400 | 844 | Distribution Circuit | 3rd Party | Vehicle | 186 | 13239 | 38.2349 | -122.4611 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025785 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1811014 | 0 | EPSS Ckt | N | 2023 | AC
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | FUSE | 14093 | 20230206 | 1400 | 20230206 | 1507 | 1978513 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 134 | 38.3526 | -122.9525 | No | Clear;32-90 F |  |  | 23-0025844 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811028 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | OTHER | BROKEN BUMP SLEEVE 1 LD SIDE 218142425121 | 20230206 | 1848 | 20230207 | 1331 | 1978646 | 1123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 113358 | 38.3536 | -122.6476 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0025984 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1811079 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1104 | 42271104 | TRANSFORMER | 217971924007 | 20230206 | 2122 | 20230206 | 2332 | 1978750 | 130 | Transformer only | 3rd Party | Vehicle | 7 | 910 | 38.3237 | -122.708 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0025996 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811093 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1104 | 42271104 | TRANSFORMER | 217971924007 | 20230206 | 2343 | 20230207 | 342 | 1978756 | 239 | Transformer only | 3rd Party | Vehicle | 7 | 1673 | 38.3237 | -122.708 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0025998 | OH | Sus | 31636403 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811097 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1106 | 42721106 | TRANSFORMER | 218660022868 | 20230207 | 806 | 20230207 | 923 | 1978866 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 154 | 38.2936 | -122.468 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0026081 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811211 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 7465 | 20230208 | 707 | 20230208 | 1134 | 1979722 | 267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1602 | 38.166 | -122.8087 | No | Clear;32-90F |  |  | 23-0026644 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1811622 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 5743 | 20230208 | 1323 | 20230208 | 1809 | 1980149 | 286 | Distribution Circuit | Vegetation | Tree - bark fell into line | 23 | 6578 | 38.3678 | -122.855 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0026793 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1811654 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA 1101 | 43491101 | FUSE | 2253 | 20230208 | 1527 | 20230208 | 1626 | 1980251 | 59 | Distribution Circuit | Animal | Bird found | 11 | 649 | 38.2493 | -122.6628 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0026806 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1811655 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRANSFORMER | 217436531437 | 20230209 | 204 | 20230209 | 1515 | 1980426 | 791 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 791 | 38.5276 | -122.8994 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0026907 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811713 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | TRANSFORMER | 217202225050 | 20230209 | 857 | 20230209 | 1230 | 1980738 | 213 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 213 | 38.3503 | -122.9764 | No | Clear;32-90F | Transformer (OH) | Deteriorated | 23-0026985 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811809 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | JUMPER | OJ'S 1 S/S OF CGC# 217224127332 | 20230209 | 1323 | 20230209 | 1520 | 1981051 | 117 | Distribution Circuit | Vegetation | Tree - grew into line | 6 | 702 | 38.4129 | -122.9699 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0027154 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1811944 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 913 | 20230209 | 1348 | 20230209 | 1515 | 1981088 | 87 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 174 | 38.5168 | -122.8908 | No | Clear;32-90F | Pole-Wood | Burned/flashed | 23-0027171 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1811951 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | RECLOSER | 122 | 20230210 | 1451 | 20230210 | 1532 | 1981959 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 8282 | 38.7347 | -122.9441 | No | Clear;32-90 F | Recloser | Broken | 23-0027675 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1812276 | 0 | EPSS Ckt | N | 2023 | NA
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | RECLOSER | 84088 | 20230211 | 1200 | 20230211 | 2029 | 1982439 | 509 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 209 | 56905 | 38.8138 | -123.0234 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0027834 | OH | Sus | 31636576 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1812421 | 0 | EPSS Ckt | N | 2023 | A & C
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 495692 | 20230211 | 1452 | 20230211 | 2220 | 1982514 | 448 | Distribution Circuit | 3rd Party | Vehicle | 347 | 155456 | 38.4098 | -122.9354 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0027851 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1812437 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | JUMPER | OJ' SS OF 13853 | 20230212 | 1209 | 20230212 | 1256 | 1982857 | 47 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 376 | 38.4591 | -123.0481 | No | Clear;32-90F | Connector or Splice (OH) | Broken | 23-0027927 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1812518 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 1307 | 20230212 | 1358 | 20230212 | 1509 | 1982975 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 2485 | 38.2373 | -122.4571 | No | Clear;32-90F |  |  | 23-0027939 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1812536 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1104 | 43181104 | FUSE | 13177 | 20230213 | 830 | 20230213 | 1215 | 1983329 | 225 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 450 | 38.4046 | -122.7415 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0028058 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1812660 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313128861101 | 20230213 | 905 | 20230213 | 1101 | 1983396 | 116 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 232 | 38.1542 | -122.891 | No | Clear;32-90F | Fuse | Broken | 23-0028115 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1812767 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1109 | 42151109 | FUSE | 5491 | 20230213 | 1129 | 20230213 | 1352 | 1983625 | 143 | Distribution Circuit | Equipment Failure/Involved | Underground | 202 | 24024 | 38.4431 | -122.695 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0028150 | UG | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1812793 | 1 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 92211 | 20230213 | 1329 | 20230213 | 1506 | 1983639 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 485 | 38.2006 | -122.442 | No | Clear;32-90F |  |  | 23-0028194 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1812815 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE-1105 | 43371105 | TRANSFORMER | 218238121405 | 20230213 | 1427 | 20230213 | 1707 | 1983806 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 1440 | 38.2527 | -122.6145 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0028303 | OH | Sus | 45670951 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1812872 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230213 | 1435 | 20230214 | 1727 | 1983808 | 1612 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 148692 | 38.4451 | -122.9104 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028232 | OH | Sus | 31636716 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1812826 | 0 | EPSS Ckt | N | 2023 | A-B-C
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5751 | 20230213 | 1540 | 20230213 | 1738 | 1983927 | 118 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 1534 | 38.367 | -122.8987 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0028276 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1812850 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6995 | 20230213 | 1612 | 20230213 | 1817 | 1983965 | 125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 4419 | 38.41 | -122.8865 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0028320 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1812884 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217490327266 | 20230213 | 1612 | 20230213 | 2352 | 1984069 | 460 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1380 | 38.4116 | -122.877 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0028330 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1812890 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 2823 | 20230213 | 1645 | 20230213 | 1944 | 1984001 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1432 | 38.8034 | -122.9912 | No | Clear;32-90F |  |  | 23-0028346 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1812906 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | JUMPER | HOT WIRE DOWN 1 SPAN SS SIDE CGC 313088563110 | 20230214 | 305 | 20230214 | 1203 | 1984287 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2360 | 38.2079 | -122.9073 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028419 | OH | Sus | 45671479 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1812961 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRIP-SAVER | 2043 | 20230214 | 1311 | 20230214 | 1444 | 1984958 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 7161 | 38.5039 | -122.9458 | No | Clear;32-90F |  |  | 23-0028807 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1813218 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 2823 | 20230214 | 1356 | 20230214 | 1452 | 1985092 | 56 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 448 | 38.8034 | -122.9912 | No | Clear;32-90F |  |  | 23-0028822 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1813222 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230214 | 1457 | 20230214 | 2130 | 1985172 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 44016 | 38.5018 | -123.0238 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0028888 | OH | Sus | 31636881 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1813248 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 2289 | 20230215 | 653 | 20230215 | 740 | 1985698 | 47 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 34 | 1598 | 38.7162 | -122.892 | No | Clear;32-90 F |  |  | 23-0029015 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1813341 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-2107 | 43302107 | SWITCH | 8220 | 20230215 | 2314 | 20230216 | 159 | 1986545 | 165 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 165 | 38.4725 | -122.7258 | No | Clear;32-90F | Other | Normal | 23-0029504 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1813621 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | TRANSFORMER | 218514424309 | 20230216 | 907 | 20230216 | 1800 | 1986739 | 533 | Transformer only | Animal | Bird found | 1 | 533 | 38.3328 | -122.5189 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0029656 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1813743 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | TRANSFORMER | 218589624644 | 20230216 | 1517 | 20230216 | 1641 | 1987095 | 84 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 168 | 38.3419 | -122.4931 | No | Overcast;32-90 F |  |  | 23-0029883 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1813788 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1104 | 43181104 | FUSE | 3663 | 20230218 | 616 | 20230218 | 734 | 1988049 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 101 | 7878 | 38.4017 | -122.7347 | No | Clear;32-90F |  |  | 23-0030428 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814129 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | RECLOSER | 278842 | 20230218 | 1906 | 20230218 | 2318 | 1988352 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 891 | 122781 | 38.2441 | -122.6183 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0030491 | OH | Sus | 31638740 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1814225 | 0 | Non-EPSS | N | 2023 | NONE
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | TRANSFORMER | 218198030836 | 20230218 | 1907 | 20230219 | 1248 | 1988362 | 1061 | Transformer only | Vegetation | Tree - fell into line | 1 | 1061 | 38.5122 | -122.6309 | No | Clear;32-90 F | Jumper | Broken | 23-0030496 | OH | Sus | 45678382 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814231 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 10033 | 20230218 | 2032 | 20230218 | 2336 | 1988391 | 184 | Distribution Circuit | 3rd Party | Vehicle | 4 | 736 | 38.4179 | -122.9053 | No | Clear;32-90F | Other | Normal | 23-0030514 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814248 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | SWITCH | 8482 | 20230218 | 2343 | 20230218 | 2355 | 1988413 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 463 | 4167 | 38.2417 | -122.611 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030491 | OH | Sus | 31638740 | NORTH COAST | FEB | None | 0 | No | No | No | 1814249 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1112 | 42151112 | FUSE | 6087 | 20230219 | 830 | 20230219 | 922 | 1988530 | 52 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 59 | 3068 | 38.4492 | -122.7033 | Yes | Clear;32-90F |  |  | 23-0030528 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814277 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | WINDSOR-1101 | 43501101 | TRANSFORMER | 217618932493 | 20230219 | 1735 | 20230219 | 2212 | 1988986 | 277 | Transformer only | Equipment Failure/Involved | Electrical Overload | 9 | 2493 | 38.5565 | -122.8341 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0030574 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814325 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | TRANSFORMER | 217367936106 | 20230219 | 2146 | 20230220 | 505 | 1989123 | 439 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 878 | 38.6554 | -122.9216 | Yes | Clear;32-90 F |  |  | 23-0030599 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1814352 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1102 | 43181102 | FUSE | 2777 | 20230220 | 700 | 20230220 | 715 | 1989192 | 15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 30 | 38.401 | -122.7877 | No | Clear;32-90 F |  |  | 23-0030606 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814359 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1109 | 42631109 | FUSE | 933981 | 20230220 | 804 | 20230220 | 1006 | 1989256 | 122 | Distribution Circuit | Animal | Bird found | 1 | 122 | 38.2226 | -122.6337 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030645 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814451 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217443025908 | 20230220 | 1924 | 20230221 | 311 | 1989644 | 467 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 467 | 38.3745 | -122.8941 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0030725 | OH | Sus | 45680412 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814500 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1112 | 42151112 | TRANSFORMER | 217939028389 | 20230221 | 942 | 20230221 | 1648 | 1990035 | 426 | Transformer only | Equipment Failure/Involved | Overhead | 15 | 6390 | 38.4437 | -122.7207 | Yes |  | Transformer | Failed/Faulted | 23-0030921 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814726 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | WINDSOR-1102 | 43501102 | RECLOSER | 596 | 20230221 | 1055 | 20230221 | 1143 | 1990125 | 48 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 610 | 29280 | 38.5473 | -122.8179 | Yes | Partly Cloudy;32-90 F |  |  | 23-0030954 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | No | No | 1814733 | 0 | EPSS Ckt | N | 2023 | ABC
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 18253 | 20230221 | 1201 | 20230222 | 1407 | 1990260 | 1190 | Distribution Circuit | Vegetation | Tree - branch fell on line | 289 | 268684 | 38.473 | -123.0242 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0031034 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814772 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1101 | 42151101 | RECLOSER | 79038 | 20230221 | 1216 | 20230221 | 1453 | 1990301 | 157 | Distribution Circuit | Vegetation | Tree - branch fell on line | 500 | 78500 | 38.4472 | -122.7096 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031009 | OH | Sus | 0 | NORTH COAST | FEB | Multi-Fault | 0 | No | No | No | 1814760 | 0 | Non-EPSS | N | 2023 | BC GRD
SONOMA | SANTA ROSA | WINDSOR-1102 | 43501102 | RECLOSER | 596 | 20230221 | 1216 | 20230221 | 1742 | 1990300 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 610 | 98558 | 38.5473 | -122.8179 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0031028 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | No | No | 1814769 | 0 | EPSS Ckt | N | 2023 | ABC
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRIP-SAVER | 841 | 20230221 | 1219 | 20230221 | 1945 | 1995571 | 446 | Distribution Circuit | Vegetation | Tree - grew into line | 131 | 58426 | 38.5087 | -122.9261 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031796 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815395 | 0 | EPSS Ckt | N | 2023 | #1 OF 2
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20230221 | 1221 | 20230221 | 1337 | 1990321 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 9956 | 38.5089 | -122.9291 | Yes | Clear;32-90F |  |  | 23-0031104 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814813 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 2823 | 20230221 | 1238 | 20230221 | 2006 | 1990364 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3584 | 38.8034 | -122.9912 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0031135 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814838 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 3901 | 20230221 | 1244 | 20230222 | 1623 | 1994332 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 41475 | 38.5324 | -123.0858 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031635 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1815255 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 17803 | 20230221 | 1244 | 20230223 | 1201 | 1997906 | 2837 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 25533 | 38.5216 | -123.0962 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032472 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1815919 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2347 | 20230221 | 1252 | 20230222 | 1353 | 1990485 | 1501 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15010 | 38.6277 | -122.8793 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0031290 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814949 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 3203 | 20230221 | 1300 | 20230221 | 2213 | 1991695 | 553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 14378 | 38.4422 | -122.8843 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0031236 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814907 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 7285 | 20230221 | 1307 | 20230222 | 1339 | 1992783 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19136 | 38.3647 | -122.821 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031403 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815042 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 485 | 20230221 | 1312 | 20230222 | 2318 | 1993559 | 2046 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2046 | 38.4829 | -123.0002 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031541 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815167 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 298 | 20230221 | 1313 | 20230222 | 2317 | 1990581 | 2044 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 356110 | 38.4726 | -122.9108 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031075 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1814800 | 0 | EPSS Ckt | N | 2023 | AC
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 41392 | 20230221 | 1319 | 20230221 | 1736 | 1990648 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 486 | 60112 | 38.4457 | -122.868 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031103 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814812 | 0 | EPSS Ckt | N | 2023 | B GRD
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20230221 | 1325 | 20230223 | 1656 | 1991135 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 433552 | 38.5286 | -123.1572 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031146 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1814845 | 0 | EPSS Ckt | N | 2023 | ABC
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | FUSE | 2963 | 20230221 | 1325 | 20230223 | 1357 | 1997654 | 2912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2912 | 38.5847 | -123.1175 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032370 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815861 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 293941 | 20230221 | 1331 | 20230222 | 2117 | 1990732 | 1906 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 19060 | 38.5105 | -123.0679 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032763 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1816138 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2911 | 20230221 | 1335 | 20230222 | 1204 | 1990786 | 1349 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 25631 | 38.6453 | -122.9187 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031354 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1815008 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230221 | 1345 | 20230221 | 2004 | 1990934 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 42448 | 38.5018 | -123.0238 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031364 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815013 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | OTHER | WIRE BROKE 5 SPANS S/S OF 9779 | 20230221 | 1351 | 20230222 | 1730 | 1991145 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29435 | 38.4174 | -122.896 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0032030 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | No | 1815630 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | TRANSFORMER | 217986528957 | 20230221 | 1355 | 20230222 | 1354 | 1991196 | 1439 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 8634 | 38.4594 | -122.7044 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0031330 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814988 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 7389 | 20230221 | 1356 | 20230221 | 1717 | 1991129 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 4020 | 38.5126 | -122.9338 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031219 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1814901 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | TRANSFORMER | 217805927535 | 20230221 | 1358 | 20230222 | 1558 | 1991234 | 1560 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 6240 | 38.42 | -122.7671 | Yes | Clear;32-90 F | Transformer | Arcing | 23-0031506 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815135 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | RECLOSER | 47964 | 20230221 | 1404 | 20230221 | 2156 | 1991242 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 28792 | 38.3919 | -122.53 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031161 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814856 | 0 | EPSS Ckt | N | 2023 | C + GRD
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | OTHER | 16131 | 20230221 | 1409 | 20230221 | 2153 | 1991288 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6032 | 38.4025 | -122.8685 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031412 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | No | 1815050 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA-1101 | 43491101 | TRIP-SAVER | 825 | 20230221 | 1410 | 20230222 | 1331 | 1991307 | 1401 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 131381 | 38.3081 | -122.6907 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031240 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814911 | 1 | EPSS Ckt | N | 2023 | B
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIRE DOWN LD SIDE 14437 | 20230221 | 1417 | 20230222 | 1201 | 1991386 | 1304 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 30107 | 38.5996 | -122.9692 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031384 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1815026 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 15609 | 20230221 | 1435 | 20230221 | 1620 | 1991714 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 10290 | 38.5128 | -122.9981 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031458 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815093 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 3075 | 20230221 | 1436 | 20230221 | 1712 | 1991725 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2340 | 38.3861 | -122.4872 | Yes | Clear;32-90 F |  |  | 23-0031538 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815163 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | JUMPER | OJ 2/S/SS CGC 217647826130 | 20230221 | 1440 | 20230221 | 1830 | 1993222 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 460 | 38.3813 | -122.8191 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031488 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1815119 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | JUMPER | OJ 2/S/SS MTR 1008701956 | 20230221 | 1440 | 20230221 | 2000 | 1994607 | 320 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 640 | 38.3755 | -122.8132 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031653 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1815271 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | RECLOSER | 468882 | 20230221 | 1441 | 20230221 | 1812 | 1991818 | 106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3522 | 630665 | 38.4061 | -122.8266 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031272 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1814933 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | SANTA ROSA A-1109 | 42151109 | TRANSFORMER | 218029028515 | 20230221 | 1445 | 20230221 | 1508 | 1991180 | 23 | Transformer only | Vegetation | Tree - grew into line | 13 | 299 | 38.4474 | -122.6893 | Yes | Clear;32-90F | Conductor- Overhead | Arcing | 23-0031333 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1814990 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1111 | 42151111 | FUSE | 18533 | 20230221 | 1451 | 20230221 | 2120 | 1992813 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 389 | 38.433 | -122.6988 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031409 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815047 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE-1101 | 43471101 | FUSE | 7187 | 20230221 | 1453 | 20230221 | 1900 | 1991984 | 247 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 138 | 34086 | 38.3364 | -122.629 | Yes | Clear;32-90 F |  |  | 23-0031404 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815043 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | TRANSFORMER | 217924128214 | 20230221 | 1503 | 20230221 | 1955 | 1995800 | 292 | Transformer only | Vegetation | Tree - fell into line | 12 | 3504 | 38.4388 | -122.7259 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031880 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815479 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 5607 | 20230221 | 1514 | 20230221 | 2253 | 1996205 | 459 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 459 | 38.4971 | -123.137 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031953 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815551 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216989029815 | 20230221 | 1514 | 20230223 | 1401 | 1991352 | 2807 | Transformer only | Equipment Failure/Involved | Electrical Overload | 6 | 16842 | 38.4804 | -123.0529 | Yes | Clear;32-90 F | Transformer | Broken | 23-0033194 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816324 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2345 | 20230221 | 1516 | 20230221 | 2205 | 1992357 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 27403 | 38.6373 | -122.8818 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031516 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815144 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1108 | 42151108 | JUMPER | OJ'S @ FRAZIER & RUTLEDGE | 20230221 | 1525 | 20230222 | 1530 | 1992415 | 1445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 24565 | 38.4271 | -122.7085 | Yes | Clear-Strong Winds;32-90 F | Jumper | Burned Open | 23-0031700 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1815307 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20230221 | 1534 | 20230222 | 1626 | 1991321 | 1492 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 24134 | 38.6773 | -123.0625 | Yes | Clear;32-90 F |  |  | 23-0031374 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815021 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 1935 | 20230221 | 1538 | 20230221 | 1737 | 1992579 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2499 | 38.255 | -122.4529 | Yes | Clear;32-90 F |  |  | 23-0031595 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815216 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 17327 | 20230221 | 1552 | 20230221 | 2025 | 1993208 | 273 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1365 | 38.6575 | -122.795 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031843 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815440 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | SWITCH | 7587 | 20230221 | 1553 | 20230221 | 1714 | 1993819 | 81 | Distribution Circuit | Vegetation | Tree - branch fell on line | 152 | 12312 | 38.4444 | -122.7393 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0031576 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1815200 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | FUSE | 17883 | 20230221 | 1555 | 20230221 | 1855 | 1992820 | 180 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 720 | 38.3549 | -122.5374 | Yes | Clear;32-90 F |  |  | 23-0031732 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815335 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20230221 | 1601 | 20230222 | 207 | 1995553 | 606 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 61 | 36966 | 38.422 | -122.954 | Yes | Clear;32-90 F |  |  | 23-0032014 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815613 | 0 | EPSS Ckt | N | 2023 | ABC
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 15417 | 20230221 | 1602 | 20230222 | 1611 | 1995552 | 1449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 23184 | 38.4215 | -122.957 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031791 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1815390 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1111 | 42151111 | JUMPER | OJ'S 1 SS OF CGC 218072027591 | 20230221 | 1620 | 20230223 | 1548 | 1992546 | 2848 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5696 | 38.4217 | -122.6745 | Yes | Clear-Strong Winds;32-90 F | Transformer (OH) | Normal | 23-0031452 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1815088 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | ANNAPOLIS-1101 | 42861101 | FUSE | 4585 | 20230221 | 1629 | 20230222 | 1746 | s1816045 | 1517 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3034 | 38.6605 | -123.2922 | Yes | Clear;32-90 F |  |  | 23-0032649 |  | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1816045 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1102 | 42151102 | FUSE | 802305 | 20230221 | 1631 | 20230222 | 1758 | 1993203 | 1527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 21109 | 38.4268 | -122.7187 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031725 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815331 | 1 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 6589 | 20230221 | 1645 | 20230221 | 2003 | 1993242 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1188 | 38.2953 | -122.7501 | Yes | Clear;32-90 F |  |  | 23-0031812 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815410 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1105 | 42561105 | FUSE | 5891 | 20230221 | 1650 | 20230221 | 2254 | 1993423 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2913 | 38.4828 | -122.8254 | Yes | Clear;32-90 F |  |  | 23-0031946 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815544 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 15093 | 20230221 | 1704 | 20230222 | 1703 | s1815715 | 1439 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7195 | 38.3681 | -122.7835 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032128 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815715 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20230221 | 1732 | 20230222 | 1842 | 1993986 | 1177 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1521 | 678908 | 38.4031 | -122.9214 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031103 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1815294 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20230221 | 1732 | 20230221 | 2040 | 1994006 | 188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 15228 | 38.4984 | -122.9914 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031616 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1815237 | 0 | EPSS Ckt | N | 2023 | N/A
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 2055 | 20230221 | 1732 | 20230222 | 1727 | 1995914 | 1435 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 50225 | 38.4939 | -122.9611 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031859 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1815457 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 1967 | 20230221 | 1744 | 20230222 | 1811 | 1994121 | 1467 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 117360 | 38.4261 | -122.963 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032300 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815826 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 10537 | 20230221 | 1750 | 20230223 | 1100 | 1998249 | 2470 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9880 | 38.3986 | -122.9877 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032602 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816015 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | RECLOSER | 332 | 20230221 | 1754 | 20230221 | 1938 | 1993962 | 104 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 807 | 83928 | 38.509 | -122.9241 | Yes | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0031650 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815268 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | FUSE | 7821 | 20230221 | 1804 | 20230222 | 1715 | 1994700 | 1391 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 4824 | 38.438 | -122.781 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0031768 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815368 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7803 | 20230221 | 1820 | 20230222 | 1602 | 1994864 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 40307 | 38.3441 | -122.8499 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031984 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815581 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 172865 | 20230221 | 1826 | 20230222 | 703 | 1994920 | 757 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 10598 | 38.379 | -122.811 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032060 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815655 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA-1101 | 43491101 | TRANSFORMER | 218088121737 | 20230221 | 1832 | 20230222 | 1755 | 1994959 | 1403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 9821 | 38.2616 | -122.6671 | Yes | Clear;32-90 F | Secondary | Normal | 23-0031928 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815526 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 366758 | 20230221 | 1837 | 20230222 | 538 | 1995145 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 23135 | 38.4586 | -122.9351 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032036 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815638 | 0 | EPSS Ckt | N | 2023 | A & C
SONOMA | SANTA ROSA | MONTE RIO-1112 | 42811112 | FUSE | 15399 | 20230221 | 1857 | 20230223 | 1052 | 1995220 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 89341 | 38.4247 | -122.9608 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031869 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1815467 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 2327 | 20230221 | 2006 | 20230221 | 2105 | 1995759 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 2006 | 38.511 | -122.9287 | Yes | Clear;32-90 F |  |  | 23-0031864 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815462 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-2107 | 43302107 | TRANSFORMER | 217955629153 | 20230221 | 2025 | 20230221 | 2042 | 1993629 | 17 | Transformer only | Equipment Failure/Involved | Overhead | 21 | 357 | 38.4647 | -122.7153 | Yes | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0031903 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815502 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1789 | 20230221 | 2220 | 20230222 | 1203 | 1996173 | 823 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 32920 | 38.4155 | -122.9409 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032307 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1815829 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 17907 | 20230221 | 2240 | 20230222 | 138 | 1996192 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 6764 | 38.5034 | -123.0289 | Yes | Clear;32-90 F |  |  | 23-0032007 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815606 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 17165 | 20230221 | 2250 | 20230222 | 1335 | 1996211 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4425 | 38.4051 | -122.836 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031959 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815557 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1102 | 42151102 | SWITCH | 14975 | 20230222 | 258 | 20230222 | 531 | 1996347 | 153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 14076 | 38.4123 | -122.7396 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0032006 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1815624 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 4123 | 20230222 | 647 | 20230222 | 938 | 1997106 | 168 | Distribution Circuit | Vegetation | Tree - bark fell into line | 22 | 3696 | 38.1893 | -122.9109 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032176 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815754 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2257 | 20230222 | 937 | 20230222 | 1317 | 1997046 | 220 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 660 | 38.2583 | -122.9275 | No | Clear;32-90 F | Fuse | Normal | 23-0032379 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815865 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1104 | 42721104 | TRANSFORMER | 218343523915 | 20230222 | 1244 | 20230223 | 1005 | 1997354 | 1281 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1281 | 38.331 | -122.5765 | No | Clear;32-90 F | Transformer | Broken | 23-0032999 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816236 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1689 | 20230222 | 1526 | 20230222 | 1738 | 1998065 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 792 | 38.4025 | -122.9515 | No | Clear;32-90 F |  |  | 23-0032637 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816040 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 12033 | 20230222 | 1830 | 20230222 | 1910 | 1998505 | 40 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 80 | 38.4064 | -122.9733 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0032699 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1816082 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | FUSE | 1655 | 20230222 | 2227 | 20230222 | 2326 | 1998721 | 59 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 43 | 2537 | 38.3628 | -122.8063 | No | Clear;32-90 F |  |  | 23-0032819 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1816164 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRANSFORMER | 217270329648 | 20230223 | 712 | 20230223 | 754 | 1998906 | 42 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 126 | 38.4769 | -122.9549 | Yes | Clear;32-90 F | Fuse | Normal | 23-0032907 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816195 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | TRANSFORMER | T0658 | 20230223 | 722 | 20230223 | 1409 | 1998750 | 407 | Transformer only | Equipment Failure/Involved | Underground | 9 | 3663 | 38.3792 | -123.0771 | Yes | Clear;32-90 F | Transformer | Broken | 23-0032877 | UG | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816190 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 10825 | 20230223 | 1035 | 20230223 | 1305 | 1999187 | 150 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 2 | 300 | 38.2736 | -122.4478 | Yes | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0033000 | UG | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1816237 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 4523 | 20230223 | 1054 | 20230223 | 1617 | 1999293 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5168 | 38.536 | -123.1403 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0033310 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816388 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217147530621 | 20230223 | 1350 | 20230223 | 1813 | 1999502 | 263 | Transformer only | Vegetation | Tree - fell into line | 7 | 1841 | 38.5029 | -122.9975 | Yes | Clear;32-90 F | Transformer | Bent or Twisted | 23-0033237 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816347 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | SWITCH | 1607 | 20230223 | 1637 | 20230223 | 1914 | 2000029 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 16799 | 38.3057 | -122.6871 | Yes | Clear;32-90 F | Switch (OH) | Failed/Faulted | 23-0033230 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1816400 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | JUMPER | 9092 | 20230223 | 1738 | 20230224 | 1708 | 2000166 | 1410 | Distribution Circuit | 3rd Party | Vehicle | 380 | 535800 | 38.2576 | -122.6311 | Yes | Overcast-Rain;32-90 F | Switch (UG) | Broken | 23-0033282 | UG | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1816425 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 7295 | 20230223 | 1944 | 20230227 | 1731 | 2005186 | 5627 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 191318 | 38.8631 | -123.0866 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034051 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | No | 1817006 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 15747 | 20230223 | 2037 | 20230225 | 853 | 2000528 | 2176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 26112 | 38.8636 | -123.0358 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033489 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816521 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230223 | 2050 | 20230227 | 1654 | 2001444 | 5524 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 494557 | 38.826 | -123.0003 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033580 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816616 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 6085 | 20230223 | 2105 | 20230225 | 1822 | 2000415 | 2717 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 95026 | 38.8365 | -123.0538 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033448 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | No | 1816477 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | RECLOSER | 84088 | 20230223 | 2137 | 20230223 | 2153 | 2000707 | 16 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 1872 | 38.8138 | -123.0234 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033455 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816485 | 0 | EPSS Ckt | N | 2023 | B GRD
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 1231 | 20230223 | 2137 | 20230225 | 1812 | 2000728 | 2675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 61525 | 38.8222 | -123.0239 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033460 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816490 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1112 | 42151112 | FUSE | 8931 | 20230223 | 2246 | 20230224 | 218 | 2000840 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 218 | 46216 | 38.4452 | -122.72 | Yes | Overcast-Fog;32-90 F | Transformer (OH) | Normal | 23-0033504 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816536 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | RECLOSER | 534 | 20230223 | 2330 | 20230226 | 1229 | 2000992 | 2500 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 289715 | 38.3792 | -122.5191 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033500 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816532 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 809 | 20230224 | 2 | 20230225 | 1543 | 2001115 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 42858 | 38.8824 | -123.0474 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033829 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1816840 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 3517 | 20230224 | 33 | 20230224 | 1902 | 2001312 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 16635 | 38.7345 | -122.8363 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033786 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816805 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 10787 | 20230224 | 102 | 20230224 | 1715 | 2001448 | 973 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 27244 | 38.7139 | -123.012 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033601 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816637 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | RECLOSER | 399855 | 20230224 | 122 | 20230226 | 1356 | 2001604 | 3634 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 43608 | 38.8125 | -123.0291 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033644 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816682 | 0 | EPSS Ckt | N | 2023 | A GRD
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | RECLOSER | 672 | 20230224 | 126 | 20230224 | 219 | 2001621 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 43 | 2279 | 38.8238 | -123.0032 | Yes | Clear;32-90 F |  |  | 23-0033556 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816588 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 4007 | 20230224 | 206 | 20230224 | 1152 | 2001821 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 22670 | 38.6808 | -122.9506 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 23-0033633 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816671 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | TRANSFORMER | 217098543006 | 20230224 | 235 | 20230224 | 1230 | 2001909 | 595 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 2380 | 38.8462 | -123.0171 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033695 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816732 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | FUSE | 6121 | 20230224 | 245 | 20230225 | 1757 | 2001937 | 2352 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 30576 | 38.54 | -122.6385 | Yes | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 23-0033764 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1816789 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | RECLOSER | 4646 | 20230224 | 316 | 20230226 | 1846 | 2002147 | 3810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1447 | 193470 | 38.7891 | -123.0171 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0033688 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816725 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 17797 | 20230224 | 316 | 20230227 | 1527 | 2010853 | 5051 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5051 | 38.7939 | -123.1631 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035948 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1818758 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1112 | 42151112 | TRANSFORMER | 217946328446 | 20230224 | 719 | 20230225 | 1502 | 2003732 | 1903 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3806 | 38.4453 | -122.7182 | Yes | Clear;32-90 F | Transformer | Malfunctioning | 23-0033769 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816792 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | RECLOSER | 570 | 20230224 | 727 | 20230226 | 806 | 2003776 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 273 | 44043 | 38.7762 | -122.981 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033759 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1816785 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | TRANSFORMER | 217433940147 | 20230224 | 727 | 20230227 | 1406 | 2009876 | 4719 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9438 | 38.767 | -122.8979 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0035669 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818512 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20230224 | 745 | 20230302 | 1708 | 2003911 | 9203 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 152088 | 38.6773 | -123.0625 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034392 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1817256 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1104 | 42721104 | TRANSFORMER | 218425323581 | 20230224 | 756 | 20230224 | 1352 | 2004015 | 356 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 712 | 38.3127 | -122.5497 | Yes | Clear;32-90 F | Transformer | Broken | 23-0033938 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816926 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | JUMPER | WIRE DOWN 2 S/OF CGC# 217272033175 | 20230224 | 909 | 20230227 | 1252 | 2006240 | 4543 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27258 | 38.5735 | -122.955 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034373 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1817242 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 2957 | 20230224 | 918 | 20230224 | 1102 | 2004597 | 104 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 1456 | 38.5857 | -123.1195 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0033981 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1816956 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 11845 | 20230224 | 1009 | 20230301 | 1530 | 2010153 | 7521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 52647 | 38.801 | -123.0589 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035751 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818586 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 1403 | 20230224 | 1045 | 20230227 | 1405 | 2005106 | 4106 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 189928 | 38.7712 | -122.9593 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034259 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817153 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | TRANSFORMER | 217086342210 | 20230224 | 1146 | 20230225 | 1811 | 2005236 | 1825 | Transformer only | Vegetation | Tree - fell into line | 6 | 10950 | 38.8209 | -123.0238 | Yes | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0034119 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1817060 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 2815 | 20230224 | 1353 | 20230224 | 1417 | 2005723 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 216 | 38.8462 | -123.019 | Yes | Clear;32-90 F | Insulator | Broken | 23-0034211 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1817114 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 7373 | 20230224 | 1405 | 20230301 | 1530 | 2005950 | 7285 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 123845 | 38.7944 | -123.0298 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035765 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | Yes | 1818598 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | RECLOSER | 213984 | 20230224 | 1721 | 20230225 | 1044 | 2006418 | 1043 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 6947 | 38.2983 | -122.8208 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0034467 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1817319 | 0 | EPSS Ckt | N | 2023 | A B
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | JUMPER | WIRE DOWN N/OF 3977 | 20230224 | 1859 | 20230225 | 1321 | 2006793 | 1051 | Distribution Circuit | Equipment Failure/Involved | Overhead | 244 | 18184 | 38.4519 | -122.8067 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034545 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | Yes | 1817398 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1106 | 42151106 | TRANSFORMER | T0383 | 20230224 | 2028 | 20230225 | 1056 | 2007325 | 868 | Transformer only | Equipment Failure/Involved | Underground | 46 | 39928 | 38.4421 | -122.7365 | Yes | Clear;32-90F | Connector or Splice (UG) | Deteriorated | 23-0034933 | UG | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1817798 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 3537 | 20230225 | 934 | 20230227 | 901 | 2008067 | 2847 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 9495 | 38.5307 | -122.8667 | Yes | Clear;32-90F | Fuse | Burned Open | 23-0035178 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818027 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 56475 | 20230225 | 1608 | 20230225 | 1730 | 2008879 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 82 | 38.2026 | -122.7321 | Yes | Clear;32-90F |  |  | 23-0035407 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1818249 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 15705 | 20230225 | 1633 | 20230226 | 1140 | 2002213 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4588 | 38.8674 | -123.0379 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035380 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1818218 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | RECLOSER | 570 | 20230225 | 1747 | 20230225 | 1820 | 2009062 | 33 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 312 | 8817 | 38.7762 | -122.981 | Yes | Clear;32-90 F |  |  | 23-0035422 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818268 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 735 | 20230225 | 1759 | 20230301 | 1545 | 2009078 | 5626 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 56260 | 38.8027 | -122.8323 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035423 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1818269 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | OTHER | WIRE DOWN LOAD SIDE OF 11511 | 20230225 | 1908 | 20230227 | 1531 | 2009243 | 2663 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2663 | 38.8291 | -123.0451 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036274 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1818971 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 662717 | 20230225 | 1913 | 20230226 | 1300 | 2009258 | 1067 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 29876 | 38.3844 | -122.4654 | Yes | Clear;32-90 F |  |  | 23-0035468 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1818315 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | FUSE | 7303 | 20230225 | 2116 | 20230226 | 1430 | 2009357 | 1034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 12408 | 38.8489 | -123.073 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035551 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818398 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRANSFORMER | 217396728578 | 20230226 | 933 | 20230226 | 1750 | 2009796 | 497 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 994 | 38.4477 | -122.9101 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0035659 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818501 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7369 | 20230226 | 2004 | 20230227 | 900 | 2010865 | 776 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 8281 | 38.7777 | -123.041 | Yes | Clear;32-90F |  |  | 23-0033688 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818763 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | RECLOSER | 352 | 20230226 | 2141 | 20230227 | 504 | 2010974 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 463 | 93077 | 38.6126 | -122.8546 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0036032 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1818839 | 0 | EPSS Ckt | N | 2023 | A & B
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2439 | 20230227 | 822 | 20230227 | 1822 | 2011382 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | 38.2162 | -122.9225 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036236 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818956 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | OCB | 1102/2 | 20230227 | 834 | 20230227 | 1058 | 2011408 | 144 | Distribution Circuit | Vegetation | Tree - grew into line | 3891 | 511804 | 38.4257 | -122.8329 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036141 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1818899 | 0 | EPSS Ckt | N | 2023 | B & C INST
SONOMA | SANTA ROSA | SANTA ROSA A-1104 | 42151104 | FUSE | 5409 | 20230227 | 908 | 20230227 | 949 | 2011518 | 41 | Distribution Circuit | Animal | Squirrel | 19 | 779 | 38.4524 | -122.6906 | Yes | Clear;32-90 F | Fuse | Broken | 23-0036196 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1818930 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 9793 | 20230227 | 1138 | 20230227 | 2134 | 2012026 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1788 | 38.4237 | -122.8641 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036354 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819025 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 217067329425 | 20230227 | 1200 | 20230227 | 1444 | 2012144 | 164 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 656 | 38.4699 | -123.0254 | Yes | Clear;32-90 F | Fuse | Normal | 23-0036542 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819131 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217163831476 | 20230227 | 1313 | 20230227 | 1827 | 2012390 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 3140 | 38.5264 | -122.9925 | Yes | Clear;32-90 F | Transformer | Broken | 23-0036640 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819211 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | FUSE | 4015 | 20230227 | 1329 | 20230227 | 1506 | 2012455 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 135 | 13095 | 38.4379 | -122.8013 | Yes | Clear;32-90 F |  |  | 23-0036521 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819117 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | RECLOSER | 464 | 20230227 | 1336 | 20230227 | 1432 | 2012491 | 56 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5317 | 297752 | 38.3002 | -122.7115 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0036469 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819089 | 0 | EPSS Ckt | N | 2023 | UNK
SONOMA | SANTA ROSA | SANTA ROSA A-1103 | 42151103 | FUSE | 2683 | 20230227 | 1338 | 20230227 | 1448 | 2012510 | 70 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 1540 | 38.4311 | -122.7228 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036526 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819120 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 3075 | 20230227 | 1354 | 20230227 | 1502 | 2012599 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 952 | 38.3861 | -122.4872 | Yes | Clear;32-90 F |  |  | 23-0036554 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819139 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 18267 | 20230227 | 1529 | 20230227 | 1637 | 2012608 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1360 | 38.4156 | -122.5116 | Yes | Clear;32-90 F |  |  | 23-0036636 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819208 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | TRANSFORMER | 217720329547 | 20230227 | 1534 | 20230227 | 1659 | 2012882 | 85 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 85 | 38.4748 | -122.7976 | Yes | Partly Cloudy;32-90 F |  |  | 23-0036659 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819228 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230227 | 1609 | 20230227 | 1725 | 2012972 | 76 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 3346 | 38.4735 | -123.023 | Yes | Clear;32-90 F | Secondary | Normal | 23-0036660 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819229 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 985 | 20230227 | 1843 | 20230228 | 915 | 2013208 | 872 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 6979 | 38.837 | -122.9749 | Yes | Clear;32-90 F |  |  | 23-0036742 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819300 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA-1101 | 43491101 | TRANSFORMER | 218077720936 | 20230228 | 721 | 20230228 | 1308 | 2014244 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 13 | 4511 | 38.2396 | -122.6701 | Yes | Overcast-Fog-Drizzle;32-90 F | Transformer | Broken- wire on ground | 23-0037162 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819638 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217215131348 | 20230228 | 825 | 20230301 | 1948 | 2014247 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 42460 | 38.5233 | -122.974 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037163 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1819640 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7803 | 20230228 | 858 | 20230228 | 1730 | 2014514 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 40448 | 38.3441 | -122.8499 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037177 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1819650 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230228 | 1125 | 20230228 | 1210 | 2014943 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 66 | 2970 | 38.4735 | -123.023 | Yes | Clear;32-90F |  |  | 23-0037314 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819736 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1104 | 42561104 | TRANSFORMER | 217761532540 | 20230228 | 1300 | 20230228 | 1947 | 2015640 | 407 | Transformer only | Vegetation | Tree - fell into line | 4 | 1628 | 38.5574 | -122.784 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0037447 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819835 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 217064729514 | 20230228 | 1300 | 20230228 | 1846 | 2015487 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 6258 | 38.4725 | -123.026 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0037448 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819836 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 4023 | 20230228 | 1435 | 20230301 | 1521 | 2015904 | 1486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 6388 | 38.8021 | -122.9917 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0037549 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819902 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRANSFORMER | 217343130850 | 20230228 | 1438 | 20230301 | 1812 | 2016209 | 1654 | Transformer only | Vegetation | Tree - fell into line | 14 | 23156 | 38.5101 | -122.9293 | Yes | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 23-0037643 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819979 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 1929 | 20230228 | 1510 | 20230228 | 1748 | 2016193 | 158 | Distribution Circuit | Animal | Bird found | 19 | 3002 | 38.2648 | -122.4555 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0037635 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819971 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 7723 | 20230301 | 955 | 20230301 | 1046 | 2017977 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 306 | 38.2582 | -122.4155 | No | Clear;32-90F |  |  | 23-0038063 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1820333 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1102 | 42271102 | FUSE | 819 | 20230301 | 1038 | 20230301 | 1137 | 2018080 | 59 | Distribution Circuit | Vegetation | Tree - branch fell on line | 261 | 15399 | 38.3215 | -122.7016 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0038098 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1820357 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | JUMPER | WIRE DOWN 1 SP LD SIDE OF 179993 | 20230301 | 1341 | 20230302 | 1353 | 2018403 | 1452 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 34536 | 38.5389 | -123.1176 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038323 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1820515 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON-1102 | 43321102 | TRANSFORMER | 218092529518 | 20230301 | 1341 | 20230301 | 1905 | 2018395 | 324 | Transformer only | Environmental/External | Water | 3 | 972 | 38.4751 | -122.6675 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0038268 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820480 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1102 | 43181102 | TRANSFORMER | 217860225092 | 20230301 | 1636 | 20230302 | 1117 | 2018776 | 1121 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3363 | 38.3534 | -122.747 | No | Clear;32-90 F | Transformer | Broken | 23-0038425 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820626 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1101 | 42821101 | TRANSFORMER | 217041841180 | 20230301 | 2217 | 20230301 | 2248 | 2019266 | 31 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 62 | 38.7958 | -123.0372 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0038541 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820724 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | TRANSFORMER | 218800921461 | 20230302 | 1007 | 20230302 | 1635 | 2019728 | 388 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 388 | 38.2551 | -122.4188 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0038732 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820821 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | TRANSFORMER | T34579 | 20230302 | 1119 | 20230303 | 1045 | 2019707 | 1406 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2812 | 38.8834 | -122.9938 | No | Clear;32-90 F |  |  | 23-0038803 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820867 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217484523715 | 20230302 | 1345 | 20230302 | 1732 | 2019778 | 227 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 227 | 38.3145 | -122.8783 | No | Clear;32-90 F | Service conductor | Burned Open | 23-0038817 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820874 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | JUMPER | 218618423994 | 20230303 | 807 | 20230303 | 1237 | 2020863 | 270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 7882 | 38.3243 | -122.483 | No | Overcast-Fog;32-90 F | Jumper | Burned Open | 23-0039374 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1821246 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | FUSE | 8065 | 20230303 | 859 | 20230303 | 1221 | 2020947 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 42 | 8484 | 38.3962 | -122.5511 | No | Clear;32-90F |  |  | 23-0039438 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821289 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 13161 | 20230303 | 1602 | 20230303 | 1757 | 2021622 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 1955 | 38.5088 | -122.9305 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039582 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1821367 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217670725906 | 20230304 | 1003 | 20230304 | 1933 | 2022337 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3736 | 38.3755 | -122.8137 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0039957 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821712 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | FUSE | 4015 | 20230304 | 1006 | 20230304 | 1100 | 2022226 | 54 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 135 | 7290 | 38.4379 | -122.8013 | No | Clear;32-90F |  |  | 23-0039932 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1821689 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | RECLOSER | 128824 | 20230304 | 1011 | 20230304 | 1408 | 2022239 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 728 | 17386 | 38.393 | -122.8777 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039925 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1821682 | 0 | EPSS Ckt | N | 2023 | B & GRD
SONOMA | SANTA ROSA | MONROE 2102 | 43302102 | FUSE | 7269 | 20230304 | 1921 | 20230305 | 1110 | 2022835 | 949 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 15184 | 38.4722 | -122.7366 | No | Overcast;32-90 F | Pothead(Riser Termination) | Broken | 23-0040082 | OH | Sus | 31639604 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821826 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 1581 | 20230304 | 2338 | 20230305 | 1857 | 2022993 | 1159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 8152 | 38.4926 | -123.0608 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0040185 | OH | Sus | 45688770 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821933 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | FUSE | 3489 | 20230305 | 9 | 20230305 | 218 | 2023008 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2709 | 38.4428 | -122.8454 | No | Clear;32-90F |  |  | 23-0040194 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1821942 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | FUSE | 4015 | 20230305 | 15 | 20230305 | 108 | 2023009 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 4808 | 38.4379 | -122.8013 | No | Overcast-Heavy Rain;32-90 F | Jumper | Burned/flashed | 23-0040180 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821928 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | FUSE | 4350 | 20230305 | 55 | 20230305 | 345 | 2023069 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 9520 | 38.2392 | -122.6222 | No | Overcast-Rain;32-90 F |  |  | 23-0040207 | UG | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1821955 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 2113 | 20230305 | 629 | 20230305 | 801 | 2023295 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 7084 | 38.3837 | -122.6868 | No | Clear;32-90F |  |  | 23-0040238 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821986 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 5907 | 20230305 | 630 | 20230305 | 819 | 2023403 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1635 | 38.3992 | -122.695 | No | Clear;32-90F |  |  | 23-0040238 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1821987 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 12397 | 20230305 | 1241 | 20230305 | 1327 | 2023730 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 46 | 38.403 | -122.9327 | No | Clear;32-90F |  |  | 23-0040359 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1822084 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1103 | 42571103 | RECLOSER | 4894 | 20230305 | 1810 | 20230306 | 108 | 2024022 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 411 | 73346 | 38.4509 | -122.8463 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040456 | OH | Sus | 45688777 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822190 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20230306 | 448 | 20230306 | 1458 | 2024220 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 66267 | 38.3871 | -122.89 | No | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0040543 | OH | Sus | 45688981 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822279 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | SONOMA-1104 | 42721104 | FUSE | 10547 | 20230306 | 639 | 20230306 | 744 | 2024239 | 65 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 69 | 4485 | 38.296 | -122.4904 | No | Clear;32-90F |  |  | 23-0040569 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1822285 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 3377 | 20230306 | 700 | 20230306 | 852 | 2024257 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 104 | 11648 | 38.3451 | -122.6667 | No | Clear;32-90F |  |  | 23-0040577 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1822288 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2105 | 43182105 | FUSE | 3721 | 20230306 | 804 | 20230306 | 951 | 2024310 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 535 | 38.3526 | -122.7058 | No | Clear;32-90 F |  |  | 23-0040618 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1822321 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | TRANSFORMER | 218654226450 | 20230306 | 827 | 20230306 | 2029 | 2024343 | 722 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1444 | 38.3921 | -122.4706 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0040628 | OH | Sus | 45689039 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822332 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | LAKEVILLE-1101 | 43371101 | FUSE | 2525 | 20230306 | 1629 | 20230307 | 657 | 2024968 | 868 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 68572 | 38.2116 | -122.5489 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0040979 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1822521 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | TRANSFORMER | 217242537587 | 20230307 | 830 | 20230307 | 1227 | 2025317 | 237 | Transformer only | Unknown Cause | Patrol - not conducted | 3 | 711 | 38.6961 | -122.9657 | No | Clear;32-90 F |  |  | 23-0041067 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1822568 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20230308 | 515 | 20230308 | 1337 | 2026212 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4518 | 38.4671 | -122.909 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0041486 | OH | Sus | 45689990 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1822809 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PENNGROVE-1101 | 43471101 | RECLOSER | 3476 | 20230308 | 625 | 20230308 | 722 | 2026241 | 57 | Distribution Circuit | Animal | Bird found | 332 | 18924 | 38.3207 | -122.6669 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0041476 | OH | Sus | 0 | NORTH COAST | MAR | Multi-Fault | 0 | No | No | No | 1822803 | 0 | EPSS Ckt | N | 2023 | ABC
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20230308 | 706 | 20230308 | 1808 | 2026266 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 45592 | 38.5087 | -123.0696 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041489 | OH | Sus | 45690155 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1822811 | 0 | EPSS Ckt | N | 2023 | A GRD
SONOMA | SANTA ROSA | WINDSOR-1103 | 43501103 | FUSE | 11795 | 20230308 | 803 | 20230308 | 904 | 2026316 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1525 | 38.5625 | -122.8143 | No | Clear;32-90F |  |  | 23-0041549 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1822843 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1102 | 43071102 | FUSE | 14753 | 20230308 | 1915 | 20230309 | 1215 | 2026942 | 1020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1361 | 38.3795 | -122.5254 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0041847 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1822987 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | JUMPER | OJ'S 1 S/OF 531 | 20230309 | 1030 | 20230309 | 1300 | 2027409 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 300 | 38.6622 | -122.8711 | Yes | Clear;32-90F | Insulator | Broken | 23-0042063 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1823097 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230309 | 1254 | 20230309 | 1332 | 2027537 | 38 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 104 | 3952 | 38.826 | -123.0003 | Yes | Clear;32-90F |  |  | 23-0042153 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823124 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 217699321751 | 20230309 | 1306 | 20230309 | 1814 | 2027546 | 308 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 308 | 38.2608 | -122.8024 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0042235 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823151 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1102 | 42631102 | TRANSFORMER | 218221620745 | 20230309 | 1445 | 20230309 | 1508 | 2027579 | 23 | Transformer only | Equipment Failure/Involved | Underground | 3 | 69 | 38.2345 | -122.62 | Yes | Clear;32-90F | Connector or Splice (UG) |  | 23-0042261 | UG | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823156 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | JUMPER | OJ 1 LD SIDE OF 2427 ON MAINLINE | 20230309 | 1741 | 20230309 | 1842 | 2028331 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1024 | 61827 | 38.2718 | -122.8606 | Yes | Overcast-Rain-Strong Winds;32-90 F | Jumper | Broken | 23-0042392 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1823230 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 443 | 20230309 | 1807 | 20230309 | 1916 | 2028468 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 5106 | 38.3741 | -122.7919 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042454 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823282 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 7779 | 20230309 | 1858 | 20230309 | 2218 | 2028770 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3400 | 38.3435 | -122.8405 | Yes | Clear;32-90F | Jumper | Broken | 23-0042479 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1823303 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 2883 | 20230309 | 1920 | 20230310 | 1143 | 2028967 | 983 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 37354 | 38.2749 | -122.7159 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042484 | OH | Sus | 0 | NORTH COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823307 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 5783 | 20230309 | 1924 | 20230309 | 2037 | 2028959 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 438 | 38.396 | -122.8637 | Yes | Clear;32-90F |  |  | 23-0042525 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823343 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | JUMPER | OJ'S SS OF CGC 217166027761 | 20230309 | 2000 | 20230310 | 912 | 2029346 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 792 | 38.424 | -122.9906 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042566 | OH | Sus | 0 | NORTH COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1823384 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | RECLOSER | 532 | 20230309 | 2253 | 20230310 | 1629 | 2029650 | 1056 | Distribution Circuit | Environmental/External | Flood/Erosion | 37 | 38608 | 38.4949 | -123.0108 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042654 | OH | Sus | 0 | NORTH COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1823462 | 0 | EPSS Ckt | N | 2023 | A- B- C
SONOMA | SANTA ROSA | LAKEVILLE-1105 | 43371105 | FUSE | 8325 | 20230310 | 120 | 20230310 | 1546 | 2029862 | 866 | Distribution Circuit | Equipment Failure/Involved | Underground | 446 | 191136 | 38.2566 | -122.6193 | No | Overcast-Fog;32-90 F | Transformer (UG) | Failed/Faulted | 23-0042702 | UG | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823515 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 2987 | 20230310 | 237 | 20230310 | 720 | 2029958 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7075 | 38.5423 | -123.0896 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042772 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1823575 | 0 | EPSS Ckt | N | 2023 | 1 & 2
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20230310 | 241 | 20230310 | 1453 | 2030288 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 39528 | 38.5579 | -123.0951 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042772 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823576 | 0 | EPSS Ckt | N | 2023 | 2
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | RECLOSER | 416 | 20230310 | 246 | 20230310 | 353 | 2029963 | 67 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 1742 | 38.4361 | -122.5779 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042704 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823517 | 0 | EPSS Ckt | N | 2023 | B & GRD
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | RECLOSER | 107941 | 20230310 | 246 | 20230310 | 434 | -2029963 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 756 | 38.4429 | -122.5759 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042704 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1823535 | 0 | EPSS Ckt | N | 2023 | A & B
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | JUMPER | OJ'S S/S OF CGC# 218359528520 | 20230310 | 246 | 20230310 | 1559 | 2030063 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7214 | 38.4477 | -122.5738 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042735 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | Yes | No | 1823549 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | RECLOSER | 126 | 20230310 | 847 | 20230310 | 1927 | 2030493 | 640 | Distribution Circuit | Environmental/External | Water | 502 | 43764 | 38.2596 | -122.483 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042848 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1823613 | 0 | EPSS Ckt | N | 2023 | SGF
SONOMA | SANTA ROSA | FULTON-1104 | 42561104 | TRANSFORMER | T5673 | 20230310 | 1000 | 20230310 | 1840 | 2030742 | 520 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 520 | 38.5437 | -122.7978 | No | Clear;32-90F | Transformer (UG) | Failed/Faulted | 23-0042966 | UG | Sus | 0 | NORTH COAST | MAR | Multi-Fault | 0 | No | No | No | 1823680 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 3463 | 20230310 | 1128 | 20230310 | 1327 | 2030813 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 1309 | 38.2512 | -122.4755 | No | Clear;32-90F |  |  | 23-0043095 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823733 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 8055 | 20230310 | 1221 | 20230310 | 1743 | 2030940 | 322 | Distribution Circuit | Vegetation | Tree - grew into line | 15 | 4830 | 38.5086 | -122.9199 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0043057 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1823714 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE-1105 | 43301105 | TRANSFORMER | 217708828614 | 20230310 | 1221 | 20230310 | 1326 | 2030939 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 325 | 38.4498 | -122.8012 | No | Overcast;32-90 F | Connector or Splice (OH) | Broken | 23-0043107 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823739 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | RECLOSER | 338 | 20230310 | 1620 | 20230311 | 200 | 2031386 | 580 | Distribution Circuit | 3rd Party | Vehicle | 366 | 47364 | 38.3959 | -122.8512 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0043201 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1823794 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | TRANSFORMER | 218768121129 | 20230311 | 549 | 20230311 | 705 | 2031891 | 76 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 76 | 38.246 | -122.4301 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Burned Open | 23-0043348 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823928 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1107 | 42151107 | SWITCH | 8746 | 20230311 | 956 | 20230311 | 1031 | 2032253 | 35 | Distribution Circuit | Equipment Failure/Involved | Underground | 18 | 461 | 38.4428 | -122.6936 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0028150 | UG | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823977 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217397627519 | 20230311 | 1119 | 20230311 | 1741 | 2032304 | 382 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 382 | 38.4189 | -122.9114 | No | Clear;32-90 F | Transformer | Broken | 23-0043461 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1824019 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1112 | 42751112 | TRANSFORMER | 217618234649 | 20230311 | 1731 | 20230311 | 1928 | 2032751 | 117 | Transformer only | Vegetation | Tree - branch fell on line | 4 | 468 | 38.615 | -122.8351 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0043567 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1824107 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | SWITCH | 4479 | 20230311 | 1923 | 20230312 | 6 | 2032878 | 283 | Distribution Circuit | Environmental/External | Water | 97 | 4400 | 38.3679 | -122.8459 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0043562 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1824110 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 7683 | 20230312 | 1020 | 20230312 | 1145 | 2033193 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 255 | 38.497 | -122.8558 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0043706 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1824223 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | WINDSOR-1103 | 43501103 | FUSE | 6267 | 20230312 | 1058 | 20230312 | 1230 | 2033208 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 460 | 38.5412 | -122.846 | No | Clear;32-90 F |  |  | 23-0043726 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1824242 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | JUMPER | WIRE DOWN @ CGC 217489025790 | 20230312 | 1100 | 20230312 | 2006 | 2033267 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3474 | 38.3721 | -122.876 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043723 | OH | Sus | 45698202 | NORTH COAST | MAR | Force Out | 0 | No | Yes | No | 1824239 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | TRANSFORMER | 216980229870 | 20230312 | 1353 | 20230312 | 2353 | 2033345 | 600 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 1200 | 38.4822 | -123.0564 | No | Clear;32-90 F |  |  | 23-0043758 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1824273 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230313 | 722 | 20230313 | 1850 | 2034041 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 70584 | 38.4451 | -122.9104 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043956 | OH | Sus | 31639884 | NORTH COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1824457 | 0 | EPSS Ckt | N | 2023 | A-B-GRD
SONOMA | SANTA ROSA | BELLEVUE-1104 | 43181104 | TRANSFORMER | 217897726745 | 20230313 | 955 | 20230313 | 1115 | 2034201 | 80 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 400 | 38.3986 | -122.7347 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 23-0044013 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1824491 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | RECLOSER | 612266 | 20230314 | 324 | 20230314 | 1834 | 2035161 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35490 | 38.5329 | -123.2715 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044467 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824733 | 0 | EPSS Ckt | N | 2023 | A
SONOMA | SANTA ROSA | SANTA ROSA A-1112 | 42151112 | FUSE | 5221 | 20230314 | 328 | 20230314 | 1739 | 2035163 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 219558 | 38.4505 | -122.7138 | Yes |  | Pole-Wood | Broken- wire on ground | 23-0044469 | OH | Sus | 45698721 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1824735 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 6399 | 20230314 | 618 | 20230314 | 1841 | 2035193 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 23033 | 38.5038 | -122.9115 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044508 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824749 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FORT ROSS-1121 | 42851121 | RECLOSER | 37326 | 20230314 | 746 | 20230314 | 1832 | 2035248 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 96861 | 38.5346 | -123.2752 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0044560 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1824764 | 0 | EPSS Ckt | N | 2023 | B GRD
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | RECLOSER | 933786 | 20230314 | 945 | 20230314 | 1145 | 2035725 | 120 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 3240 | 38.4881 | -122.9208 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044670 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1824823 | 0 | EPSS Ckt | N | 2023 | A-B
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230314 | 949 | 20230314 | 1209 | 2035613 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 18480 | 38.4451 | -122.9104 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0044638 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1824805 | 0 | EPSS Ckt | N | 2023 | A- GRD
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 7547 | 20230314 | 956 | 20230314 | 1735 | 2035633 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1377 | 38.4148 | -122.9717 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0044907 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1825004 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 13171 | 20230314 | 957 | 20230315 | 1323 | 2042169 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6584 | 38.4629 | -122.9488 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045325 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1825324 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | JUMPER | OJ 2 SPANS SS MTR # 1008891754 | 20230314 | 1002 | 20230314 | 1526 | 2037349 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 648 | 38.4909 | -122.9302 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044844 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824954 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 6125 | 20230314 | 1011 | 20230314 | 1350 | 2035750 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 876 | 38.3762 | -122.8338 | Yes | Clear;32-90 F |  |  | 23-0045180 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825227 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 13907 | 20230314 | 1018 | 20230314 | 1109 | 2035812 | 51 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 1683 | 38.4946 | -123.0156 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0044751 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1824884 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230314 | 1022 | 20230314 | 2102 | 2036689 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 28160 | 38.4756 | -122.9526 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0045056 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1825126 | 0 | EPSS Ckt | N | 2023 | NONE
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 433 | 20230314 | 1030 | 20230314 | 1235 | 2035924 | 125 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 4250 | 38.509 | -122.9283 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0044972 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825055 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | TRANSFORMER | 217314130291 | 20230314 | 1032 | 20230314 | 1354 | 2035968 | 202 | Transformer only | Unknown Cause | Patrol - found nothing | 6 | 1212 | 38.4949 | -122.9396 | Yes | Overcast-Fog-Heavy Rain;32-90 F |  |  | 23-0045249 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1825273 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 18723 | 20230314 | 1037 | 20230314 | 1544 | 2035959 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10745 | 38.4826 | -122.8794 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044866 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1824973 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 4663 | 20230314 | 1043 | 20230314 | 1801 | 2035851 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3504 | 38.4984 | -122.9935 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0044911 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825008 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 707 | 20230314 | 1059 | 20230314 | 1148 | 2036248 | 49 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 78 | 3822 | 38.2665 | -122.7144 | Yes | Clear;32-90F |  |  | 23-0044857 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1824966 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 15429 | 20230314 | 1113 | 20230314 | 1858 | 2036573 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1395 | 38.4792 | -122.909 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0045051 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825121 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20230314 | 1113 | 20230314 | 1432 | 2036736 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1791 | 38.509 | -122.8869 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045230 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825260 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 7415 | 20230314 | 1114 | 20230314 | 1649 | 2036593 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 23015 | 38.826 | -123.0003 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0044957 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825042 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | OCB | 1105/2 | 20230314 | 1129 | 20230314 | 1255 | 2037114 | 86 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3102 | 266772 | 38.3098 | -122.7318 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 23-0044825 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1824939 | 0 | EPSS Ckt | N | 2023 | B/C 51 TIME
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | JUMPER | OJ 1 W OF 14127 | 20230314 | 1129 | 20230314 | 1521 | 2037053 | 232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 169 | 30298 | 38.3528 | -122.9517 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Jumper | Burned/flashed | 23-0045035 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1825107 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 858093 | 20230314 | 1130 | 20230314 | 1448 | 2036958 | 198 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 20 | 3960 | 38.6478 | -122.8503 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0045347 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825338 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 4899 | 20230314 | 1132 | 20230314 | 1904 | 2037209 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5876 | 38.4083 | -122.9372 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045379 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1825367 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20230314 | 1142 | 20230314 | 2149 | 2037645 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 31266 | 38.3721 | -122.9117 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044932 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825022 | 0 | EPSS Ckt | N | 2023 | A-GRD
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | FUSE | 1747 | 20230314 | 1146 | 20230314 | 1418 | 2037629 | 152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 7600 | 38.4119 | -122.856 | Yes | Clear;32-90F |  |  | 23-0045290 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825301 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20230314 | 1156 | 20230314 | 1327 | 2037798 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 131 | 11921 | 38.5089 | -122.9291 | Yes | Clear;32-90F |  |  | 23-0044978 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825060 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217370426529 | 20230314 | 1156 | 20230314 | 1659 | 2037795 | 303 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 606 | 38.3911 | -122.9197 | Yes | Clear;32-90 F |  |  | 23-0045443 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1825420 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2101 | 43182101 | FUSE | 8881 | 20230314 | 1200 | 20230314 | 2353 | 2037898 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17112 | 38.3664 | -122.6257 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045026 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1825098 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | JUMPER | WIRE DOWN AT 1 SS CGC 217513526029 | 20230314 | 1216 | 20230314 | 2210 | 2042286 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3742 | 38.3779 | -122.869 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045348 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1825339 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 4615 | 20230314 | 1230 | 20230314 | 1410 | 2038885 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 2900 | 38.4805 | -123 | Yes | Clear;32-90F |  |  | 23-0045267 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825285 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 1301 | 20230314 | 1231 | 20230314 | 1335 | 2038908 | 64 | Distribution Circuit | Vegetation | Tree - bark fell into line | 38 | 2432 | 38.2361 | -122.4621 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045166 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825215 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 15181 | 20230314 | 1255 | 20230315 | 1840 | 2042632 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 17850 | 38.5108 | -123.0736 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0045683 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825624 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1105 | 42631105 | FUSE | 6029 | 20230314 | 1257 | 20230314 | 1404 | 2039648 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 164 | 10988 | 38.2544 | -122.626 | Yes | Clear;32-90F |  |  | 23-0045253 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825275 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | SONOMA 1103 | 42721103 | RECLOSER | 849082 | 20230314 | 1303 | 20230314 | 1714 | 2040005 | 251 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 14558 | 38.3024 | -122.4401 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 23-0045120 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825178 | 0 | EPSS Ckt | N | 2023 | B-C
SONOMA | SANTA ROSA | SONOMA-1107 | 42721107 | FUSE | 10569 | 20230314 | 1305 | 20230314 | 1431 | 2039955 | 86 | Distribution Circuit | Vegetation | Tree - bark fell into line | 175 | 15050 | 38.2602 | -122.4845 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0045300 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825308 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 3175 | 20230314 | 1310 | 20230314 | 1749 | 2038201 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 558 | 38.2202 | -122.8185 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045218 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825251 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | TRANSFORMER | 218772622079 | 20230314 | 1334 | 20230314 | 1834 | 2040689 | 300 | Transformer only | Vegetation | Tree - grew into line | 4 | 1200 | 38.2721 | -122.4286 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045747 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825681 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SONOMA-1105 | 42721105 | FUSE | 1351 | 20230314 | 1339 | 20230314 | 1524 | 2040817 | 105 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 3675 | 38.279 | -122.4371 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0045429 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825407 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1106 | 42631106 | SWITCH | 4350SW | 20230314 | 1341 | 20230314 | 1536 | 2040868 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 6440 | 38.2393 | -122.6222 | Yes | Clear;32-90 F |  |  | 23-0045372 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825358 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217665325521 | 20230314 | 1457 | 20230314 | 1815 | 2038884 | 198 | Transformer only | Vegetation | Tree - fell into line | 5 | 990 | 38.3646 | -122.8156 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0045722 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825658 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1102 | 42091102 | FUSE | 913 | 20230314 | 1520 | 20230314 | 2201 | 2042765 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2601 | 38.5168 | -122.8908 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045447 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1825423 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | TRANSFORMER | 217784725050 | 20230314 | 1534 | 20230314 | 1909 | 2042836 | 215 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 1505 | 38.3518 | -122.7738 | Yes | Clear;32-90 F | Secondary | Together | 23-0045682 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825623 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 10527 | 20230314 | 1902 | 20230315 | 1039 | 2044391 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 31858 | 38.444 | -123.0622 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken | 23-0045856 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1825778 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SANTA ROSA A-1103 | 42151103 | TRANSFORMER | 217811127620 | 20230314 | 2040 | 20230315 | 1003 | 2044721 | 803 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 8030 | 38.4224 | -122.7657 | Yes | Clear;32-90 F | Transformer | Broken | 23-0045922 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825845 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | FUSE | 13499 | 20230314 | 2048 | 20230315 | 1445 | 2046175 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8616 | 38.3964 | -122.4716 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046333 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | Yes | No | 1826157 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | JUMPER | OJ 1 SS OF CGC 313113964395 | 20230314 | 2132 | 20230315 | 1054 | 2044489 | 802 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 802 | 38.2443 | -122.8975 | Yes | Partly Cloudy;32-90 F | Jumper | Broken | 23-0045914 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1825838 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1101 | 43071101 | RECLOSER | 818762 | 20230314 | 2138 | 20230315 | 1259 | 2044719 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 93021 | 38.3876 | -122.4954 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045906 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | Yes | No | 1825831 | 0 | EPSS Ckt | N | 2023 | none
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | JUMPER | OJ 2 P LD SIDE OF 79306 | 20230314 | 2230 | 20230315 | 3 | 2043839 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 7347 | 38.37 | -122.9109 | Yes | Clear;32-90 F | Jumper | Burned Open | 23-0045981 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | No | No | 1825907 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 1787 | 20230315 | 113 | 20230315 | 1317 | 2045044 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 17155 | 38.4195 | -122.931 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046047 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1825965 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FULTON-1102 | 42561102 | FUSE | 12989 | 20230315 | 828 | 20230315 | 845 | 2045564 | 17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 17 | 38.5401 | -122.779 | No | Clear;32-90 F |  |  | 23-0046134 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1826029 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1111 | 42811111 | FUSE | 42419 | 20230315 | 910 | 20230315 | 1741 | 2045634 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1022 | 38.5214 | -123.0614 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046349 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1826165 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | SALMON CREEK-1101 | 43161101 | SWITCH | 3229 | 20230315 | 948 | 20230315 | 1002 | 2045756 | 14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 1092 | 38.3564 | -122.9258 | No | Clear;32-90 F | Jumper | Burned Open | 23-0045981 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1826061 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA C-1108 | 42631108 | FUSE | 12279 | 20230315 | 1646 | 20230315 | 1757 | 2046878 | 71 | Distribution Circuit | 3rd Party | Metallic Balloon | 72 | 5112 | 38.2448 | -122.65 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0046577 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826299 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1102 | 43181102 | TRANSFORMER | 217854325882 | 20230315 | 1838 | 20230315 | 1940 | 2047077 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 186 | 38.3749 | -122.7496 | No | Clear;32-90 F | Transformer (OH) |  | 23-0046678 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826363 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | FUSE | 593 | 20230316 | 709 | 20230316 | 840 | 2047703 | 91 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 71 | 6461 | 38.8329 | -123.0106 | No | Clear;32-90 F |  |  | 23-0046889 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1826483 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 6581 | 20230316 | 715 | 20230316 | 958 | 2047716 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 815 | 38.3405 | -122.7525 | No | Clear;32-90 F |  |  | 23-0046894 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1826486 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1111 | 42751111 | TRANSFORMER | 217582331740 | 20230316 | 1316 | 20230316 | 1459 | 2048522 | 103 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 206 | 38.5359 | -122.847 | No | Clear;32-90 F |  |  | 23-0047106 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1826614 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1104 | 42571104 | TRANSFORMER | 217701327103 | 20230316 | 1342 | 20230316 | 1938 | 2048567 | 356 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 356 | 38.408 | -122.8035 | No | Clear;32-90 F |  |  | 23-0047095 | OH | Sus | 31639902 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826607 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20230316 | 1815 | 20230317 | 416 | 2049094 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5409 | 38.6025 | -123.0037 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047249 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1826709 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | FITCH MOUNTAIN-1111 | 42751111 | FUSE | 1033 | 20230316 | 2104 | 20230316 | 2113 | 2049295 | 9 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 27 | 38.5322 | -122.8498 | No | Clear;32-90 F |  |  | 23-0047267 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826729 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | DUNBAR-1103 | 43071103 | TRANSFORMER | 218401027845 | 20230317 | 747 | 20230317 | 1621 | 2049533 | 514 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1028 | 38.4301 | -122.5595 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0047397 | OH | Sus | 45701569 | NORTH COAST | MAR | Open Circuit | 0 | No | Yes | No | 1826805 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | PETALUMA A-0411 | 42120411 | TRANSFORMER | 218151520699 | 20230317 | 1128 | 20230317 | 1313 | 2049942 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 22 | 2310 | 38.2332 | -122.6446 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0047553 | OH | Sus | 45701914 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826885 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | FUSE | 1995 | 20230317 | 1732 | 20230318 | 1638 | 2050611 | 1386 | Distribution Circuit | Vegetation | Tree - grew into line | 9 | 12474 | 38.5326 | -123.0037 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0047733 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1826977 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | RINCON-1103 | 43321103 | TRANSFORMER | 218198030836 | 20230317 | 1935 | 20230319 | 1355 | 2050656 | 2540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 5276 | 38.5122 | -122.6309 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0047756 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1826997 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-2107 | 43182107 | FUSE | 5807 | 20230317 | 2154 | 20230318 | 1052 | 2050814 | 778 | Distribution Circuit | Equipment Failure/Involved | Underground | 197 | 31722 | 38.3424 | -122.7122 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0047850 | UG | Sus | 45702235 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827082 | 0 | Non-EPSS | N | 2023
SONOMA | SANTA ROSA | CORONA-1103 | 43491103 | FUSE | 1600 | 20230318 | 821 | 20230318 | 834 | 2050898 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 214 | 2141 | 38.2651 | -122.6339 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0048256 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827481 | 1 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | TRANSFORMER | 313370565355 | 20230318 | 839 | 20230318 | 1119 | 2050978 | 160 | Transformer only | Animal | Bird found | 1 | 160 | 38.2722 | -122.8107 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0048291 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827513 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | CORONA-1103 | 43491103 | FUSE | 1600 | 20230318 | 2047 | 20230319 | 218 | 2051556 | 229 | Distribution Circuit | Equipment Failure/Involved | Underground | 431 | 69846 | 38.2651 | -122.6339 | No | Overcast;32-90 F | Elbow | Contaminated | 23-0048365 | UG | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827569 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | OTHER | WIRE DOWN @ CGC 217797824949 | 20230319 | 838 | 20230319 | 1358 | 2051815 | 320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 596 | 38.3485 | -122.769 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0048459 | OH | Sus | 45702854 | NORTH COAST | MAR | Open Circuit | 0 | No | Yes | Yes | 1827670 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 6973 | 20230319 | 1312 | 20230320 | 150 | 2052061 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3790 | 38.3961 | -122.9391 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048524 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827730 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1105 | 42271105 | FUSE | 3833 | 20230319 | 1340 | 20230319 | 2026 | 2052012 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1624 | 38.3029 | -122.9551 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048501 | OH | Sus | 31640084 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1827708 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONTE RIO-1113 | 42811113 | TRANSFORMER | 217100830161 | 20230319 | 1405 | 20230319 | 1645 | 2052111 | 160 | Transformer only | Equipment Failure/Involved | Overhead | 23 | 3680 | 38.4905 | -123.0136 | No | Clear;32-90 F | Service conductor | Together | 23-0048504 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1827711 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230319 | 1500 | 20230319 | 2158 | 2052147 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 20064 | 38.4756 | -122.9526 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0048528 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1827734 | 0 | EPSS Ckt | N | 2023 | AC
SONOMA | SANTA ROSA | GEYSERVILLE-1101 | 42891101 | RECLOSER | 711966 | 20230319 | 1617 | 20230319 | 1801 | 2052217 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 151 | 15704 | 38.7488 | -122.9616 | No | Overcast-Drizzle;32-90 F |  |  | 23-0048531 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827739 | 0 | EPSS Ckt | N | 2023 | C GRD
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | FUSE | 2561 | 20230320 | 320 | 20230320 | 1243 | 2052548 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11823 | 38.4113 | -122.9652 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0048603 | OH | Sus | 31640126 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1827811 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | COTATI-1103 | 42271103 | FUSE | 4123 | 20230320 | 655 | 20230320 | 846 | 2052581 | 111 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2442 | 38.1893 | -122.9109 | No | Partly Cloudy;32-90 F |  |  | 23-0048688 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1827859 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MIRABEL-1101 | 42091101 | FUSE | 15441 | 20230320 | 955 | 20230320 | 1723 | 2052830 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4480 | 38.4737 | -122.9145 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0048838 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1827912 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1102 | 42571102 | TRANSFORMER | 217234727142 | 20230320 | 1319 | 20230321 | 825 | 2053089 | 1146 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4584 | 38.4069 | -122.965 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0048994 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827959 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MOLINO-1101 | 42571101 | TRANSFORMER | 217447326776 | 20230320 | 1412 | 20230321 | 901 | 2053165 | 1129 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1129 | 38.3991 | -122.892 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0049017 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1827974 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | MONROE 2103 | 43302103 | FUSE | 809101 | 20230320 | 1456 | 20230320 | 1557 | 2053213 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1525 | 38.4826 | -122.7553 | No | Partly Cloudy;32-90 F |  |  | 23-0048982 | OH | Sus | 0 | NORTH COAST | MAR | None | 0 | No | No | No | 1827954 | 0 | EPSS Ckt | N | 2023
SONOMA | SANTA ROSA | BELLEVUE-1102 | 43181102 | FUSE | 11523 | 20230321 | 712 | 20230321 | 1443 | 2053599 | 451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1353 | 38.3863 | -122.7229 | Yes | Overcast-Rain;32-90 F | Anchor or Guy | Broken | 23-0049130 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1828049 | 0 | EPSS Ckt | N | 2023