## 1b
Count Distribution Poles in High, Severe, Extreme Plat Maps | Count of Plat Maps in High, Severe, Extreme | Average Number of Distribution Poles per Plat Map
77796 | 1488 | 52.2823

## 1c 1d 1e
Count of Outage_ID | ME_Day
Basic_Cause | No | Yes | Total Result
3rd Party | 94 | 2 | 96
Animal | 72 | 1 | 73
Company Initiated | 91 | 2 | 93
Environmental/External | 101 | 44 | 145
Equipment Failure/Involved | 656 | 127 | 783
Unknown Cause | 380 | 154 | 534
Vegetation | 269 | 332 | 601
Wildfire Mitigation | 59 | 53 | 112
Total Result | 1722 | 715 | 2437
1c
There are 2,437 unplanned outages in PG&E's High, Severe, and Extreme plat maps from Jan 1, 2023 to Dec 31, 2024.
1d
There are 601 unplanned distribution outages in PG&E's High, Severe, and Extreme plat maps caused by vegetation contact from Jan 1, 2023 to Dec 31, 2024.
1di
There are 332 unplanned distribution outages in PG&E's High, Severe, and Extreme plat maps caused by vegetation contact from Jan 1, 2023 to Dec 31, 2024 on major event days.
1e
There are 783 unplanned distribution outages in PG&E's High, Severe, and Extreme plat maps caused by equipment failure from Jan 1, 2023 to Dec 31, 2024.
1ei
There are 127 unplanned distribution outages in PG&E's High, Severe, and Extreme plat maps caused by equipment failure from Jan 1, 2023 to Dec 31, 2024 on major event days.

## 1f
Outage_ID | Division | District_Name | Feeder_Name | Feeder_ | Device | Oper_ | Out_Date | FNL | In_Date | InTime | OIS_ | Duration | Outage_Level | Basic_Cause | Supplemental_Cause | CESO | C_Min | Open_PointLatitude | Open_PointLongitude | ME_Day | Weather | Failed_Equipment | Failed_EquipmentCondition | Event_ | ConstType | SusMom | PM | Region | Month | Fault_Type | NRC_Min | FireMitigation | Wire-DownOutage | Wire-DownEnergized | Out_ | SinglePhase | EPSS_Ckt | FTS | Year | Target
127 | CENTRAL COAST | KING CITY | KING CITY 1103 | 182031103 | RECLOSER | 7038 | 2023-01-04 | 1331 | 20230104 | 2215 | 1914100 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 793 | 408108 | 36.1935 | -121.1442 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005991 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1796336 | 0 | EPSS Ckt | N | 2023 | A & G
437 | CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 2023-01-09 | 531 | 20230109 | 1449 | 1935817 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 42833 | 36.6116 | -120.9293 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010788 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1800649 | 0 | EPSS Ckt | N | 2023 | C-GRD
632 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9607 | 2023-01-10 | 658 | 20230112 | 1339 | s1803791 | 3281 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16405 | 36.32 | -120.7121 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014566 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Three Phase Fault | 0 | No | Yes | No | 1803791 | 0 | EPSS Ckt | N | 2023
657 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9901 | 2023-01-10 | 927 | 20230110 | 1730 | 1944151 | 483 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 21252 | 36.2687 | -121.394 | Yes | Clear;32-90 F |  |  | 23-0012941 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1802505 | 0 | EPSS Ckt | N | 2023
663 | CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 51053 | 2023-01-10 | 1044 | 20230111 | 1647 | 1944584 | 1803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5409 | 36.6195 | -121.2226 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0012690 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1802329 | 0 | EPSS Ckt | N | 2023
1087 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 2023-02-03 | 125 | 20230203 | 220 | 1975469 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 935 | 36.1984 | -120.7147 | No | Clear;32-90F | Anchor or Guy | Broken | 23-0024698 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1810166 | 0 | EPSS Ckt | N | 2023
1194 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7169 | 2023-02-21 | 1002 | 20230222 | 1335 | 1990056 | 1653 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 13761 | 36.4105 | -120.9532 | Yes | Clear;32-90 F |  |  | 23-0031609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815230 | 1 | EPSS Ckt | N | 2023
1194 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 7169 | 2023-02-21 | 1002 | 20230222 | 1335 | 1990056 | 1653 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 8 | 13761 | 36.4105 | -120.9532 | Yes | Clear;32-90 F |  |  | 23-0031609 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1815230 | 1 | EPSS Ckt | N | 2023
1320 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 3027 | 2023-02-21 | 1926 | 20230221 | 2358 | 1995499 | 272 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 153 | 41616 | 36.2497 | -121.4319 | Yes | Clear;32-90F |  |  | 23-0031976 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1815573 | 0 | EPSS Ckt | N | 2023
1505 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9501 | 2023-02-24 | 2247 | 20230302 | 1823 | 2018714 | 8376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 50256 | 36.1841 | -120.6775 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820540 | 0 | EPSS Ckt | N | 2023
1505 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 9501 | 2023-02-24 | 2247 | 20230302 | 1823 | 2018714 | 8376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 50256 | 36.1841 | -120.6775 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038348 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820540 | 0 | EPSS Ckt | N | 2023
1507 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 2023-02-24 | 2248 | 20230302 | 1809 | 2018710 | 8361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 142137 | 36.1984 | -120.7147 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1820538 | 0 | EPSS Ckt | N | 2023
1570 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 553 | 2023-02-28 | 1330 | 20230302 | 1433 | 2014955 | 2943 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 12161 | 36.0629 | -120.6454 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0037499 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1819870 | 0 | EPSS Ckt | N | 2023
1768 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 2527 | 2023-03-10 | 738 | 20230311 | 1618 | 2030342 | 1960 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 76440 | 36.147 | -121.199 | No | Clear;32-90 F | Insulator | Broken | 23-0042913 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1823655 | 0 | EPSS Ckt | N | 2023
2037 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | FUSE | 9609 | 2023-03-15 | 145 | 20230316 | 1903 | 2047050 | 2478 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 416065 | 36.2816 | -121.4563 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046611 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1826328 | 0 | EPSS Ckt | N | 2023
2082 | CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 413490547650 | 2023-03-16 | 1822 | 20230317 | 1400 | 2049105 | 1168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2676 | 36.6221 | -121.2199 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047309 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | Yes | No | 1826770 | 0 | EPSS Ckt | N | 2023
2407 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | FUSE | 8937 | 2023-03-21 | 1448 | 20230322 | 1303 | 2055109 | 1335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 8472 | 36.189 | -121.1477 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 23-0049651 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1828389 | 0 | EPSS Ckt | N | 2023
2600 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 2023-03-29 | 2039 | 20230330 | 1058 | 2073716 | 859 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 9740 | 36.1984 | -120.7147 | No | Clear;32-90 F |  |  | 23-0054960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1831948 | 1 | EPSS Ckt | N | 2023
2792 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 9609 | 2023-04-27 | 738 | 20230427 | 1310 | 2098084 | 332 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 2985 | 36.2802 | -121.4545 | No | Clear;32-90 F |  |  | 23-0065596 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1839046 | 1 | Non-EPSS | N | 2023
2885 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412814734071 | 2023-05-12 | 1003 | 20230512 | 1449 | 2111152 | 286 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 286 | 36.2434 | -121.4382 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071355 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1842881 | 0 | EPSS Ckt | N | 2023
2989 | CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | TRANSFORMER | 414008343185 | 2023-06-02 | 857 | 20230602 | 903 | 2127193 | 6 | Transformer only | Animal | Bird found | 2 | 12 | 36.501 | -121.0394 | No | Partly Cloudy;32-90 F | Transformer | Burned Open | 23-0078154 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1847517 | 0 | EPSS Ckt | N | 2023
3097 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 2023-06-19 | 543 | 20230619 | 722 | 2140165 | 99 | Distribution Circuit | Animal | Bird found | 794 | 45762 | 36.1935 | -121.1442 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0083585 | OH | Sus | 45851763 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1851526 | 0 | EPSS Ckt | Y | 2023 | AC
3109 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412708533790 | 2023-06-20 | 2007 | 20230621 | 1001 | 2141762 | 834 | Transformer only | Vegetation | Tree - cutting- PG&E contractor | 5 | 4170 | 36.2358 | -121.4733 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0084068 | OH | Sus | 45854662 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852004 | 0 | EPSS Ckt | N | 2023
3124 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412773235032 | 2023-06-23 | 1255 | 20230623 | 1711 | 2144187 | 256 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 256 | 36.2712 | -121.4531 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0085185 | OH | Sus | 31653274 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1852748 | 0 | EPSS Ckt | N | 2023
3170 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | SWITCH | 8621 | 2023-06-29 | 1450 | 20230629 | 1600 | 2149067 | 70 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 3570 | 36.3604 | -120.8491 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0087257 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854118 | 0 | EPSS Ckt | N | 2023
3176 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7107 | 2023-06-29 | 2246 | 20230630 | 309 | 2149429 | 263 | Distribution Circuit | Environmental/External | Flood/Erosion | 17 | 4471 | 36.1979 | -120.714 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0087403 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Force Out | 0 | No | No | No | 1854209 | 0 | EPSS Ckt | N | 2023
3241 | CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | FUSE | 4153 | 2023-07-07 | 805 | 20230707 | 1337 | 2156048 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1660 | 36.6386 | -121.0493 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0089697 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855648 | 0 | EPSS Ckt | N | 2023
3257 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 2023-07-09 | 1607 | 20230709 | 1702 | 2157755 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1705 | 36.3588 | -120.7683 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0090247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855974 | 0 | Non-EPSS | N | 2023
3257 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 2023-07-09 | 1607 | 20230709 | 1702 | 2157755 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 1705 | 36.3588 | -120.7683 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0090247 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855974 | 0 | Non-EPSS | N | 2023
3281 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 2023-07-13 | 814 | 20230713 | 1028 | 2161315 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 4154 | 36.3588 | -120.7683 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0091608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856981 | 0 | Non-EPSS | N | 2023
3281 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | FUSE | 7865 | 2023-07-13 | 814 | 20230713 | 1028 | 2161315 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 4154 | 36.3588 | -120.7683 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0091608 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1856981 | 0 | Non-EPSS | N | 2023
3454 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414228540760 | 2023-08-07 | 1148 | 20230807 | 1804 | 2184564 | 376 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 376 | 36.4362 | -120.9671 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0101308 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1863737 | 0 | Non-EPSS | N | 2023
3464 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | JUMPER | JMPRS 1 N/O CGC 412877534455 | 2023-08-08 | 958 | 20230808 | 1340 | 2185425 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 222 | 36.2559 | -121.4173 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0101613 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Force Out | 0 | No | No | No | 1863973 | 0 | EPSS Ckt | N | 2023
3512 | CENTRAL COAST | MONTEREY | LOS OSITOS-2103 | 182082103 | SWITCH | 2237 | 2023-08-16 | 1107 | 20230816 | 1130 | 2192826 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 38 | 874 | 36.3339 | -121.499 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104947 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1866247 | 0 | EPSS Ckt | N | 2023
3521 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-08-17 | 1022 | 20230817 | 1211 | 2193671 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 981 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0105520 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1866525 | 0 | EPSS Ckt | Y | 2023 | A 50 INST
3632 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-08-31 | 941 | 20230831 | 1113 | 2206895 | 92 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 828 | 36.0057 | -121.2422 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0111173 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1870506 | 0 | EPSS Ckt | Y | 2023 | NA
3663 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-09-05 | 1539 | 20230905 | 1641 | 2210273 | 62 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 558 | 36.0057 | -121.2422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0112756 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1871379 | 0 | EPSS Ckt | Y | 2023 | AC
3732 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-09-12 | 2146 | 20230913 | 540 | 2217112 | 474 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 4266 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0115747 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1873452 | 0 | EPSS Ckt | Y | 2023 | A GRD INST
3753 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-09-15 | 1510 | 20230915 | 1635 | 2219996 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 765 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 23-0117310 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1874408 | 0 | EPSS Ckt | Y | 2023 | C-GRD
3783 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-09-22 | 2055 | 20230922 | 2213 | 2225127 | 78 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 702 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F |  |  | 23-0119968 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1876128 | 0 | EPSS Ckt | Y | 2023 | A GRD
3785 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2023-09-23 | 735 | 20230923 | 919 | 2225219 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 936 | 36.0057 | -121.2422 | No | Fog;32-90 F |  |  | 23-0120001 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1876157 | 0 | EPSS Ckt | Y | 2023 | A- C
4085 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414226140431 | 2023-11-11 | 1501 | 20231112 | 1119 | 2266824 | 1218 | Transformer only | Vegetation | Tree - fell into line | 1 | 1218 | 36.4274 | -120.9653 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0138132 | OH | Sus | 35511348 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | Yes | No | 1889784 | 0 | Non-EPSS | N | 2023
4402 | CENTRAL COAST | KING CITY | KING CITY-1106 | 182031106 | JUMPER | JMPRS 1 SPAN SOURCE SIDE CGC 415010331216 | 2023-12-28 | 3 | 20231229 | 306 | 2301635 | 1623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1623 | 36.1771 | -120.6899 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0149169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900428 | 0 | EPSS Ckt | N | 2023
4409 | CENTRAL COAST | KING CITY | JOLON-1102 | 182981102 | JUMPER | OJ 6 SS OF CGC#414075523120 | 2023-12-28 | 1240 | 20231228 | 1519 | 2301344 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2385 | 35.9399 | -121.0178 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0149111 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | DEC | Force Out | 0 | No | No | No | 1900359 | 0 | EPSS Ckt | N | 2023
4541 | CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 549180 | 2024-01-14 | 1733 | 20240114 | 1809 | 2315508 | 36 | Distribution Circuit | Equipment Failure/Involved | Overhead | 525 | 18900 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F | Regulator | Malfunctioning | 24-0010724 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1903994 | 0 | EPSS Ckt | N | 2024 | SGF/I
4551 | CENTRAL COAST | KING CITY | KING CITY-1104 | 182031104 | RECLOSER | 549180 | 2024-01-16 | 1612 | 20240116 | 2018 | 2316655 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 686 | 130438 | 36.0057 | -121.2422 | No | Partly Cloudy;32-90 F |  |  | 24-0011263 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1904349 | 0 | EPSS Ckt | N | 2024 | SGF/INST
4998 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | FUSE | 8997 | 2024-02-04 | 1401 | 20240208 | 1715 | 2341039 | 5954 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17862 | 36.0219 | -121.2481 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021354 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1911188 | 0 | EPSS Ckt | N | 2024
5411 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412869034355 | 2024-02-19 | 736 | 20240219 | 1358 | 2380443 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 764 | 36.2528 | -121.4194 | No | Partly Cloudy-Fog;32-90 F | Transformer (OH) | Broken | 24-0030714 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917932 | 0 | EPSS Ckt | N | 2024
5424 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | TRANSFORMER | 413488430321 | 2024-02-19 | 1806 | 20240220 | 1 | 2381952 | 355 | Transformer only | Vegetation | Tree - fell into line | 1 | 355 | 36.1474 | -121.2055 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0031069 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1918185 | 0 | EPSS Ckt | N | 2024
5609 | CENTRAL COAST | HOLLISTER | HOLLISTER-2105 | 182492105 | FUSE | 51053 | 2024-03-07 | 1340 | 20240307 | 1515 | 2399441 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 285 | 36.6195 | -121.2226 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0039360 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1923293 | 0 | EPSS Ckt | N | 2024
5864 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7093 | 2024-04-13 | 222 | 20240415 | 1126 | 2430087 | 3424 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 13696 | 36.096 | -120.6843 | No | Clear;32-90 F |  |  | 24-0054338 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1933262 | 0 | EPSS Ckt | N | 2024
6105 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7109 | 2024-05-26 | 12 | 20240526 | 1229 | 2467680 | 737 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 21373 | 36.1946 | -120.7075 | No | Clear;32-90 F |  |  | 24-0070057 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1944256 | 0 | EPSS Ckt | N | 2024
6269 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414202241254 | 2024-06-18 | 733 | 20240618 | 1752 | 2488928 | 619 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 619 | 36.4478 | -120.9785 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0078133 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950237 | 0 | Non-EPSS | N | 2024
6272 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414207541535 | 2024-06-18 | 1154 | 20240618 | 2030 | 2489311 | 516 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 516 | 36.4553 | -120.981 | No | Clear;32-90 F | Transformer (OH) | Deteriorated | 24-0078153 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1950243 | 0 | Non-EPSS | N | 2024
6276 | CENTRAL COAST | HOLLISTER | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 2024-06-19 | 9 | 20240619 | 1028 | 2489728 | 619 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 73042 | 36.6116 | -120.9293 | No | Clear;32-90 F |  |  | 24-0078359 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1950339 | 0 | EPSS Ckt | Y | 2024 | B-C
6332 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-06-26 | 1331 | 20240626 | 1417 | 2496870 | 46 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 414 | 36.0057 | -121.2422 | No | Clear;Above 90 | Switch (OH) | Normal | 24-0080914 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Three Phase Fault | 0 | No | No | No | 1952227 | 0 | EPSS Ckt | Y | 2024 | ABC
6349 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-06-28 | 757 | 20240628 | 954 | 2498296 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1053 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0081665 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1952696 | 0 | EPSS Ckt | Y | 2024 | B- GRD- INST OC
6383 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-07-02 | 407 | 20240702 | 704 | 2501509 | 177 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 1593 | 36.0057 | -121.2422 | No | Clear;32-90 F | Metering Equipment | Normal | 24-0082770 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1953465 | 0 | EPSS Ckt | Y | 2024 | A GRD
6396 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-07-04 | 1003 | 20240704 | 1115 | 2504891 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 648 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0083971 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954124 | 0 | EPSS Ckt | Y | 2024 | A PHASE AND GRD
6402 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-07-04 | 1507 | 20240704 | 1607 | 2505165 | 60 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 540 | 36.0057 | -121.2422 | No | Clear;Above 90 | Customer Equipment | Normal | 24-0084045 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Three Phase Fault | 0 | No | No | No | 1954157 | 0 | EPSS Ckt | Y | 2024 | ABC PHASE
6405 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-07-05 | 200 | 20240705 | 439 | 2505644 | 159 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1431 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0084181 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954266 | 0 | EPSS Ckt | Y | 2024 | A&GRD
6423 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 2024-07-07 | 347 | 20240707 | 1145 | 2508669 | 478 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 796 | 380488 | 36.1935 | -121.1442 | No | Clear;32-90 F |  |  | 24-0084803 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1954701 | 0 | EPSS Ckt | Y | 2024 | SGF & DCD ALARM
6514 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-07-18 | 2148 | 20240719 | 3 | 2520588 | 135 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1215 | 36.0057 | -121.2422 | No | Clear;32-90 F |  |  | 24-0089526 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1957761 | 0 | EPSS Ckt | Y | 2024 | A GRD
6555 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414694938071 | 2024-07-25 | 1827 | 20240726 | 2040 | 2526957 | 1573 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1573 | 36.3652 | -120.8024 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0092215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959598 | 0 | Non-EPSS | N | 2024
6555 | CENTRAL COAST | KING CITY | LOS OSITOS-2101 | 182082101 | TRANSFORMER | 414694938071 | 2024-07-25 | 1827 | 20240726 | 2040 | 2526957 | 1573 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1573 | 36.3652 | -120.8024 | No | Clear;Above 90 | Service conductor | Broken- wire on ground | 24-0092215 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1959598 | 0 | Non-EPSS | N | 2024
6966 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 2024-09-26 | 727 | 20240926 | 935 | 2577939 | 128 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 796 | 101888 | 36.1935 | -121.1442 | No | Fog;32-90 F |  |  | 24-0115772 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975412 | 0 | EPSS Ckt | Y | 2024 | A C INST
6978 | CENTRAL COAST | KING CITY | LOS OSITOS-2103 | 182082103 | TRANSFORMER | 412733535900 | 2024-09-27 | 1418 | 20240928 | 2028 | 2579529 | 1810 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 3620 | 36.2948 | -121.4683 | No | Clear;Above 90 | Transformer | Deteriorated | 24-0116900 | OH | Sus | 31710322 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1976180 | 0 | EPSS Ckt | N | 2024
7111 | CENTRAL COAST | KING CITY | SAN ARDO-1102 | 182191102 | FUSE | 7109 | 2024-10-15 | 8 | 20241015 | 215 | 2594742 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 3683 | 36.1946 | -120.7075 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0123147 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1980510 | 0 | EPSS Ckt | N | 2024
7116 | CENTRAL COAST | MONTEREY | LAURELES-1111 | 182371111 | SWITCH | 2237 | 2024-10-15 | 1924 | 20241015 | 1938 | 2595657 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 27 | 378 | 36.3339 | -121.499 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0114389 | OH | Sus | 35541161 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1980843 | 0 | EPSS Ckt | N | 2024
7139 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-10-18 | 231 | 20241019 | 1136 | 2598123 | 1985 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 17865 | 36.0057 | -121.2422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124333 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | None | 0 | No | No | No | 1981615 | 0 | EPSS Ckt | N | 2024 | N/A
7195 | CENTRAL COAST | KING CITY | JOLON-1103 | 182981103 | RECLOSER | 549180 | 2024-10-23 | 541 | 20241023 | 548 | 2601759 | 7 | Distribution Circuit | 3rd Party | Customer Equipment | 9 | 63 | 36.0062 | -121.2421 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0126630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Three Phase Fault | 0 | No | No | No | 1982772 | 0 | EPSS Ckt | Y | 2024 | A B & C PHSE
7332 | CENTRAL COAST | KING CITY | KING CITY-1103 | 182031103 | RECLOSER | 7038 | 2024-11-10 | 1526 | 20241110 | 1712 | 2620277 | 106 | Distribution Circuit | Animal | Bird found | 796 | 84376 | 36.1935 | -121.1442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133955 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1988227 | 0 | EPSS Ckt | Y | 2024 | A&C
11084 | DIABLO | DIABLO | CLAYTON 2212 | 12022212 | FUSE | 1226 | 2023-01-02 | 1818 | 20230102 | 2153 | 1910508 | 215 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 1217 | 37.889 | -121.8698 | No | Clear;32-90 F |  |  | 23-0004904 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1795508 | 1 | EPSS Ckt | N | 2023
11130 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | SWITCH | 7764 | 2023-01-05 | 2005 | 20230106 | 16 | 1923785 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 226 | 56726 | 37.8931 | -121.8734 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0007913 | OH | Sus | 0 | BAY AREA | JAN | Force Out | 0 | No | No | No | 1798059 | 0 | EPSS Ckt | N | 2023
11228 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7619 | 2023-01-15 | 1121 | 20230115 | 1738 | 1955859 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2639 | 37.8885 | -121.8693 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016660 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | Yes | No | 1805396 | 0 | EPSS Ckt | N | 2023
11254 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2944 | 2023-01-17 | 513 | 20230117 | 750 | 1959083 | 157 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 151 | 23707 | 37.8969 | -121.8597 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0017467 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1806132 | 0 | EPSS Ckt | N | 2023
11278 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 1226 | 2023-01-22 | 2225 | 20230123 | 939 | 1965204 | 674 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 11458 | 37.889 | -121.8698 | No | Clear;32-90 F |  |  | 23-0019989 | OH | Sus | 0 | BAY AREA | JAN | Line to Line | 0 | No | No | No | 1807422 | 0 | EPSS Ckt | N | 2023
11291 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7143 | 2023-01-26 | 852 | 20230126 | 1101 | 1968644 | 129 | Distribution Circuit | Animal | Squirrel | 25 | 3225 | 37.9241 | -121.912 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0021719 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1808403 | 0 | EPSS Ckt | N | 2023
11300 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2956 | 2023-02-01 | 915 | 20230201 | 1305 | 1973654 | 230 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 690 | 37.9033 | -121.8844 | No | Clear;32-90F |  |  | 23-0023954 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1809781 | 0 | EPSS Ckt | N | 2023
11471 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 681608 | 2023-03-14 | 1308 | 20230315 | 1210 | 2043294 | 1382 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 557 | 767968 | 37.9245 | -121.9125 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0046275 | OH | Sus | 35431781 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1826119 | 0 | EPSS Ckt | N | 2023 | A PHASE GRD TIMED
11526 | DIABLO | DIABLO | CLAYTON-2213 | 12022213 | FUSE | 1424 | 2023-03-16 | 1213 | 20230316 | 1430 | 2048366 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 274 | 37.9429 | -121.8905 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0047001 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826555 | 0 | EPSS Ckt | N | 2023
11526 | DIABLO | DIABLO | CLAYTON-2213 | 12022213 | FUSE | 1424 | 2023-03-16 | 1213 | 20230316 | 1430 | 2048366 | 137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 274 | 37.9429 | -121.8905 | No | Clear;32-90 F | Conductor- Overhead | Burned/flashed | 23-0047001 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1826555 | 0 | EPSS Ckt | N | 2023
11657 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 16798 | 2023-03-25 | 1638 | 20230325 | 1812 | 2067183 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1222 | 37.8862 | -121.7755 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0052527 | OH | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | Yes | No | 1830478 | 0 | EPSS Ckt | N | 2023
11705 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2951 | 2023-04-06 | 652 | 20230406 | 902 | 2081368 | 130 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 63 | 8182 | 37.8879 | -121.8675 | No | Clear;32-90 F |  |  | 23-0057800 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1833657 | 1 | EPSS Ckt | N | 2023
11839 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | TRANSFORMER | T5311 | 2023-06-13 | 902 | 20230613 | 1218 | 2136038 | 196 | Transformer only | Equipment Failure/Involved | Underground | 9 | 1764 | 37.9278 | -121.9406 | No | Clear;32-90 F | Transformer (UG) | Broken | 23-0081846 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1850289 | 0 | EPSS Ckt | N | 2023
11840 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | SWITCH | 7810 | 2023-06-13 | 1337 | 20230613 | 1538 | 2136232 | 121 | Distribution Circuit | Equipment Failure/Involved | Underground | 19 | 1149 | 37.9328 | -121.9393 | No | Clear;32-90 F | Transformer (UG) | Deteriorated | 23-0081846 | UG | Sus | 0 | BAY AREA | JUN | Force Out | 0 | No | No | No | 1850350 | 0 | EPSS Ckt | N | 2023
11846 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 9748 | 2023-06-16 | 146 | 20230616 | 1210 | 2138125 | 624 | Distribution Circuit | 3rd Party | Vehicle | 557 | 16138 | 37.8792 | -121.7708 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0082993 | OH | Sus | 35458390 | BAY AREA | JUN | Line to Ground | 0 | No | Yes | Yes | 1850964 | 0 | EPSS Ckt | Y | 2023
11849 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2023-06-17 | 2333 | 20230618 | 33 | 2139634 | 60 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 15360 | 37.9039 | -121.8741 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0083468 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1851411 | 0 | EPSS Ckt | Y | 2023 | A- GRD
12078 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 681608 | 2023-08-22 | 627 | 20230822 | 1051 | 2198862 | 264 | Distribution Circuit | Company Initiated | Coordination failure | 297 | 62505 | 37.9245 | -121.9125 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0107354 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867836 | 0 | EPSS Ckt | Y | 2023 | INST OC- B GRD
12079 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2023-08-22 | 627 | 20230822 | 1205 | 2199233 | 338 | Distribution Circuit | Company Initiated | Personnel- company | 241 | 80338 | 37.9039 | -121.8741 | No | Clear;32-90 F | Recloser | Normal | 23-0107354 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1867999 | 0 | EPSS Ckt | Y | 2023 | A GRD
12080 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 11145 | 2023-08-22 | 627 | 20230822 | 1358 | 2199334 | 451 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1804 | 37.8877 | -121.782 | No | Clear;32-90 F |  |  | 23-0107626 | OH | Sus | 0 | BAY AREA | AUG | Line to Ground | 0 | No | No | No | 1868053 | 0 | EPSS Ckt | N | 2023
12108 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7888 | 2023-08-30 | 1553 | 20230830 | 2014 | 2206207 | 261 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 261 | 37.8878 | -121.87 | No | Clear;Above 90 | Pothead(Riser Termination) | Arcing | 23-0110949 | OH | Sus | 0 | BAY AREA | AUG | Force Out | 0 | No | No | No | 1870277 | 0 | EPSS Ckt | N | 2023
12139 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2023-09-13 | 859 | 20230913 | 1405 | 2217527 | 306 | Distribution Circuit | Animal | Squirrel | 243 | 45449 | 37.9039 | -121.8741 | No | Clear;32-90 F | Fuse | Broken | 23-0115938 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1873663 | 0 | EPSS Ckt | Y | 2023 | C- GRD
12392 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7745 | 2024-01-13 | 2146 | 20240114 | 841 | 2315099 | 655 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 16375 | 37.9174 | -121.9067 | No | Overcast-Drizzle;32-90 F |  |  | 24-0010629 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1903920 | 0 | EPSS Ckt | N | 2024
12439 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7143 | 2024-01-31 | 2044 | 20240201 | 648 | 2330449 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7862 | 37.9241 | -121.912 | No | Overcast-Rain;32-90 F | Other | Broken | 24-0017693 | OH | Sus | 0 | BAY AREA | JAN | Line to Ground | 0 | No | No | No | 1908088 | 0 | EPSS Ckt | N | 2024
12528 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7141 | 2024-02-04 | 1728 | 20240205 | 1129 | 2350126 | 1081 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 38916 | 37.9226 | -121.9068 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0021869 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1911607 | 0 | EPSS Ckt | N | 2024
12580 | DIABLO | DIABLO | TASSAJARA-2107 | 14662107 | TRANSFORMER | 100000037035 | 2024-02-13 | 1329 | 20240214 | 218 | 2375280 | 769 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 769 | 37.8784 | -121.9152 | No | Partly Cloudy;32-90 F | Transformer | Normal | 24-0028596 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916630 | 0 | EPSS Ckt | N | 2024
12582 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 15456 | 2024-02-14 | 1220 | 20240214 | 1836 | 2376339 | 376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 376 | 37.8589 | -121.8916 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0028974 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | Yes | 1916869 | 0 | EPSS Ckt | N | 2024
12583 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7141 | 2024-02-14 | 2018 | 20240214 | 2210 | 2376723 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 4032 | 37.9226 | -121.9068 | No | Overcast-Drizzle;32-90 F |  |  | 24-0029237 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1916955 | 0 | EPSS Ckt | N | 2024
12595 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7745 | 2024-02-19 | 913 | 20240219 | 1049 | 2380584 | 96 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 2400 | 37.9174 | -121.9067 | No | Partly Cloudy-Rain;32-90 F |  |  | 24-0030747 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1917959 | 0 | EPSS Ckt | N | 2024
12604 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 7745 | 2024-02-19 | 1327 | 20240219 | 1638 | 2381397 | 191 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 4775 | 37.9174 | -121.9067 | No | Overcast-Drizzle;32-90 F |  |  | 24-0030996 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918131 | 0 | EPSS Ckt | N | 2024
12607 | DIABLO | DIABLO | CLAYTON-2213 | 12022213 | TRANSFORMER | 316008352817 | 2024-02-20 | 1052 | 20240220 | 1740 | 2382840 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 972 | 37.9426 | -121.8855 | No | Overcast-Drizzle;32-90 F | Transformer | Burned Open | 24-0031448 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | No | No | 1918430 | 0 | EPSS Ckt | N | 2024
12663 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 681608 | 2024-03-04 | 741 | 20240304 | 901 | s1922266 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 554 | 44320 | 37.9245 | -121.9125 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0037430 | OH | Sus | 0 | BAY AREA | MAR | None | 0 | No | No | No | 1922266 | 0 | EPSS Ckt | N | 2024 | N/A
12685 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2427 | 2024-03-14 | 1012 | 20240318 | 1101 | 2404476 | 5809 | Distribution Circuit | 3rd Party | Customer Equipment | 4 | 23236 | 37.8834 | -121.8771 | No | Clear;32-90 F | Customer Equipment | Failed/Faulted | 24-0042007 | OH | Sus | 0 | BAY AREA | MAR | Line to Line | 0 | No | No | No | 1925058 | 0 | EPSS Ckt | N | 2024
12689 | DIABLO | DIABLO | KIRKER-2104 | 14452104 | FUSE | 8769 | 2024-03-14 | 1048 | 20240314 | 1307 | 2404814 | 139 | Distribution Circuit | 3rd Party | Customer Equipment | 2 | 278 | 37.9762 | -121.8976 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0042158 | OH | Sus | 0 | BAY AREA | MAR | Line to Ground | 0 | No | No | No | 1925140 | 0 | EPSS Ckt | N | 2024
12752 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 8109 | 2024-04-08 | 1955 | 20240409 | 849 | 2426608 | 774 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 12384 | 37.905 | -121.8744 | No | Clear;32-90 F |  |  | 24-0052389 | OH | Sus | 0 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1932018 | 0 | EPSS Ckt | N | 2024
12965 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2024-06-16 | 2107 | 20240616 | 2245 | 2487265 | 98 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 254 | 24688 | 37.9039 | -121.8741 | No | Clear;32-90 F |  |  | 24-0077531 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1949681 | 0 | EPSS Ckt | Y | 2024 | C- GRD
12969 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 13039 | 2024-06-17 | 1314 | 20240617 | 1541 | 2487917 | 147 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 207 | 37.881 | -121.8673 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0077753 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1949910 | 0 | EPSS Ckt | N | 2024
12992 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2024-06-23 | 619 | 20240623 | 1615 | 2492862 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 254 | 40317 | 37.9039 | -121.8741 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079503 | OH | Sus | 0 | BAY AREA | JUN | Line to Ground | 0 | No | No | No | 1951120 | 0 | EPSS Ckt | Y | 2024 | C & GRD
13132 | DIABLO | DIABLO | KIRKER-2104 | 14452104 | FUSE | 8769 | 2024-07-13 | 2312 | 20240714 | 2326 | 2516335 | 1454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2908 | 37.9762 | -121.8976 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0087647 | OH | Sus | 0 | BAY AREA | JUL | Force Out | 0 | No | No | No | 1956559 | 0 | EPSS Ckt | N | 2024
13330 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 13083 | 2024-09-15 | 1650 | 20240916 | 327 | 2568953 | 637 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5733 | 37.8905 | -121.7698 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0111215 | OH | Sus | 46321985 | BAY AREA | SEP | Line to Ground | 0 | No | Yes | No | 1972288 | 0 | EPSS Ckt | N | 2024
13331 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 16798 | 2024-09-15 | 1658 | 20240915 | 1948 | 2568956 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 680 | 37.8862 | -121.7755 | No | Clear-Strong Winds;32-90 F |  |  | 24-0111227 | OH | Sus | 0 | BAY AREA | SEP | Line to Ground | 0 | No | No | No | 1972304 | 0 | EPSS Ckt | N | 2024
13442 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 681608 | 2024-10-17 | 2056 | 20241019 | 1502 | 2597989 | 2526 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 300 | 757800 | 37.9245 | -121.9125 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0123752 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981565 | 0 | EPSS Ckt | N | 2024 | N/A
13443 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2024-10-17 | 2056 | 20241019 | 1506 | 2597998 | 2530 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 250 | 632500 | 37.9039 | -121.8741 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123752 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981566 | 0 | EPSS Ckt | N | 2024 | N/A
13444 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2427 | 2024-10-17 | 2056 | 20241019 | 1515 | 2598156 | 2539 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 10156 | 37.8834 | -121.8771 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123752 | OH | Sus | 0 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981634 | 0 | EPSS Ckt | N | 2024
13492 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 1703 | 2024-11-01 | 425 | 20241101 | 710 | 2609985 | 165 | Distribution Circuit | Animal | Squirrel | 3 | 495 | 37.8936 | -121.794 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0130371 | OH | Sus | 0 | BAY AREA | NOV | Line to Ground | 0 | No | No | No | 1985370 | 0 | EPSS Ckt | N | 2024
13512 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | JUMPER | OJ 1P/NE CGC 316032451545 | 2024-11-05 | 912 | 20241105 | 1116 | 2614076 | 124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 124 | 37.908 | -121.8758 | Yes | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0131931 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986533 | 0 | EPSS Ckt | N | 2024
13522 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 681608 | 2024-11-06 | 700 | 20241107 | 854 | 2615719 | 1554 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 299 | 464646 | 37.9245 | -121.9125 | No | Clear;32-90 F |  |  | 24-0131749 | OH | Sus | 8216497 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986973 | 0 | EPSS Ckt | N | 2024 | NONE
13523 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 2024-11-06 | 700 | 20241107 | 856 | 2615730 | 1556 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 98 | 152488 | 37.9039 | -121.8741 | No | Clear;32-90 F |  |  | 24-0131749 | OH | Sus | 8216497 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986975 | 0 | EPSS Ckt | N | 2024 | NONE
13524 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | RECLOSER | 204416 | 2024-11-06 | 700 | 20241107 | 857 | 2615737 | 1557 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 152 | 236664 | 37.8796 | -121.8679 | No | Clear;32-90 F |  |  | 24-0131749 | OH | Sus | 8216497 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986980 | 0 | EPSS Ckt | N | 2024 | NONE
13525 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2427 | 2024-11-06 | 700 | 20241107 | 904 | 2616258 | 1564 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 6256 | 37.8834 | -121.8771 | No | Clear;32-90 F |  |  | 24-0131749 | OH | Sus | 8216497 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987147 | 0 | EPSS Ckt | N | 2024
13684 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | FUSE | 2944 | 2024-12-12 | 908 | 20241212 | 1122 | 2650663 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 149 | 19966 | 37.8969 | -121.8597 | No | Overcast-Drizzle;32-90 F |  |  | 24-0144598 | OH | Sus | 0 | BAY AREA | DEC | Line to Line | 0 | No | No | No | 1996825 | 0 | EPSS Ckt | N | 2024
13774 | DIABLO | DIABLO | CLAYTON-2212 | 12022212 | TRANSFORMER | 316066851065 | 2024-12-30 | 1043 | 20241231 | 457 | 2672452 | 1094 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5210 | 37.8948 | -121.8642 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0148218 | OH | Sus | 0 | BAY AREA | DEC | Line to Ground | 0 | No | No | No | 2001456 | 0 | EPSS Ckt | N | 2024
15975 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418947058460 | 2023-01-10 | 812 | 20230110 | 2201 | 1943522 | 829 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 829 | 36.9458 | -119.3617 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0013136 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802691 | 0 | EPSS Ckt | N | 2023
15977 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-01-10 | 1043 | 20230111 | 1503 | 1947600 | 1700 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3400 | 37.0399 | -119.2916 | Yes | Clear;32-90F |  |  | 23-0013517 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1803014 | 0 | EPSS Ckt | N | 2023
15977 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-01-10 | 1043 | 20230111 | 1503 | 1947600 | 1700 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3400 | 37.0399 | -119.2916 | Yes | Clear;32-90F |  |  | 23-0013517 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1803014 | 0 | EPSS Ckt | N | 2023
16032 | FRESNO | FRESNO | BALCH NO 1 1101 | 252501101 | FUSE | D4128 | 2023-01-14 | 1956 | 20230114 | 2215 | 1955155 | 139 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1 | 139 | 36.9031 | -119.1189 | Yes | Clear;32-90F |  |  | 23-0016397 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805147 | 1 | EPSS Ckt | N | 2023
16175 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418715064384 | 2023-01-23 | 907 | 20230123 | 1327 | 1965537 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 260 | 37.1003 | -119.4416 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020079 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807520 | 0 | EPSS Ckt | N | 2023
16647 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-02-24 | 2042 | 20230228 | 1548 | 2010205 | 5466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 10932 | 37.0399 | -119.2916 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035786 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818611 | 0 | EPSS Ckt | N | 2023
16647 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-02-24 | 2042 | 20230228 | 1548 | 2010205 | 5466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 10932 | 37.0399 | -119.2916 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035786 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818611 | 0 | EPSS Ckt | N | 2023
16658 | FRESNO | FRESNO | DUNLAP-1103 | 254061103 | FUSE | 665776 | 2023-02-25 | 117 | 20230301 | 953 | 2010243 | 6276 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 50208 | 36.7347 | -119.0611 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035024 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818635 | 0 | EPSS Ckt | N | 2023
16661 | FRESNO | FRESNO | BALCH NO 1-1101 | 252501101 | RECLOSER | 406582 | 2023-02-25 | 133 | 20230228 | 1710 | 2007477 | 5257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5257 | 36.9079 | -119.1008 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0035015 | OH | Sus | 35427376 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817882 | 0 | EPSS Ckt | N | 2023 | AB
16671 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D1982 | 2023-02-25 | 237 | 20230227 | 1300 | 2007521 | 3503 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 24521 | 36.949 | -119.3733 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035911 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818725 | 0 | EPSS Ckt | N | 2023
16696 | FRESNO | FRESNO | BALCH NO 1-1101 | 252501101 | FUSE | D4128 | 2023-02-25 | 824 | 20230226 | 1758 | 2008691 | 2014 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 2014 | 36.9031 | -119.1189 | Yes | Strong Winds-Snow-Clear;32-90 F |  |  | 23-0035288 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818126 | 0 | EPSS Ckt | N | 2023
16713 | FRESNO | FRESNO | COALINGA NO 1-1108 | 252161108 | FUSE | 9854F | 2023-02-25 | 1314 | 20230225 | 1655 | 2008507 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1326 | 36.1295 | -120.6041 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035433 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818281 | 0 | EPSS Ckt | N | 2023
17119 | FRESNO | FRESNO | BALCH NO 1-1101 | 252501101 | FUSE | D4128 | 2023-03-21 | 1243 | 20230324 | 1157 | 2059361 | 4274 | Distribution Circuit | Environmental/External | Lightning | 1 | 4274 | 36.9031 | -119.1189 | Yes | Overcast-Rain;32-90 F | Lightning Arrestor | Burned/flashed | 23-0049936 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828624 | 1 | EPSS Ckt | N | 2023
18172 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-06-27 | 1808 | 20230630 | 1542 | 2147272 | 4174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12522 | 36.3481 | -120.6014 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0086313 | OH | Sus | 45862193 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1853544 | 0 | EPSS Ckt | N | 2023
18172 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-06-27 | 1808 | 20230630 | 1542 | 2147272 | 4174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12522 | 36.3481 | -120.6014 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0086313 | OH | Sus | 45862193 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1853544 | 0 | EPSS Ckt | N | 2023
18172 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-06-27 | 1808 | 20230630 | 1542 | 2147272 | 4174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12522 | 36.3481 | -120.6014 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0086313 | OH | Sus | 45862193 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | Yes | No | 1853544 | 0 | EPSS Ckt | N | 2023
18185 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D4495 | 2023-06-28 | 2217 | 20230629 | 244 | 2148386 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 6942 | 37.1133 | -119.4488 | No | Clear;32-90 F | Other | Broken | 23-0086894 | OH | Sus | 31653904 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853890 | 0 | EPSS Ckt | N | 2023
18272 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-07-07 | 1015 | 20230707 | 1400 | 2156092 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 675 | 36.3481 | -120.6014 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0089729 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855669 | 0 | EPSS Ckt | N | 2023
18272 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-07-07 | 1015 | 20230707 | 1400 | 2156092 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 675 | 36.3481 | -120.6014 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0089729 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855669 | 0 | EPSS Ckt | N | 2023
18272 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2023-07-07 | 1015 | 20230707 | 1400 | 2156092 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 675 | 36.3481 | -120.6014 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0089729 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1855669 | 0 | EPSS Ckt | N | 2023
18468 | FRESNO | FRESNO | BALCH NO 1-1101 | 252501101 | RECLOSER | 105414 | 2023-07-26 | 11 | 20230726 | 1036 | 2173958 | 625 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 16875 | 36.9089 | -119.0887 | No | Overcast-Heat Wave;Above 90 |  |  | 23-0096817 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1860489 | 0 | EPSS Ckt | Y | 2023 | B GRD TIME OC
18683 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-08-18 | 2240 | 20230819 | 1340 | 2195369 | 900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1800 | 37.0399 | -119.2916 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0106311 | OH | Sus | 31664007 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866955 | 0 | EPSS Ckt | N | 2023
18683 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2023-08-18 | 2240 | 20230819 | 1340 | 2195369 | 900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1800 | 37.0399 | -119.2916 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0106311 | OH | Sus | 31664007 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866955 | 0 | EPSS Ckt | N | 2023
18850 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | TRANSFORMER | 415161038120 | 2023-08-23 | 1416 | 20230823 | 1558 | 2200279 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 204 | 36.3694 | -120.6454 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0108215 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868377 | 0 | EPSS Ckt | N | 2023
18850 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | TRANSFORMER | 415161038120 | 2023-08-23 | 1416 | 20230823 | 1558 | 2200279 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 204 | 36.3694 | -120.6454 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0108215 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868377 | 0 | EPSS Ckt | N | 2023
18850 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | TRANSFORMER | 415161038120 | 2023-08-23 | 1416 | 20230823 | 1558 | 2200279 | 102 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 204 | 36.3694 | -120.6454 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0108215 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1868377 | 0 | EPSS Ckt | N | 2023
18962 | FRESNO | FRESNO | COALINGA NO 1-1108 | 252161108 | FUSE | 9995F | 2023-09-07 | 1621 | 20230907 | 1807 | 2212017 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 636 | 36.0972 | -120.5208 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0113796 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871953 | 0 | EPSS Ckt | N | 2023
19854 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9509F | 2024-01-07 | 856 | 20240107 | 1059 | 2309135 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3075 | 36.2315 | -120.5752 | No | Clear;32-90 F |  |  | 24-0007752 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902121 | 0 | EPSS Ckt | N | 2024
19854 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9509F | 2024-01-07 | 856 | 20240107 | 1059 | 2309135 | 123 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3075 | 36.2315 | -120.5752 | No | Clear;32-90 F |  |  | 24-0007752 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1902121 | 0 | EPSS Ckt | N | 2024
20240 | FRESNO | FRESNO | COALINGA NO 1-1108 | 252161108 | FUSE | 9854F | 2024-02-20 | 1827 | 20240220 | 2310 | 2383342 | 283 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1698 | 36.1291 | -120.6045 | No | Partly Cloudy;32-90 F |  |  | 24-0031778 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1918586 | 0 | EPSS Ckt | N | 2024
20903 | FRESNO | FRESNO | COALINGA NO 1-1108 | 252161108 | FUSE | 9854F | 2024-04-25 | 1500 | 20240425 | 1645 | 2438976 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 630 | 36.1291 | -120.6045 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0058904 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936436 | 0 | EPSS Ckt | N | 2024
21042 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2024-05-07 | 1313 | 20240507 | 1432 | 2447976 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 158 | 37.0399 | -119.2916 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0063088 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939682 | 0 | EPSS Ckt | N | 2024
21042 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D3816 | 2024-05-07 | 1313 | 20240507 | 1432 | 2447976 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 158 | 37.0399 | -119.2916 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0063088 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1939682 | 0 | EPSS Ckt | N | 2024
21125 | FRESNO | FRESNO | DUNLAP-1103 | 254061103 | FUSE | 7258F | 2024-05-14 | 1252 | 20240514 | 1353 | 2453573 | 61 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 2135 | 36.7368 | -119.0473 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0065821 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941613 | 0 | EPSS Ckt | N | 2024
21271 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418933058820 | 2024-05-29 | 1208 | 20240529 | 1222 | 2469860 | 14 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 14 | 36.9356 | -119.3667 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0070930 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1944944 | 0 | EPSS Ckt | N | 2024
21441 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418903458023 | 2024-06-12 | 816 | 20240612 | 902 | 2483252 | 46 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 46 | 36.9264 | -119.3766 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0076110 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948610 | 0 | EPSS Ckt | N | 2024
21513 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-06-18 | 1113 | 20240618 | 1239 | 2489163 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 258 | 36.3481 | -120.6014 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0078035 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950186 | 0 | EPSS Ckt | N | 2024
21513 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-06-18 | 1113 | 20240618 | 1239 | 2489163 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 258 | 36.3481 | -120.6014 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0078035 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950186 | 0 | EPSS Ckt | N | 2024
21513 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-06-18 | 1113 | 20240618 | 1239 | 2489163 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 258 | 36.3481 | -120.6014 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0078035 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950186 | 0 | EPSS Ckt | N | 2024
21716 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418981061953 | 2024-06-25 | 1343 | 20240626 | 357 | 2495956 | 854 | Transformer only | Environmental/External | Lightning | 2 | 1708 | 37.0341 | -119.3505 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0080557 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1951982 | 0 | EPSS Ckt | N | 2024
21758 | FRESNO | FRESNO | BALCH NO 1-1101 | 252501101 | FUSE | 235255 | 2024-06-27 | 1717 | 20240703 | 1725 | s1952561 | 8648 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 28 | 6397 | 36.9035 | -119.1209 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081380 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 214898 | No | No | No | 1952561 | 0 | EPSS Ckt | N | 2024
21812 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | TRANSFORMER | 418981061953 | 2024-07-02 | 1632 | 20240703 | 135 | 2502441 | 543 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1086 | 37.0341 | -119.3505 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0083290 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953726 | 0 | EPSS Ckt | N | 2024
22499 | FRESNO | FRESNO | COALINGA NO 1-1108 | 252161108 | FUSE | 9808F | 2024-09-03 | 1513 | 20240909 | 1230 | 2558556 | 8250 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 8 | 31 | 36.1181 | -120.5863 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0106263 | OH | Sus | 31707253 | CENTRAL VALLEY | SEP | Force Out | 59187 | No | No | No | 1969144 | 0 | EPSS Ckt | N | 2024
22513 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9514F | 2024-09-04 | 1700 | 20240909 | 1256 | 2559573 | 6956 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 60 | 7801 | 36.2257 | -120.5333 | No | Clear;Above 90 | Cutout- fuse holder | Normal | 24-0106910 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 406019 | No | No | No | 1969494 | 0 | EPSS Ckt | N | 2024
23548 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-12-14 | 938 | 20241215 | 1230 | 2661781 | 1612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3226 | 36.3481 | -120.6014 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0146352 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998724 | 1 | EPSS Ckt | N | 2024
23548 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-12-14 | 938 | 20241215 | 1230 | 2661781 | 1612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3226 | 36.3481 | -120.6014 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0146352 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998724 | 1 | EPSS Ckt | N | 2024
23548 | FRESNO | FRESNO | COALINGA NO 2-1105 | 252381105 | FUSE | 9507 | 2024-12-14 | 938 | 20241215 | 1230 | 2661781 | 1612 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3226 | 36.3481 | -120.6014 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0146352 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998724 | 1 | EPSS Ckt | N | 2024
23631 | FRESNO | FRESNO | AUBERRY-1101 | 254151101 | FUSE | D4386 | 2024-12-25 | 1139 | 20241225 | 1516 | 2669639 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 6076 | 36.9333 | -119.3682 | No | Partly Cloudy-Drizzle;32-90 F | Jumper | Bent or Twisted | 24-0147733 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000794 | 0 | EPSS Ckt | N | 2024
23710 | HUMBOLDT | WILLOW CREEK | HOOPA-1101 | 192401101 | FUSE | 978307 | 2023-01-03 | 1443 | 20230108 | 1530 | 1911723 | 7247 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 94211 | 41.3493 | -123.8694 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005288 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1795771 | 0 | EPSS Ckt | N | 2023
23949 | HUMBOLDT | UKIAH | MIDDLETOWN 1101 | 43141101 | TRIP-SAVER | 1325 | 2023-01-04 | 1233 | 20230106 | 1541 | 1913854 | 3068 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 300664 | 38.8761 | -122.7755 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0006186 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1796500 | 0 | EPSS Ckt | N | 2023 | A B
24054 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4831 | 2023-01-04 | 2137 | 20230105 | 1845 | 1918953 | 1268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 22824 | 38.7073 | -122.6091 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007189 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | Yes | No | 1797469 | 0 | EPSS Ckt | N | 2023
24108 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4831 | 2023-01-06 | 854 | 20230106 | 1850 | 1924501 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 10728 | 38.7073 | -122.6091 | No | Clear;32-90F | Pole-Wood | Burned/flashed | 23-0008163 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798249 | 0 | EPSS Ckt | N | 2023
24182 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 1015 | 2023-01-07 | 2340 | 20230108 | 750 | 1930981 | 490 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 7840 | 38.7249 | -122.6196 | Yes | Clear;32-90F |  |  | 23-0009854 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799707 | 0 | EPSS Ckt | N | 2023
24183 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4823 | 2023-01-07 | 2340 | 20230108 | 730 | 1931351 | 470 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 5170 | 38.7227 | -122.6196 | Yes | Clear;32-90F |  |  | 23-0009857 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1799710 | 0 | EPSS Ckt | N | 2023
24184 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | FUSE | 724805 | 2023-01-07 | 2341 | 20230108 | 827 | 1929471 | 526 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 10520 | 38.9891 | -122.5383 | Yes | Clear;32-90 F |  |  | 23-0009936 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799786 | 0 | EPSS Ckt | N | 2023
24203 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 1671 | 2023-01-08 | 903 | 20230108 | 1705 | 1932848 | 482 | Distribution Circuit | Environmental/External | Lightning | 1 | 482 | 38.7272 | -122.6192 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0010019 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1799864 | 0 | EPSS Ckt | N | 2023
24248 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 238925 | 2023-01-09 | 58 | 20230109 | 1112 | 1935139 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13508 | 38.8481 | -122.7563 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011086 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1800901 | 0 | EPSS Ckt | N | 2023
24269 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 1113 | 2023-01-09 | 1143 | 20230109 | 1704 | 1937926 | 321 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 11235 | 39.0442 | -122.9544 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011463 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1801221 | 0 | EPSS Ckt | N | 2023
24273 | HUMBOLDT | WILLOW CREEK | HOOPA-1101 | 192401101 | FUSE | 177643 | 2023-01-09 | 1240 | 20230112 | 1304 | 1938504 | 4344 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 86880 | 41.3297 | -123.8569 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0011331 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1801106 | 0 | EPSS Ckt | N | 2023
24352 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | TRANSFORMER | 216895046930 | 2023-01-11 | 1335 | 20230112 | 1658 | 1948135 | 1643 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3286 | 38.9525 | -123.0931 | No | Heavy Rain-Strong Winds-Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0013787 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1803183 | 0 | EPSS Ckt | N | 2023
24388 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2023-01-12 | 1131 | 20230112 | 1611 | 1949972 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 15680 | 38.8967 | -122.5542 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 23-0014442 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1803730 | 0 | EPSS Ckt | N | 2023 | N/A
24391 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | FUSE | 499 | 2023-01-12 | 1159 | 20230112 | 1658 | 1950031 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 11063 | 38.9576 | -123.1012 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0014479 | OH | Sus | 0 | NORTH COAST | JAN | Force Out | 0 | No | No | No | 1803755 | 0 | EPSS Ckt | N | 2023
24565 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 951123 | 2023-01-30 | 1029 | 20230131 | 207 | 1971908 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12194 | 38.8184 | -122.7014 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0022976 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1809192 | 0 | EPSS Ckt | N | 2023
24571 | HUMBOLDT | UKIAH | KONOCTI-1102 | 43311102 | TRANSFORMER | 218131346802 | 2023-01-31 | 1248 | 20230131 | 2150 | 1972919 | 542 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1378 | 38.9498 | -122.6582 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0023518 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1809502 | 0 | EPSS Ckt | N | 2023
24580 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 76103 | 2023-02-02 | 1044 | 20230202 | 1400 | 1974844 | 196 | Distribution Circuit | Animal | Squirrel | 2 | 392 | 38.7042 | -122.6056 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0024475 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1810063 | 0 | EPSS Ckt | N | 2023
24663 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | SWITCH | 1159 | 2023-02-09 | 1442 | 20230209 | 1752 | 1981127 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 214 | 40660 | 39.1561 | -122.9953 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0027213 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | No | 1811963 | 0 | EPSS Ckt | N | 2023
24698 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 1105 | 2023-02-13 | 1539 | 20230214 | 46 | 1983932 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6564 | 39.1669 | -122.9795 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0028313 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1812879 | 0 | EPSS Ckt | N | 2023
24709 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | TRANSFORMER | 218271551005 | 2023-02-14 | 924 | 20230214 | 1529 | 1984592 | 365 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1460 | 39.066 | -122.6087 | No | Clear;32-90 F | Transformer | Deteriorated | 23-0021231 | OH | Sus | 35306044 | NORTH COAST | FEB | None | 0 | No | No | No | 1813108 | 0 | EPSS Ckt | N | 2023
24784 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 1039 | 2023-02-21 | 1745 | 20230222 | 1159 | 1994955 | 1094 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6564 | 38.7363 | -122.6361 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0031853 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1815451 | 0 | EPSS Ckt | N | 2023
24944 | HUMBOLDT | UKIAH | COVELO-1101 | 43061101 | RECLOSER | 112804 | 2023-02-23 | 1912 | 20230303 | 1819 | 2000312 | 8551 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 799144 | 39.7129 | -123.2793 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033396 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | Yes | 1816434 | 0 | EPSS Ckt | N | 2023 | B- C 51T
24946 | HUMBOLDT | UKIAH | COVELO-1101 | 43061101 | FUSE | 2477 | 2023-02-23 | 1912 | 20230301 | 1743 | 2010223 | 8551 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 68408 | 39.7259 | -123.3245 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0035796 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818616 | 0 | EPSS Ckt | N | 2023
24965 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2337 | 2023-02-23 | 1951 | 20230302 | 901 | 2010203 | 9430 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 94300 | 39.2013 | -122.902 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035784 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | No | 1818610 | 0 | EPSS Ckt | N | 2023
24968 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 3773 | 2023-02-23 | 1951 | 20230228 | 1250 | 2012953 | 6779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 155917 | 39.1938 | -122.9753 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036611 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | No | 1819185 | 0 | EPSS Ckt | N | 2023
24973 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | OCB | 1101/2 | 2023-02-23 | 1954 | 20230228 | 1925 | 2000404 | 7171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 735 | 3699170 | 39.146 | -122.9171 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033411 | OH | Sus | 0 | NORTH COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1816444 | 0 | EPSS Ckt | N | 2023 | ABC
24990 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | JUMPER | JUMPERS LD SIDE OF CGC# 217262350314 | 2023-02-23 | 2034 | 20230302 | 1320 | 2009828 | 9646 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19292 | 39.044 | -122.9657 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035646 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1818489 | 0 | EPSS Ckt | N | 2023
25023 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 655 | 2023-02-23 | 2147 | 20230228 | 1753 | 2008998 | 6966 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 48762 | 38.9647 | -122.8981 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035397 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818239 | 1 | EPSS Ckt | N | 2023
25025 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 65363 | 2023-02-23 | 2147 | 20230228 | 1700 | 2009006 | 6913 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 20739 | 38.9489 | -122.8906 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0035403 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818244 | 0 | EPSS Ckt | N | 2023
25026 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 1977 | 2023-02-23 | 2147 | 20230301 | 1108 | 2010714 | 8001 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 88011 | 38.9628 | -122.9071 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035918 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818732 | 1 | EPSS Ckt | N | 2023
25029 | HUMBOLDT | UKIAH | KONOCTI-1102 | 43311102 | FUSE | 9001 | 2023-02-23 | 2208 | 20230228 | 1748 | 2009091 | 6940 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20820 | 38.9155 | -122.865 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035427 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818274 | 0 | EPSS Ckt | N | 2023
25034 | HUMBOLDT | UKIAH | MIDDLETOWN-1103 | 43141103 | FUSE | 5495 | 2023-02-23 | 2249 | 20230227 | 1100 | 2005903 | 5051 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15153 | 38.7348 | -122.5618 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034278 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1817167 | 0 | EPSS Ckt | N | 2023
25038 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | JUMPER | OJ'S 1 LOAD SIDE OF CGC# 217175153631 | 2023-02-23 | 2334 | 20230301 | 1410 | 2016397 | 8076 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 16152 | 39.1344 | -122.997 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0037651 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1819987 | 0 | EPSS Ckt | N | 2023
25047 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | FUSE | 4343 | 2023-02-24 | 25 | 20230226 | 1914 | 2008675 | 4009 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 501125 | 39.0708 | -122.6039 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035282 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818120 | 0 | EPSS Ckt | N | 2023
25057 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2023-02-24 | 100 | 20230226 | 848 | 2006389 | 3348 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 435 | 1118433 | 39.0581 | -122.693 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0034395 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1817279 | 0 | EPSS Ckt | N | 2023 | N/A
25059 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | FUSE | 4347 | 2023-02-24 | 100 | 20230227 | 1526 | 2009742 | 5186 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 62232 | 39.0926 | -122.6795 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035613 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1818462 | 0 | EPSS Ckt | N | 2023
25062 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | TRANSFORMER | 218478044615 | 2023-02-24 | 110 | 20230301 | 1505 | 2011791 | 8035 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8035 | 38.89 | -122.5365 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0036247 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818961 | 0 | EPSS Ckt | N | 2023
25083 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 1167 | 2023-02-24 | 207 | 20230228 | 1641 | 2009000 | 6634 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 165850 | 38.954 | -122.8964 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035398 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818240 | 1 | EPSS Ckt | N | 2023
25084 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 4231 | 2023-02-24 | 207 | 20230301 | 1411 | 2009848 | 7924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 166404 | 39.0078 | -122.8088 | Yes | Clear;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 23-0035652 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1818495 | 0 | EPSS Ckt | N | 2023
25090 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 42947 | 2023-02-24 | 241 | 20230301 | 1715 | 2015694 | 8074 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 8074 | 38.6886 | -122.5951 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0037429 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1819826 | 0 | EPSS Ckt | N | 2023
25090 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 42947 | 2023-02-24 | 241 | 20230301 | 1715 | 2015694 | 8074 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 8074 | 38.6886 | -122.5951 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0037429 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1819826 | 0 | EPSS Ckt | N | 2023
25090 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 42947 | 2023-02-24 | 241 | 20230301 | 1715 | 2015694 | 8074 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 8074 | 38.6886 | -122.5951 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0037429 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1819826 | 0 | EPSS Ckt | N | 2023
25100 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2023-02-24 | 310 | 20230228 | 1703 | 2002144 | 6548 | Distribution Circuit | Environmental/External | Ice or snow | 1453 | 3627095 | 38.695 | -122.5975 | Yes | Overcast;32-90 F | Other | On Ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816635 | 0 | EPSS Ckt | N | 2023 | B & 51T
25100 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2023-02-24 | 310 | 20230228 | 1703 | 2002144 | 6548 | Distribution Circuit | Environmental/External | Ice or snow | 1453 | 3627095 | 38.695 | -122.5975 | Yes | Overcast;32-90 F | Other | On Ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816635 | 0 | EPSS Ckt | N | 2023 | B & 51T
25100 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2023-02-24 | 310 | 20230228 | 1703 | 2002144 | 6548 | Distribution Circuit | Environmental/External | Ice or snow | 1453 | 3627095 | 38.695 | -122.5975 | Yes | Overcast;32-90 F | Other | On Ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1816635 | 0 | EPSS Ckt | N | 2023 | B & 51T
25101 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 1425 | 2023-02-24 | 310 | 20230225 | 1720 | 2006408 | 2290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 84730 | 38.7571 | -122.6149 | Yes | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0034432 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1817285 | 0 | EPSS Ckt | N | 2023
25107 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 3001 | 2023-02-24 | 347 | 20230228 | 1728 | 2011742 | 6581 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 52648 | 38.8654 | -122.6241 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036234 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1818953 | 0 | EPSS Ckt | N | 2023
25108 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 4611 | 2023-02-24 | 347 | 20230228 | 1722 | 2011913 | 6575 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 223550 | 38.8589 | -122.628 | Yes | Clear;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0033605 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1818980 | 0 | EPSS Ckt | N | 2023
25111 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2023-02-24 | 352 | 20230227 | 1029 | 2011637 | 4717 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 55 | 259435 | 38.8967 | -122.5542 | Yes | Clear;32-90 F |  |  | 23-0033617 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1818934 | 0 | EPSS Ckt | N | 2023 | N/A
25113 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | JUMPERS @ MTR# 1010705833 | 2023-02-24 | 353 | 20230226 | 1607 | 2008463 | 3614 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3614 | 38.787 | -122.6884 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | No | 1818079 | 0 | EPSS Ckt | N | 2023
25115 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 657 | 2023-02-24 | 414 | 20230228 | 1643 | 2013220 | 6509 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 58581 | 38.8617 | -122.6286 | Yes | Clear;32-90F |  |  | 23-0036671 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1819235 | 0 | EPSS Ckt | N | 2023
25124 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | LINE AND BUCK TWD CGC# 218206039220 | 2023-02-24 | 652 | 20230228 | 1230 | 2007904 | 6098 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6098 | 38.741 | -122.6302 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1817939 | 0 | EPSS Ckt | N | 2023
25194 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 78083 | 2023-02-25 | 1006 | 20230227 | 1701 | 2008163 | 3295 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 19770 | 38.7171 | -122.6192 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035853 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1818675 | 0 | EPSS Ckt | N | 2023
25195 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 1039 | 2023-02-25 | 1009 | 20230227 | 1501 | 2008471 | 3172 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19032 | 38.7363 | -122.6361 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035958 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1818768 | 0 | EPSS Ckt | N | 2023
25200 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 7835 | 2023-02-25 | 1248 | 20230228 | 1517 | 2012763 | 4469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 40221 | 38.6869 | -122.6602 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033599 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1819153 | 0 | EPSS Ckt | N | 2023
25242 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | TRANSFORMER | 216664848599 | 2023-02-26 | 824 | 20230226 | 1116 | 2009778 | 172 | Transformer only | Animal | Squirrel | 1 | 172 | 38.9947 | -123.1761 | Yes | Clear;32-90F | Fuse | Failed/Faulted | 23-0035677 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1818521 | 0 | EPSS Ckt | N | 2023
25308 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | JUMPER | OJ'S @ CGC 218504541665 | 2023-02-27 | 1427 | 20230228 | 1034 | 2012884 | 1207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2414 | 38.8095 | -122.5256 | Yes | Clear;32-90F | Jumper | Burned Open | 23-0036591 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | No | No | 1819167 | 0 | EPSS Ckt | N | 2023
25362 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | OJ'S SS OF CGC 217907843844 | 2023-02-28 | 930 | 20230301 | 1656 | 2014656 | 1886 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3772 | 38.8689 | -122.7359 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037482 | OH | Sus | 0 | NORTH COAST | FEB | Open Circuit | 0 | No | Yes | Yes | 1819856 | 0 | EPSS Ckt | N | 2023
25363 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 2023-02-28 | 935 | 20230228 | 1535 | 2014680 | 360 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 11520 | 39.1923 | -122.9711 | Yes | Clear;32-90 F |  |  | 23-0037535 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1819890 | 0 | EPSS Ckt | N | 2023
25369 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 7895 | 2023-02-28 | 1102 | 20230228 | 1718 | 2014964 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 752 | 38.8772 | -122.6178 | Yes | Clear;32-90 F | Crossarm- Wood | Broken | 23-0037253 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1819695 | 0 | EPSS Ckt | N | 2023
25378 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4823 | 2023-02-28 | 1243 | 20230228 | 1610 | 2015585 | 207 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2277 | 38.7227 | -122.6196 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0037560 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1819908 | 0 | EPSS Ckt | N | 2023
25383 | HUMBOLDT | UKIAH | POTTER VALLEY P H-1105 | 42281105 | JUMPER | OJ 3 SPANS SS CGC 217067055560 | 2023-02-28 | 1509 | 20230303 | 1322 | 2015977 | 4213 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8426 | 39.1878 | -123.0367 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0037530 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1819887 | 0 | EPSS Ckt | N | 2023
25416 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218022541905 | 2023-03-02 | 1144 | 20230302 | 1749 | 2019740 | 365 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 4 | 1460 | 38.8158 | -122.6951 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0038810 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1820871 | 0 | EPSS Ckt | N | 2023
25416 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218022541905 | 2023-03-02 | 1144 | 20230302 | 1749 | 2019740 | 365 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 4 | 1460 | 38.8158 | -122.6951 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0038810 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1820871 | 0 | EPSS Ckt | N | 2023
25451 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2331 | 2023-03-04 | 721 | 20230304 | 845 | 2022111 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1008 | 39.1932 | -122.8986 | No | Clear;Below 32 F |  |  | 23-0039891 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1821654 | 0 | EPSS Ckt | N | 2023
25491 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | OJ @ FLYERS 5 SPANS SS CGC# 217839442605 | 2023-03-05 | 834 | 20230307 | 1327 | 2023827 | 3173 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9519 | 38.838 | -122.7634 | No | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040378 | OH | Sus | 0 | NORTH COAST | MAR | Open Circuit | 0 | No | Yes | No | 1822104 | 0 | EPSS Ckt | N | 2023
25522 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 9873 | 2023-03-06 | 1415 | 20230306 | 1440 | 2024800 | 25 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 75 | 38.8692 | -122.7353 | No | Clear;32-90 F |  |  | 23-0040817 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1822407 | 0 | EPSS Ckt | N | 2023
25570 | HUMBOLDT | UKIAH | LAYTONVILLE-1102 | 42681102 | FUSE | 2477 | 2023-03-09 | 907 | 20230309 | 1320 | 2027277 | 253 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2024 | 39.7259 | -123.3245 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0042019 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1823080 | 0 | EPSS Ckt | N | 2023
25609 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4539 | 2023-03-10 | 813 | 20230310 | 940 | 2030405 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 348 | 38.7378 | -122.6428 | No | Clear;32-90F |  |  | 23-0042881 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1823637 | 0 | EPSS Ckt | N | 2023
25692 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | FUSE | 2909 | 2023-03-17 | 1308 | 20230317 | 1718 | 2050051 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 28750 | 38.9705 | -123.1453 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0047609 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1826912 | 0 | EPSS Ckt | N | 2023
25704 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 872796 | 2023-03-20 | 1438 | 20230321 | 330 | 2053196 | 772 | Distribution Circuit | Equipment Failure/Involved | Overhead | 140 | 90728 | 38.7242 | -122.6189 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0048946 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1827941 | 0 | EPSS Ckt | N | 2023 | NONE
25744 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 7769 | 2023-03-27 | 1544 | 20230327 | 1716 | 2069036 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2208 | 38.8708 | -122.7489 | No | Clear;32-90 F | Fuse | Broken | 23-0053125 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1830885 | 0 | EPSS Ckt | N | 2023
25829 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218211538885 | 2023-03-29 | 2223 | 20230329 | 2301 | 2073736 | 38 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 76 | 38.7328 | -122.6275 | No | Overcast-Drizzle;32-90 F | Fuse | Failed/Faulted | 23-0054705 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1831795 | 0 | EPSS Ckt | N | 2023
25924 | HUMBOLDT | UKIAH | REDBUD-1102 | 43191102 | SWITCH | 6373 | 2023-04-20 | 1015 | 20230420 | 1023 | 2092999 | 8 | Distribution Circuit | Animal | Other | 340 | 2720 | 38.9982 | -122.6651 | No | Clear;32-90 F | Recloser | Normal | 23-0062893 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1837228 | 0 | EPSS Ckt | N | 2023
25927 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | SWITCH | 7091 | 2023-04-20 | 1344 | 20230420 | 1417 | 2093223 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 1551 | 38.9957 | -123.181 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0063040 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1837270 | 0 | EPSS Ckt | N | 2023
25955 | HUMBOLDT | UKIAH | REDBUD-1102 | 43191102 | SWITCH | 6373 | 2023-04-27 | 1004 | 20230427 | 1015 | 2098328 | 11 | Distribution Circuit | Animal | Other | 340 | 3740 | 38.9982 | -122.6651 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0065420 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1839003 | 0 | EPSS Ckt | N | 2023
25982 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2023-05-04 | 1621 | 20230505 | 125 | 2104830 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 572 | 75598 | 39.0581 | -122.693 | No | Overcast;32-90 F | Pole-Wood | Deteriorated | 23-0068428 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1840915 | 0 | EPSS Ckt | N | 2023 | NONE
26039 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2337 | 2023-05-17 | 1530 | 20230517 | 1607 | 2115099 | 37 | Distribution Circuit | Vegetation | Tree - grew into line | 10 | 370 | 39.2013 | -122.902 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0072814 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1843995 | 0 | EPSS Ckt | N | 2023
26042 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 217785543760 | 2023-05-17 | 2254 | 20230518 | 856 | 2115479 | 602 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 602 | 38.868 | -122.7761 | No | Clear;32-90 F | Transformer | Broken | 23-0072937 | OH | Sus | 0 | NORTH COAST | MAY | Line to Ground | 0 | No | No | No | 1844065 | 0 | EPSS Ckt | N | 2023
26050 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 3773 | 2023-05-22 | 643 | 20230522 | 810 | 2118281 | 87 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 1335 | 39.1938 | -122.9753 | No | Clear;32-90 F |  |  | 23-0074108 | OH | Sus | 0 | NORTH COAST | MAY | Line to Ground | 0 | No | No | No | 1844958 | 1 | EPSS Ckt | N | 2023
26102 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | TSB 2 S/OF 4313 | 2023-06-01 | 1149 | 20230601 | 1653 | 2126709 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 29792 | 38.8773 | -122.7323 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0077633 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1847308 | 0 | EPSS Ckt | N | 2023
26116 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | JUMPER | OJ'S AT CGC 217855943085 | 2023-06-06 | 1420 | 20230606 | 1556 | 2130728 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 288 | 38.8465 | -122.7539 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0079436 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1848423 | 0 | EPSS Ckt | N | 2023
26130 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | RECLOSER | 329774 | 2023-06-09 | 1644 | 20230609 | 1828 | 2133835 | 104 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 4264 | 39.1691 | -123.0122 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0081002 | OH | Sus | 45838232 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1849451 | 0 | EPSS Ckt | N | 2023 | NONE
26138 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2023-06-12 | 2204 | 20230613 | 311 | 2135701 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 20262 | 39.0581 | -122.693 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0081697 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1850100 | 0 | EPSS Ckt | N | 2023 | NONE
26160 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 5881 | 2023-06-19 | 1001 | 20230619 | 1419 | 2140399 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1806 | 38.8988 | -122.5562 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0083619 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1851612 | 0 | EPSS Ckt | N | 2023
26170 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 1977 | 2023-06-22 | 1138 | 20230622 | 1356 | 2143179 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1518 | 38.9628 | -122.9071 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 23-0084678 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1852451 | 0 | EPSS Ckt | N | 2023
26175 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 571926 | 2023-06-23 | 1337 | 20230623 | 1414 | 2144219 | 37 | Distribution Circuit | Company Initiated | Personnel- company | 37 | 1369 | 38.7342 | -122.6319 | No | Clear;32-90 F | Fuse | Normal | 23-0085131 | OH | Sus | 0 | NORTH COAST | JUN | Line to Line | 0 | No | No | No | 1852736 | 0 | EPSS Ckt | Y | 2023 | A-C
26177 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2023-06-23 | 1758 | 20230623 | 1824 | 2144361 | 26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 573 | 14898 | 39.0581 | -122.693 | No | Clear;32-90 F | Insulator | Broken | 23-0085225 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1852766 | 0 | EPSS Ckt | N | 2023 | NONE
26193 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | TRANSFORMER | 216858547290 | 2023-06-27 | 755 | 20230627 | 913 | 2146668 | 78 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 78 | 38.9625 | -123.1056 | No | Partly Cloudy;32-90 F |  |  | 23-0085996 | OH | Sus | 0 | NORTH COAST | JUN | Line to Ground | 0 | No | No | No | 1853456 | 0 | EPSS Ckt | N | 2023
26207 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | TRANSFORMER | 217435655697 | 2023-06-30 | 1252 | 20230630 | 2234 | 2149978 | 582 | Transformer only | Vegetation | Tree - fell into line | 2 | 1164 | 39.1923 | -122.906 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0087739 | OH | Sus | 31653919 | NORTH COAST | JUN | Line to Ground | 0 | No | Yes | No | 1854421 | 0 | EPSS Ckt | N | 2023
26215 | HUMBOLDT | UKIAH | MIDDLETOWN-1103 | 43141103 | FUSE | 1441 | 2023-07-02 | 711 | 20230702 | 1427 | 2151868 | 436 | Distribution Circuit | Animal | Bird found | 5 | 2180 | 38.743 | -122.5737 | No | Clear;32-90 F | Fuse | Burned Open | 23-0088172 | OH | Sus | 0 | NORTH COAST | JUL | Line to Line | 0 | No | No | No | 1854801 | 0 | EPSS Ckt | N | 2023
26275 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 571926 | 2023-07-14 | 1221 | 20230714 | 1441 | 2162597 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2240 | 38.7342 | -122.6319 | No | Clear;32-90 F |  |  | 23-0092363 | OH | Sus | 0 | NORTH COAST | JUL | Line to Line | 0 | Yes | No | No | 1857515 | 0 | EPSS Ckt | Y | 2023 | A AND C
26280 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | FUSE | 6017 | 2023-07-15 | 1140 | 20230715 | 1645 | 2163425 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2135 | 38.8872 | -122.479 | No | Clear;Above 90 | Connector or Splice (OH) | Broken | 23-0092605 | OH | Sus | 31655607 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1857676 | 0 | EPSS Ckt | N | 2023
26299 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 829164 | 2023-07-18 | 938 | 20230718 | 1447 | 2166493 | 309 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2106 | 510214 | 38.7537 | -122.6111 | No | Clear;32-90 F |  |  | 23-0093588 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1858468 | 0 | EPSS Ckt | Y | 2023
26308 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2023-07-19 | 1455 | 20230719 | 1739 | 2168308 | 164 | Distribution Circuit | Animal | Bird found | 564 | 89897 | 39.0581 | -122.693 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0094308 | OH | Sus | 0 | NORTH COAST | JUL | Line to Line | 0 | No | No | No | 1858895 | 0 | EPSS Ckt | Y | 2023 | B-C-INST
26383 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 2023-08-04 | 934 | 20230804 | 1348 | 2182384 | 254 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 5421 | 39.1923 | -122.9711 | No | Clear;32-90 F |  |  | 23-0100687 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1863144 | 1 | EPSS Ckt | N | 2023
26426 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | FUSE | 1565 | 2023-08-13 | 1715 | 20230814 | 147 | 2189713 | 512 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 24 | 12288 | 38.9977 | -122.5558 | No | Clear;Above 90 | Pole-Wood | Burned/flashed | 23-0103771 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1865356 | 0 | EPSS Ckt | N | 2023
26450 | HUMBOLDT | UKIAH | COVELO-1101 | 43061101 | TRANSFORMER | 216861878811 | 2023-08-16 | 2041 | 20230817 | 755 | 2193330 | 674 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 674 | 39.8254 | -123.1181 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0105363 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1866403 | 0 | EPSS Ckt | N | 2023
26458 | HUMBOLDT | UKIAH | COVELO-1101 | 43061101 | TRANSFORMER | 216813479319 | 2023-08-18 | 1945 | 20230819 | 959 | 2195321 | 854 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 854 | 39.8277 | -123.119 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0106309 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1866953 | 0 | EPSS Ckt | N | 2023
26475 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 829164 | 2023-08-21 | 952 | 20230821 | 1711 | 2197882 | 401 | Distribution Circuit | Company Initiated | Personnel- company | 2086 | 369856 | 38.7537 | -122.6111 | No | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Normal | 23-0106953 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1867606 | 0 | EPSS Ckt | Y | 2023
26476 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 767107 | 2023-08-21 | 952 | 20230821 | 1418 | 2197888 | 266 | Distribution Circuit | Company Initiated | Improper Construction | 10 | 2660 | 38.725 | -122.6183 | No | Partly Cloudy-Rain;32-90 F | Conductor- Underground | Normal | 23-0101159 | UG | Sus | 35227030 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1867607 | 0 | EPSS Ckt | N | 2023
26499 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | SWITCH | 323962 | 2023-08-25 | 2308 | 20230826 | 910 | 2202591 | 602 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 505 | 77608 | 39.0662 | -122.611 | No | Clear;32-90 F |  |  | 23-0109334 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1869139 | 0 | EPSS Ckt | Y | 2023
26510 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | RECLOSER | 329774 | 2023-08-28 | 1121 | 20230828 | 1159 | 2204071 | 38 | Distribution Circuit | Company Initiated | Personnel- company | 30 | 1140 | 39.1691 | -123.0122 | No | Clear;32-90 F | Recloser | Normal | 23-0109780 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1869594 | 0 | EPSS Ckt | Y | 2023 | A C
26515 | HUMBOLDT | UKIAH | LUCERNE-1103 | 43351103 | RECLOSER | 27932 | 2023-08-29 | 807 | 20230829 | 940 | 2204664 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1488 | 39.1114 | -122.9074 | No | Clear;32-90 F |  |  | 23-0110063 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1869761 | 0 | EPSS Ckt | Y | 2023 | B INST
26520 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | TRANSFORMER | 217430446486 | 2023-08-29 | 1404 | 20230829 | 1432 | 2205135 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 38.94 | -122.9051 | No | Clear;32-90 F | Anchor or Guy | Broken | 23-0110330 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1869962 | 0 | EPSS Ckt | N | 2023
26522 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2023-08-30 | 554 | 20230830 | 1719 | 2205575 | 685 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 56 | 38360 | 38.8967 | -122.5542 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110056 | OH | Sus | 8206198 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1870062 | 0 | EPSS Ckt | N | 2023 | NONE
26524 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 98053 | 2023-08-30 | 1056 | 20230830 | 1118 | 2205938 | 22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 22 | 38.9665 | -122.8978 | No | Clear;32-90 F |  |  | 23-0110718 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1870214 | 0 | EPSS Ckt | N | 2023
26550 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 1113 | 2023-09-05 | 2041 | 20230906 | 827 | 2210429 | 706 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 35 | 24710 | 39.0442 | -122.9544 | No | Clear;32-90 F |  |  | 23-0112855 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1871422 | 0 | EPSS Ckt | N | 2023
26559 | HUMBOLDT | UKIAH | LUCERNE-1103 | 43351103 | RECLOSER | 27932 | 2023-09-08 | 829 | 20230908 | 957 | 2212490 | 88 | Distribution Circuit | 3rd Party | Customer Equipment | 16 | 1408 | 39.1114 | -122.9074 | No | Partly Cloudy;32-90 F | Other | Broken | 23-0114012 | OH | Sus | 0 | NORTH COAST | SEP | Line to Ground | 0 | No | No | No | 1872074 | 0 | EPSS Ckt | Y | 2023 | B & INST
26564 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | TRANSFORMER | 217237255862 | 2023-09-09 | 1055 | 20230910 | 1151 | 2213634 | 1496 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2992 | 39.1957 | -122.9759 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114495 | OH | Sus | 0 | NORTH COAST | SEP | Line to Ground | 0 | No | No | No | 1872434 | 0 | EPSS Ckt | N | 2023
26577 | HUMBOLDT | UKIAH | LUCERNE-1103 | 43351103 | RECLOSER | 4200 | 2023-09-13 | 744 | 20230913 | 958 | 2217371 | 134 | Distribution Circuit | 3rd Party | Customer Equipment | 39 | 5203 | 39.1174 | -122.9022 | No | Clear;32-90 F | Customer Equipment | Normal | 23-0115890 | OH | Sus | 0 | NORTH COAST | SEP | Line to Ground | 0 | No | No | No | 1873541 | 0 | EPSS Ckt | Y | 2023 | 50I
26598 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2023-09-21 | 236 | 20230921 | 1403 | 2223784 | 687 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 37785 | 38.8967 | -122.5542 | No | Clear;32-90 F |  |  | 23-0118551 | OH | Sus | 0 | NORTH COAST | SEP | None | 0 | No | No | No | 1875693 | 0 | EPSS Ckt | N | 2023 | NONE
26636 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | OCB | 1101/2 | 2023-09-26 | 1149 | 20230926 | 1354 | 2227621 | 125 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 130250 | 39.146 | -122.9171 | No | Partly Cloudy;32-90 F |  |  | 23-0120943 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1876962 | 0 | EPSS Ckt | Y | 2023 | A/C INST 50
26779 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | TRANSFORMER | 218342350048 | 2023-11-04 | 915 | 20231104 | 1335 | 2259863 | 260 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 520 | 39.0382 | -122.5838 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0135880 | OH | Sus | 0 | NORTH COAST | NOV | Line to Ground | 0 | No | No | No | 1887765 | 0 | EPSS Ckt | N | 2023
26782 | HUMBOLDT | UKIAH | HIGHLANDS 1101 | 43361101 | JUMPER | 1 SPAN SS OF CGC 218245444040 | 2023-11-04 | 1254 | 20231104 | 1542 | 2259997 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 168 | 38.8737 | -122.6174 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0135900 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1887782 | 0 | EPSS Ckt | N | 2023
26806 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | RECLOSER | 628 | 2023-11-08 | 1643 | 20231108 | 1956 | 2264515 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 6562 | 38.9822 | -122.6031 | No | Clear;32-90 F |  |  | 23-0137249 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1889001 | 0 | EPSS Ckt | N | 2023 | NONE
26847 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 9705 | 2023-11-19 | 653 | 20231119 | 1015 | 2273435 | 202 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 808 | 39.199 | -122.978 | No | Clear;32-90 F |  |  | 23-0141080 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | No | No | 1891754 | 0 | EPSS Ckt | N | 2023
26899 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | FUSE | 499 | 2023-12-04 | 1329 | 20231204 | 2200 | 2283638 | 511 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 39 | 7837 | 38.9576 | -123.1012 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0145353 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | Yes | No | 1895045 | 1 | EPSS Ckt | N | 2023
26902 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 9705 | 2023-12-05 | 658 | 20231205 | 937 | 2283975 | 159 | Distribution Circuit | Animal | Bird found | 4 | 636 | 39.199 | -122.978 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0145443 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | No | No | 1895115 | 0 | EPSS Ckt | N | 2023
26985 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 2023-12-21 | 1624 | 20231221 | 1907 | 2297919 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3479 | 39.1923 | -122.9711 | No | Clear;32-90 F |  |  | 23-0148522 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 1899517 | 1 | EPSS Ckt | N | 2023
26991 | HUMBOLDT | UKIAH | HIGHLANDS-1101 | 43361101 | TRANSFORMER | 218316443195 | 2023-12-24 | 710 | 20231224 | 1024 | 2299060 | 194 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 776 | 38.8513 | -122.594 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0148733 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 1899801 | 0 | EPSS Ckt | N | 2023
27013 | HUMBOLDT | UKIAH | HIGHLANDS-1101 | 43361101 | FUSE | 1313 | 2023-12-28 | 1802 | 20231229 | 907 | 2301567 | 905 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 2715 | 38.8853 | -122.4653 | No | Clear;32-90 F |  |  | 23-0149141 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | No | No | 1900398 | 0 | EPSS Ckt | N | 2023
27124 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | RECLOSER | 871312 | 2024-01-13 | 2339 | 20240114 | 1607 | 2315136 | 988 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 25191 | 39.1046 | -122.9739 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0010632 | OH | Sus | 0 | NORTH COAST | JAN | Multi-Fault | 0 | No | Yes | No | 1903924 | 0 | EPSS Ckt | N | 2024 | BC GRD
27278 | HUMBOLDT | WILLOW CREEK | HOOPA-1101 | 192401101 | FUSE | 978307 | 2024-02-02 | 1906 | 20240202 | 2148 | 2333249 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2106 | 41.3493 | -123.8694 | No | Clear;32-90 F |  |  | 24-0018882 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1908744 | 0 | EPSS Ckt | N | 2024
27299 | HUMBOLDT | UKIAH | KONOCTI-1102 | 43311102 | FUSE | 2341 | 2024-02-04 | 450 | 20240208 | 1000 | 2368473 | 6070 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 163890 | 38.8761 | -122.7305 | Yes | Clear;32-90 F |  |  | 24-0024639 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1913700 | 0 | EPSS Ckt | N | 2024
27312 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 7769 | 2024-02-04 | 532 | 20240209 | 1444 | 2370641 | 7752 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 186048 | 38.8708 | -122.7489 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 24-0026495 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1915233 | 0 | EPSS Ckt | N | 2024
27360 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 2024-02-04 | 1007 | 20240208 | 1739 | 2337099 | 6212 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 462418 | 38.8761 | -122.7755 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 24-0020710 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | No | No | 1913029 | 0 | EPSS Ckt | N | 2024 | NONE
27361 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | OTHER | HOT WIRE DOWN @ 6201 | 2024-02-04 | 1011 | 20240210 | 1139 | 2336962 | 8728 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 142773 | 38.8586 | -122.7472 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020547 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1910369 | 0 | EPSS Ckt | N | 2024
27410 | HUMBOLDT | UKIAH | KONOCTI-1102 | 43311102 | FUSE | 1697 | 2024-02-04 | 1610 | 20240207 | 1304 | 2345542 | 4134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 90993 | 38.9145 | -122.8574 | Yes | Clear;32-90 F |  |  | 24-0024285 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1913490 | 1 | EPSS Ckt | N | 2024
27412 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 492661 | 2024-02-04 | 1630 | 20240208 | 1627 | 2364226 | 5757 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34542 | 38.8654 | -122.7692 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 24-0023307 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1912791 | 0 | EPSS Ckt | N | 2024
27413 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 171414 | 2024-02-04 | 1630 | 20240208 | 1500 | 2365096 | 5670 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 130410 | 38.8481 | -122.7562 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020710 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1913008 | 0 | EPSS Ckt | N | 2024 | NONE
27427 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 3543 | 2024-02-04 | 1819 | 20240206 | 1755 | 2364212 | 2856 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 199920 | 38.8453 | -122.7515 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020710 | OH | Sus | 0 | NORTH COAST | FEB | None | 0 | No | Yes | No | 1912788 | 0 | EPSS Ckt | N | 2024
27460 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 571926 | 2024-02-04 | 1916 | 20240208 | 1410 | 2352379 | 5454 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 211209 | 38.7342 | -122.6319 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020848 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1910666 | 0 | EPSS Ckt | N | 2024 | AC
27466 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | RECLOSER | 768 | 2024-02-04 | 1944 | 20240205 | 1853 | 2353087 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 138900 | 38.9695 | -123.1026 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020920 | OH | Sus | 0 | NORTH COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1910739 | 0 | EPSS Ckt | N | 2024 | TIME AB GRD
27487 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 872796 | 2024-02-04 | 2149 | 20240206 | 1843 | 2355021 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 274788 | 38.7244 | -122.6188 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021178 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1911003 | 0 | EPSS Ckt | N | 2024 | AC
27531 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2337 | 2024-02-05 | 1325 | 20240208 | 756 | 2360424 | 3991 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 39910 | 39.2013 | -122.902 | No | Overcast-Fog-Snow;32-90 F | Insulator | Broken | 24-0022217 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1911885 | 0 | EPSS Ckt | N | 2024
27541 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | TRANSFORMER | 217453855690 | 2024-02-05 | 1631 | 20240207 | 1853 | 2362233 | 3022 | Transformer only | Vegetation | Tree - fell into line | 1 | 3022 | 39.1921 | -122.8997 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023203 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1912716 | 0 | EPSS Ckt | N | 2024
27545 | HUMBOLDT | UKIAH | COVELO-1101 | 43061101 | RECLOSER | 112804 | 2024-02-05 | 1713 | 20240209 | 1741 | 2361251 | 5788 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 345273 | 39.7129 | -123.2793 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022466 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1912105 | 0 | EPSS Ckt | N | 2024 | ABC
27546 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218032040383 | 2024-02-05 | 1724 | 20240210 | 1353 | 2361313 | 6989 | Transformer only | Vegetation | Tree - fell into line | 1 | 6989 | 38.7735 | -122.6916 | No | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023613 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913019 | 0 | EPSS Ckt | N | 2024
27592 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218036740424 | 2024-02-07 | 1435 | 20240210 | 1617 | 2367729 | 4422 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 26532 | 38.7747 | -122.6898 | No | Overcast-Drizzle;32-90 F | Other | Broken- wire on ground | 24-0024417 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913562 | 0 | EPSS Ckt | N | 2024
27694 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRANSFORMER | 218014041941 | 2024-02-19 | 1006 | 20240220 | 1127 | 2380893 | 1521 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 1521 | 38.8163 | -122.6984 | No | Strong Winds-Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 24-0030782 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1917985 | 0 | EPSS Ckt | N | 2024
27706 | HUMBOLDT | UKIAH | HIGHLANDS-1101 | 43361101 | FUSE | 657 | 2024-02-19 | 1213 | 20240219 | 1717 | 2381060 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2736 | 38.8617 | -122.6286 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030899 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | Yes | No | 1918071 | 0 | EPSS Ckt | N | 2024
27711 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 441113 | 2024-02-19 | 1304 | 20240220 | 1257 | 2381325 | 1433 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 42990 | 38.8196 | -122.6966 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0030911 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1918077 | 0 | EPSS Ckt | N | 2024
27814 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 2024-03-01 | 2044 | 20240302 | 1024 | 2393441 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 80360 | 38.8761 | -122.7755 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036767 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | Yes | No | 1921794 | 0 | EPSS Ckt | N | 2024 | A B
27925 | HUMBOLDT | UKIAH | CLEAR LAKE-1102 | 42141102 | TRANSFORMER | 217458547354 | 2024-03-06 | 1408 | 20240307 | 1516 | 2398712 | 1508 | Transformer only | Environmental/External | Lightning | 1 | 1508 | 38.9633 | -122.8953 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038933 | OH | Sus | 0 | NORTH COAST | MAR | Three Phase Fault | 0 | No | No | No | 1922990 | 0 | EPSS Ckt | N | 2024
27926 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | TRANSFORMER | 217458647308 | 2024-03-06 | 1411 | 20240307 | 1516 | 2398713 | 1505 | Transformer only | Environmental/External | Lightning | 1 | 1505 | 38.9622 | -122.8953 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038924 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1922982 | 0 | EPSS Ckt | N | 2024
27927 | HUMBOLDT | UKIAH | CLEAR LAKE-1102 | 42141102 | TRANSFORMER | 217466447223 | 2024-03-06 | 1414 | 20240307 | 1516 | 2398711 | 1502 | Transformer only | Environmental/External | Lightning | 1 | 1502 | 38.9598 | -122.8926 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0038927 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1922983 | 0 | EPSS Ckt | N | 2024
27933 | HUMBOLDT | UKIAH | CLEAR LAKE-1101 | 42141101 | FUSE | 81533 | 2024-03-07 | 1005 | 20240307 | 1516 | 2399232 | 311 | Distribution Circuit | Environmental/External | Lightning | 2 | 622 | 38.9622 | -122.898 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0039164 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1923230 | 0 | EPSS Ckt | N | 2024
27998 | HUMBOLDT | UKIAH | HIGHLANDS-1101 | 43361101 | FUSE | 657 | 2024-03-20 | 636 | 20240320 | 1005 | 2409866 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1881 | 38.8617 | -122.6286 | No | Clear;32-90 F |  |  | 24-0044522 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1926910 | 0 | EPSS Ckt | N | 2024
28011 | HUMBOLDT | UKIAH | HIGHLANDS-1101 | 43361101 | TRANSFORMER | 218516341343 | 2024-03-22 | 1617 | 20240323 | 1502 | 2412225 | 1365 | Transformer only | Animal | Other | 2 | 2730 | 38.8005 | -122.522 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0045928 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1927664 | 0 | EPSS Ckt | N | 2024
28114 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 2024-04-11 | 637 | 20240411 | 900 | 2428222 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4576 | 39.1923 | -122.9711 | No | Clear;32-90 F |  |  | 24-0053416 | OH | Sus | 0 | NORTH COAST | APR | Line to Line | 0 | No | No | No | 1932688 | 0 | EPSS Ckt | N | 2024
28119 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 4679 | 2024-04-13 | 804 | 20240413 | 1024 | 2430176 | 140 | Distribution Circuit | Animal | Bird found | 44 | 6163 | 38.7544 | -122.6135 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0054395 | OH | Sus | 0 | NORTH COAST | APR | Line to Ground | 0 | No | No | No | 1933298 | 1 | EPSS Ckt | N | 2024
28129 | HUMBOLDT | WILLOW CREEK | HOOPA-1101 | 192401101 | FUSE | 978307 | 2024-04-15 | 1659 | 20240415 | 1915 | 2432145 | 136 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1768 | 41.3493 | -123.8694 | No | Clear;32-90 F | Fuse | Burned Open | 24-0055175 | OH | Sus | 0 | NORTH COAST | APR | Line to Line | 0 | No | No | No | 1933880 | 0 | EPSS Ckt | N | 2024
28157 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | TRANSFORMER | 216673748675 | 2024-04-24 | 542 | 20240424 | 2208 | 2437828 | 986 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1718 | 38.9962 | -123.1723 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0058397 | OH | Sus | 0 | NORTH COAST | APR | Line to Ground | 0 | No | No | No | 1936096 | 0 | EPSS Ckt | N | 2024
28182 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | FUSE | 724805 | 2024-04-30 | 1235 | 20240430 | 1355 | 2442700 | 80 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 1440 | 38.9891 | -122.5383 | No | Clear;32-90 F |  |  | 24-0060473 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1937725 | 0 | EPSS Ckt | N | 2024
28219 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 3773 | 2024-05-07 | 559 | 20240507 | 755 | 2447558 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2668 | 39.1938 | -122.9753 | No | Clear;32-90 F |  |  | 24-0062907 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | No | No | No | 1939529 | 0 | EPSS Ckt | N | 2024
28231 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | FUSE | 4809 | 2024-05-09 | 154 | 20240509 | 435 | 2449339 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 644 | 39.0864 | -122.6791 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0063977 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | No | No | No | 1940200 | 0 | EPSS Ckt | N | 2024
28233 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | FUSE | 4809 | 2024-05-09 | 728 | 20240509 | 914 | 2449366 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 424 | 39.0864 | -122.6791 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0064010 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | No | No | No | 1940217 | 0 | EPSS Ckt | N | 2024
28238 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 2024-05-09 | 1645 | 20240509 | 1818 | 2450039 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 9114 | 38.8761 | -122.7755 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0064401 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1940461 | 0 | EPSS Ckt | N | 2024 | none
28321 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2024-05-29 | 529 | 20240529 | 738 | 2469461 | 129 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 680 | 81753 | 39.0584 | -122.6925 | No | Clear;32-90 F |  |  | 24-0070771 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | No | No | No | 1944760 | 0 | EPSS Ckt | Y | 2024 | B-C PH INST OC
28370 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 1113 | 2024-06-04 | 1311 | 20240604 | 1852 | 2475149 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 1192 | 66314 | 39.0442 | -122.9544 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0073110 | OH | Sus | 31696243 | NORTH COAST | JUN | Line to Ground | 0 | No | Yes | No | 1946488 | 0 | EPSS Ckt | N | 2024
28451 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | JUMPER | OJ'S AT CGC 217204752938 | 2024-06-19 | 1527 | 20240619 | 1854 | 2490172 | 207 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 828 | 39.1154 | -122.986 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0078509 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1950478 | 0 | EPSS Ckt | N | 2024
28460 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | JUMPER | OJS @ CGC 217204752938 | 2024-06-21 | 818 | 20240621 | 1215 | 2491335 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 948 | 39.1153 | -122.986 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0078936 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1950754 | 0 | EPSS Ckt | N | 2024
28471 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | TRANSFORMER | 218297851475 | 2024-06-22 | 1943 | 20240622 | 2319 | 2492735 | 216 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 648 | 39.0782 | -122.5989 | No | Clear;32-90 F |  |  | 24-0079495 | OH | Sus | 0 | NORTH COAST | JUN | None | 0 | No | No | No | 1951104 | 0 | EPSS Ckt | N | 2024
28507 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 463705 | 2024-07-02 | 114 | 20240702 | 1609 | 2501464 | 895 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 31 | 27745 | 38.7128 | -122.644 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082376 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953449 | 0 | EPSS Ckt | N | 2024 | N/A
28508 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 435929 | 2024-07-02 | 120 | 20240702 | 1546 | 2501484 | 866 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 90 | 77940 | 38.7747 | -122.6898 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082376 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953455 | 0 | EPSS Ckt | N | 2024
28509 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 829164 | 2024-07-02 | 121 | 20240702 | 147 | 2501468 | 26 | Distribution Circuit | Company Initiated | Personnel- company | 1968 | 51168 | 38.7537 | -122.6111 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082764 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1953452 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
28510 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 503107 | 2024-07-02 | 121 | 20240702 | 1545 | 2501486 | 864 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 10 | 8640 | 38.781 | -122.6862 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082376 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953456 | 0 | EPSS Ckt | N | 2024
28511 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 919321 | 2024-07-02 | 122 | 20240702 | 1541 | 2501487 | 859 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 859 | 38.7675 | -122.6627 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082376 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953457 | 0 | EPSS Ckt | N | 2024
28513 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2024-07-02 | 405 | 20240702 | 1334 | 2501508 | 569 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 31295 | 38.8967 | -122.5542 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082371 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953463 | 0 | EPSS Ckt | N | 2024 | N/A
28520 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 463705 | 2024-07-02 | 2346 | 20240703 | 1401 | 2503293 | 855 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 132 | 104553 | 38.7128 | -122.644 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083210 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953791 | 0 | EPSS Ckt | N | 2024 | NONE
28523 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2024-07-03 | 202 | 20240703 | 1410 | 2503410 | 728 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 40040 | 38.8967 | -122.5542 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083212 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1953827 | 0 | EPSS Ckt | N | 2024 | NONE
28547 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 583187 | 2024-07-06 | 1158 | 20240706 | 1545 | 2507554 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1816 | 38.7224 | -122.6174 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0084584 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1954518 | 0 | EPSS Ckt | N | 2024
28572 | HUMBOLDT | UKIAH | POTTER VALLEY P H-1105 | 42281105 | TRANSFORMER | 216962658853 | 2024-07-10 | 1601 | 20240710 | 2107 | 2512724 | 306 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 306 | 39.278 | -123.0741 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0086357 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1955669 | 0 | EPSS Ckt | N | 2024
28592 | HUMBOLDT | UKIAH | CLEAR LAKE-1102 | 42141102 | TRANSFORMER | 217464747481 | 2024-07-12 | 855 | 20240712 | 1046 | 2514866 | 111 | Transformer only | Animal | Other | 1 | 111 | 38.9666 | -122.893 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0087200 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1956259 | 0 | EPSS Ckt | N | 2024
28615 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | TRANSFORMER | 218297851475 | 2024-07-16 | 1533 | 20240716 | 2335 | 2518455 | 482 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1446 | 39.0782 | -122.5989 | No | Clear;32-90 F | Transformer | Leaking | 24-0088623 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1957256 | 0 | EPSS Ckt | N | 2024
28625 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | OTHER | HOT WIRE DOWN 1ST SPAN SS CGC 218246038510 | 2024-07-18 | 1704 | 20240719 | 153 | 2520459 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4040 | 38.7228 | -122.6161 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0089495 | OH | Sus | 46281614 | NORTH COAST | JUL | Open Circuit | 0 | No | Yes | Yes | 1957738 | 0 | EPSS Ckt | N | 2024
28644 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | FUSE | 724805 | 2024-07-20 | 1753 | 20240720 | 2011 | 2522008 | 138 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 2484 | 38.9891 | -122.5383 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0090077 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1958154 | 0 | EPSS Ckt | N | 2024
28682 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | RECLOSER | 871312 | 2024-07-25 | 707 | 20240725 | 2349 | 2526332 | 1002 | Distribution Circuit | Animal | Squirrel | 291 | 58712 | 39.1046 | -122.9739 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0091797 | OH | Sus | 0 | NORTH COAST | JUL | Line to Line | 0 | No | No | No | 1959336 | 0 | EPSS Ckt | Y | 2024 | A C
28690 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | FUSE | 2901 | 2024-07-26 | 1122 | 20240726 | 1142 | 2527517 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 16 | 320 | 38.9582 | -123.1152 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0092416 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1959776 | 0 | EPSS Ckt | N | 2024
28735 | HUMBOLDT | UKIAH | HOPLAND-1101 | 42251101 | FUSE | 499 | 2024-08-03 | 652 | 20240803 | 914 | 2533450 | 142 | Distribution Circuit | Animal | Other | 39 | 5538 | 38.9576 | -123.1012 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0095357 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1961699 | 0 | EPSS Ckt | N | 2024
28736 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 238925 | 2024-08-03 | 1629 | 20240803 | 2214 | 2533811 | 345 | Distribution Circuit | Vegetation | Tree - grew into line | 23 | 7935 | 38.8481 | -122.7563 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0095454 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1961779 | 0 | EPSS Ckt | N | 2024
28750 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | JUMPER | OJ'S @ CGC 217178853283 | 2024-08-07 | 946 | 20240807 | 1215 | 2536633 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 894 | 39.1251 | -122.9961 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0096702 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1962699 | 0 | EPSS Ckt | N | 2024
28762 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | TRANSFORMER | 217147254923 | 2024-08-11 | 1030 | 20240811 | 1434 | 2539759 | 244 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 244 | 39.1703 | -123.0075 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0098069 | OH | Sus | 0 | NORTH COAST | AUG | None | 0 | No | No | No | 1963542 | 0 | EPSS Ckt | N | 2024
28776 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | TRANSFORMER | 100000037670 | 2024-08-16 | 1504 | 20240816 | 1748 | 2543858 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 38.8175 | -122.4975 | No | Clear;32-90 F | Transformer | Failed/Faulted | 24-0100135 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1964852 | 0 | EPSS Ckt | N | 2024
28848 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | OCB | 1101/2 | 2024-08-30 | 1705 | 20240831 | 205 | 2556182 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 1043 | 67008 | 39.146 | -122.9171 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0105473 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | Yes | No | 1968574 | 0 | EPSS Ckt | Y | 2024 | SET A TRIP INST OC
28911 | HUMBOLDT | UKIAH | REDBUD-1102 | 43191102 | RECLOSER | 922 | 2024-09-12 | 59 | 20240912 | 408 | 2566100 | 189 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 337 | 58293 | 38.999 | -122.6724 | No | Clear;32-90 F |  |  | 24-0109998 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1971460 | 0 | EPSS Ckt | Y | 2024 | AB
29069 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2024-10-17 | 1811 | 20241019 | 1640 | 2597664 | 2789 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 153395 | 38.8967 | -122.5542 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123921 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1981475 | 0 | EPSS Ckt | N | 2024 | none
29070 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | FUSE | 1817 | 2024-10-17 | 1817 | 20241019 | 1251 | 2597802 | 2544 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 29 | 72836 | 38.8067 | -122.7066 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124263 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1981514 | 0 | EPSS Ckt | N | 2024
29072 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | RECLOSER | 628 | 2024-10-17 | 1823 | 20241019 | 1608 | 2597690 | 2745 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 33 | 90585 | 38.9822 | -122.6031 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123880 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1981481 | 0 | EPSS Ckt | N | 2024 | NONE
29073 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2024-10-17 | 1825 | 20241019 | 1809 | 2597715 | 2864 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 560 | 1581733 | 39.0584 | -122.6925 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124238 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1981488 | 0 | EPSS Ckt | N | 2024 | NONE
29074 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 829164 | 2024-10-17 | 1827 | 20241017 | 1859 | 2597782 | 32 | Distribution Circuit | Company Initiated | Operating error | 1696 | 54272 | 38.7537 | -122.6111 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124773 | OH | Sus | 0 | NORTH COAST | OCT | Line to Ground | 0 | No | No | No | 1981496 | 0 | EPSS Ckt | Y | 2024 | SFG/DCD
29077 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | OCB | 1101/2 | 2024-10-17 | 1942 | 20241017 | 2058 | 2597841 | 76 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4275 | 261035 | 38.7527 | -122.608 | Yes | Clear;32-90 F |  |  | 24-0124790 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1981517 | 0 | EPSS Ckt | Y | 2024 | INST OC
29114 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 872796 | 2024-10-30 | 859 | 20241030 | 1601 | 2608088 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 43044 | 38.7244 | -122.6188 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0129445 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1984778 | 0 | EPSS Ckt | N | 2024 | NONE
29125 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | TRANSFORMER | 217431156102 | 2024-11-01 | 955 | 20241101 | 1338 | 2610221 | 223 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 223 | 39.2034 | -122.908 | No | Overcast;32-90 F | Transformer | Deteriorated | 24-0121810 | OH | Sus | 45685611 | NORTH COAST | NOV | None | 0 | No | No | No | 1985502 | 0 | EPSS Ckt | N | 2024
29158 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 503107 | 2024-11-05 | 1850 | 20241107 | 955 | 2614701 | 2345 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 10 | 23450 | 38.781 | -122.6862 | Yes | Partly Cloudy;32-90 F |  |  | 24-0131788 | OH | Sus | 0 | NORTH COAST | NOV | None | 0 | No | No | No | 1986695 | 0 | EPSS Ckt | N | 2024
29161 | HUMBOLDT | UKIAH | HIGHLANDS-1103 | 43361103 | RECLOSER | 287766 | 2024-11-05 | 2200 | 20241107 | 907 | 2615024 | 2107 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 115885 | 38.8967 | -122.5542 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131780 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986814 | 0 | EPSS Ckt | N | 2024 | NONE
29162 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | TRANSFORMER | 218326150814 | 2024-11-05 | 2230 | 20241107 | 1040 | 2617738 | 2170 | Transformer only | Vegetation | Tree - grew into line | 1 | 2170 | 39.0603 | -122.5896 | Yes | Clear;32-90 F | Transformer (OH) | Normal | 24-0133026 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1987512 | 0 | EPSS Ckt | N | 2024
29163 | HUMBOLDT | UKIAH | REDBUD-1101 | 43191101 | RECLOSER | 754544 | 2024-11-05 | 2231 | 20241107 | 944 | 2615050 | 2113 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 552 | 1164220 | 39.0584 | -122.6925 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131798 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986826 | 0 | EPSS Ckt | N | 2024 | NONE
29165 | HUMBOLDT | UKIAH | HIGHLANDS-1102 | 43361102 | RECLOSER | 628 | 2024-11-05 | 2239 | 20241107 | 1002 | 2615074 | 2123 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 33 | 70059 | 38.9822 | -122.6031 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131777 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986834 | 0 | EPSS Ckt | N | 2024 | NONE
29167 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | OTHER | HOT WIRE DOWN 8 SPANS LD SIDE 463705 | 2024-11-06 | 510 | 20241107 | 1343 | 2615551 | 1953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 60525 | 38.7097 | -122.6479 | No | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0132372 | OH | Sus | 31716696 | NORTH COAST | NOV | Line to Ground | 0 | No | Yes | Yes | 1986939 | 0 | EPSS Ckt | N | 2024
29169 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 571926 | 2024-11-06 | 705 | 20241107 | 1158 | 2615771 | 1733 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 15 | 25995 | 38.7342 | -122.6319 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986988 | 0 | EPSS Ckt | N | 2024 | NONE
29170 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 1314 | 2024-11-06 | 705 | 20241107 | 1156 | 2615782 | 1731 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 70971 | 38.7312 | -122.6235 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986992 | 0 | EPSS Ckt | N | 2024 | NONE
29171 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | SWITCH | 433160 | 2024-11-06 | 705 | 20241107 | 1201 | 2615784 | 1736 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 19 | 32984 | 38.7253 | -122.619 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986993 | 0 | EPSS Ckt | Y | 2024
29172 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 872796 | 2024-11-06 | 705 | 20241107 | 1200 | 2615787 | 1735 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 97 | 168295 | 38.7244 | -122.6188 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986995 | 0 | EPSS Ckt | N | 2024 | NONE
29173 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2024-11-06 | 705 | 20241107 | 1202 | 2615788 | 1737 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 8685 | 38.6949 | -122.5975 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986997 | 0 | EPSS Ckt | N | 2024 | NONE
29173 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2024-11-06 | 705 | 20241107 | 1202 | 2615788 | 1737 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 8685 | 38.6949 | -122.5975 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986997 | 0 | EPSS Ckt | N | 2024 | NONE
29173 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 352182 | 2024-11-06 | 705 | 20241107 | 1202 | 2615788 | 1737 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 8685 | 38.6949 | -122.5975 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986997 | 0 | EPSS Ckt | N | 2024 | NONE
29174 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 959140 | 2024-11-06 | 708 | 20241107 | 959 | 2615790 | 1611 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 20943 | 38.7722 | -122.6244 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131789 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1987000 | 0 | EPSS Ckt | N | 2024 | NONE
29220 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | RECLOSER | 463705 | 2024-11-14 | 1306 | 20241114 | 1523 | 2625156 | 137 | Distribution Circuit | Company Initiated | Personnel- company | 31 | 4247 | 38.7128 | -122.644 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 24-0135623 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | No | No | 1989795 | 0 | EPSS Ckt | N | 2024 | N/A
29225 | HUMBOLDT | UKIAH | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 2024-11-15 | 901 | 20241115 | 1701 | 2625859 | 480 | Distribution Circuit | 3rd Party | Vehicle | 99 | 32130 | 38.8761 | -122.7755 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0135914 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | Yes | No | 1990070 | 0 | EPSS Ckt | N | 2024 | AB
29531 | HUMBOLDT | UKIAH | UPPER LAKE-1101 | 42871101 | FUSE | 743 | 2024-11-30 | 706 | 20241130 | 1010 | 2640472 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1656 | 39.2305 | -122.9444 | No | Clear;32-90 F |  |  | 24-0141385 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | No | No | 1993400 | 0 | EPSS Ckt | N | 2024
29597 | HUMBOLDT | UKIAH | MIDDLETOWN-1102 | 43141102 | TRANSFORMER | T931364 | 2024-12-08 | 1249 | 20241208 | 2308 | 2647102 | 619 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 1238 | 38.7099 | -122.5425 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0143768 | UG | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 1995519 | 0 | EPSS Ckt | N | 2024
29653 | HUMBOLDT | UKIAH | KONOCTI-1102 | 43311102 | FUSE | 1697 | 2024-12-13 | 1842 | 20241214 | 1121 | 2652259 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 32967 | 38.9145 | -122.8574 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0144962 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | Yes | No | 1997262 | 0 | EPSS Ckt | N | 2024
29721 | HUMBOLDT | UKIAH | CLEAR LAKE-1102 | 42141102 | SWITCH | 3555 | 2024-12-23 | 1031 | 20241223 | 1238 | 2668253 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 11430 | 38.9574 | -122.894 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0147475 | OH | Sus | 0 | NORTH COAST | DEC | Force Out | 0 | No | No | No | 2000517 | 0 | EPSS Ckt | N | 2024
29746 | HUMBOLDT | UKIAH | HARTLEY-1101 | 43211101 | FUSE | 1113 | 2024-12-26 | 1047 | 20241226 | 1554 | 2670051 | 307 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 10438 | 39.0442 | -122.9544 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0147817 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | No | No | 2000915 | 0 | EPSS Ckt | N | 2024
29963 | KERN | KERN | SISQUOC-1102 | 182811102 | FUSE | 15497 | 2023-01-28 | 1022 | 20230128 | 1620 | 1970383 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1074 | 35.1908 | -119.9528 | No | Clear;32-90F |  |  | 23-0022659 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1808848 | 0 | EPSS Ckt | N | 2023
30172 | KERN | KERN | SISQUOC-1102 | 182811102 | TRIP-SAVER | 45261 | 2023-02-27 | 1000 | 20230412 | 1252 | 2011718 | 63532 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 193577 | 35.1099 | -120.09 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 23-0036225 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818948 | 0 | EPSS Ckt | N | 2023 | NONE
30172 | KERN | KERN | SISQUOC-1102 | 182811102 | TRIP-SAVER | 45261 | 2023-02-27 | 1000 | 20230412 | 1252 | 2011718 | 63532 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 193577 | 35.1099 | -120.09 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 23-0036225 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818948 | 0 | EPSS Ckt | N | 2023 | NONE
30172 | KERN | KERN | SISQUOC-1102 | 182811102 | TRIP-SAVER | 45261 | 2023-02-27 | 1000 | 20230412 | 1252 | 2011718 | 63532 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 193577 | 35.1099 | -120.09 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 23-0036225 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818948 | 0 | EPSS Ckt | N | 2023 | NONE
30179 | KERN | KERN | TEJON-1102 | 252931102 | FUSE | 14746 | 2023-02-27 | 1829 | 20230228 | 127 | 2013540 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 569 | 131435 | 34.8751 | -118.8937 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0036718 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819278 | 0 | EPSS Ckt | N | 2023
30232 | KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 2023-03-10 | 352 | 20230323 | 1449 | 2030031 | 19377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 116262 | 35.0707 | -119.9955 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042719 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1823530 | 0 | EPSS Ckt | N | 2023 | B C
30354 | KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517325550185 | 2023-03-26 | 2006 | 20230326 | 2221 | 2067969 | 135 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 135 | 34.876 | -118.8932 | No | Partly Cloudy;32-90 F |  |  | 23-0052756 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1830690 | 0 | EPSS Ckt | N | 2023
30655 | KERN | KERN | CUYAMA-1103 | 253141103 | TRANSFORMER | 514419558517 | 2023-05-16 | 1418 | 20230516 | 1953 | 2114268 | 335 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 670 | 35.0915 | -119.8656 | No | Partly Cloudy;32-90 F |  |  | 23-0072388 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1843657 | 0 | EPSS Ckt | N | 2023
30903 | KERN | KERN | SISQUOC-1102 | 182811102 | FUSE | 15497 | 2023-06-22 | 1200 | 20230622 | 1533 | 2143223 | 213 | Distribution Circuit | Animal | Bird found | 3 | 478 | 35.1907 | -119.9531 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0084712 | OH | Sus | 31653165 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1852461 | 0 | EPSS Ckt | N | 2023
31001 | KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 2023-07-07 | 1221 | 20230707 | 1614 | 2156301 | 233 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1398 | 35.0707 | -119.9955 | No | Clear;32-90 F |  |  | 23-0089890 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855732 | 0 | EPSS Ckt | Y | 2023 | A
31450 | KERN | KERN | SCE TEHACHAPI-1101 | 258131101 | OCB | 1101/2 | 2023-09-16 | 2104 | 20230917 | 254 | 2220809 | 350 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 1050 | 35.1976 | -118.7007 | No | Clear;32-90 F |  |  | 23-0117499 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1874577 | 0 | Non-EPSS | N | 2023 | SCE RELAY
32118 | KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 2024-02-04 | 905 | 20240206 | 1337 | 2335967 | 3152 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 18912 | 35.0707 | -119.9955 | Yes | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0019332 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1909239 | 0 | EPSS Ckt | N | 2024 | BC
32185 | KERN | KERN | TEJON-1102 | 252931102 | TRANSFORMER | 517168050770 | 2024-02-04 | 1253 | 20240206 | 2142 | 2342614 | 3409 | Transformer only | Environmental/External | Water | 1 | 3409 | 34.8887 | -118.9491 | Yes | Strong Winds-Overcast-Heavy Rain;32-90 F | Transformer | Normal | 24-0022317 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1911970 | 0 | EPSS Ckt | N | 2024
32646 | KERN | KERN | CUYAMA-1103 | 253141103 | RECLOSER | 684566 | 2024-04-13 | 1213 | 20240414 | 935 | 2430304 | 1282 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 7692 | 35.0707 | -119.9955 | No | Overcast-Rain;32-90 F |  |  | 24-0054421 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1933312 | 0 | EPSS Ckt | N | 2024 | B- C
32806 | KERN | KERN | CUYAMA-2101 | 253142101 | FUSE | 14274 | 2024-04-29 | 1140 | 20240429 | 1228 | 2441706 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 48 | 34.8121 | -119.4569 | No | Clear;32-90 F | Jumper | Deteriorated | 24-0059994 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1937335 | 0 | EPSS Ckt | N | 2024
33789 | KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 2024-10-17 | 2119 | 20241017 | 2232 | 2598007 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 550 | 40150 | 34.8817 | -118.9019 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124807 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1981574 | 0 | EPSS Ckt | Y | 2024 | B- C
33861 | KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 2024-11-03 | 305 | 20241103 | 1056 | 2612123 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 566 | 238586 | 34.8817 | -118.9019 | No | Overcast-Fog;32-90 F | Lightning Arrestor | Failed/Faulted | 24-0131073 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1985931 | 0 | EPSS Ckt | Y | 2024 | BC
33873 | KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 2024-11-06 | 530 | 20241107 | 946 | s1986948 | 1696 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 69536 | 34.8817 | -118.9019 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131199 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1986948 | 0 | EPSS Ckt | N | 2024 | NA
34130 | KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 2024-12-09 | 2001 | 20241210 | 1659 | s1995861 | 1258 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 51578 | 34.8817 | -118.9019 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143773 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1995861 | 0 | EPSS Ckt | N | 2024 | N/A
34151 | KERN | KERN | TEJON-1102 | 252931102 | RECLOSER | 732836 | 2024-12-14 | 1117 | 20241214 | 1242 | 2658263 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 566 | 48110 | 34.8817 | -118.9019 | Yes | Partly Cloudy;32-90 F |  |  | 24-0145573 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997896 | 0 | EPSS Ckt | Y | 2024 | B C
34371 | LOS PADRES | PASO ROBLES | PASO ROBLES-1104 | 182611104 | TRANSFORMER | 511873279404 | 2023-01-09 | 1941 | 20230112 | 1109 | 1939509 | 3808 | Transformer only | Environmental/External | Lightning | 1 | 3808 | 35.6515 | -120.7356 | Yes | Clear;32-90 F | Transformer | Burned/flashed | 23-0013885 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1803246 | 0 | EPSS Ckt | N | 2023
34376 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 2023-01-09 | 2108 | 20230115 | 756 | 1939662 | 7848 | Distribution Circuit | Environmental/External | Flood/Erosion | 56 | 76103 | 35.4345 | -120.2869 | Yes | Clear;32-90F | Pole-Wood | On Ground | 23-0011630 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1801394 | 0 | EPSS Ckt | N | 2023 | A GRD
34419 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 3945 | 2023-01-12 | 1213 | 20230112 | 1513 | 1950136 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 10260 | 35.4394 | -120.4877 | No | Clear;32-90F | Secondary | Broken | 23-0014564 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Line | 0 | No | No | No | 1803790 | 0 | EPSS Ckt | N | 2023
34464 | LOS PADRES | PASO ROBLES | SAN MIGUEL 1106 | 182661106 | FUSE | 5707 | 2023-01-16 | 737 | 20230116 | 1132 | 1957220 | 235 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 784 | 35.9307 | -120.6774 | Yes | Clear;32-90F |  |  | 23-0017169 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | No | No | 1805857 | 1 | EPSS Ckt | N | 2023
34676 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 2023-02-24 | 2122 | 20230227 | 1655 | 2007224 | 4037 | Distribution Circuit | Environmental/External | Ice or snow | 394 | 545003 | 35.3806 | -120.4438 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034663 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817520 | 0 | EPSS Ckt | N | 2023 | B-C- GRD
34678 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30681 | 2023-02-24 | 2122 | 20230227 | 1454 | 2009484 | 3932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 19660 | 35.3678 | -120.3989 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035569 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | Yes | No | 1818420 | 0 | EPSS Ckt | N | 2023
34679 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5143 | 2023-02-24 | 2122 | 20230226 | 1900 | 2009787 | 2738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 38332 | 35.3109 | -120.3215 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035631 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818476 | 0 | EPSS Ckt | N | 2023
34680 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7047 | 2023-02-24 | 2122 | 20230228 | 1557 | 2009895 | 5435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16305 | 35.3807 | -120.419 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | Yes | No | 1818518 | 0 | EPSS Ckt | N | 2023
34682 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | SWITCH | 6535 | 2023-02-24 | 2122 | 20230301 | 1715 | 2010827 | 6953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 27812 | 35.2555 | -120.2714 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035944 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818755 | 0 | EPSS Ckt | N | 2023
34683 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 2023-02-24 | 2126 | 20230226 | 2130 | 2007226 | 2884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 156400 | 35.4345 | -120.2869 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034683 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1817541 | 0 | EPSS Ckt | N | 2023 | C GRD
34685 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 2023-02-24 | 2232 | 20230225 | 2127 | 2007344 | 1375 | Distribution Circuit | Environmental/External | Ice or snow | 18 | 24750 | 35.8461 | -120.3793 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034996 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | Yes | No | 1817862 | 0 | EPSS Ckt | N | 2023 | A- B- GRD- 51 TIME
34689 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | JUMPER | FB 1 E OF 30299 | 2023-02-24 | 2238 | 20230227 | 1430 | 2010398 | 3832 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 76640 | 35.9207 | -120.4923 | Yes | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035857 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818679 | 0 | EPSS Ckt | N | 2023
34693 | LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | JUMPER | OJ 2 POLES SS CGC 513347454906 | 2023-02-25 | 57 | 20230228 | 1245 | 2013587 | 5028 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15084 | 34.9893 | -120.222 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0036737 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | None | 0 | No | No | No | 1819297 | 0 | EPSS Ckt | N | 2023
34704 | LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 30019 | 2023-02-25 | 1615 | 20230228 | 1755 | 2008905 | 4420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 11086 | 35.291 | -120.4757 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035496 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818344 | 0 | EPSS Ckt | N | 2023
34737 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30681 | 2023-03-03 | 658 | 20230303 | 1058 | 2020743 | 238 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1190 | 35.3678 | -120.3989 | No | Clear;32-90F |  |  | 23-0039414 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1821272 | 0 | EPSS Ckt | N | 2023
34866 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 5293 | 2023-03-21 | 908 | 20230321 | 1609 | 2053755 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 5909 | 35.3811 | -120.449 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049378 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | Yes | No | 1828161 | 0 | EPSS Ckt | N | 2023
34883 | LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 5707 | 2023-03-22 | 1014 | 20230322 | 1212 | 2062246 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 394 | 35.9307 | -120.6774 | No | Clear;32-90 F |  |  | 23-0050674 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Ground | 0 | No | No | No | 1829164 | 1 | EPSS Ckt | N | 2023
34888 | LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | FUSE | 30017 | 2023-03-23 | 1119 | 20230323 | 1522 | 2064546 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 35.2993 | -120.4896 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051328 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Three Phase Fault | 0 | No | Yes | No | 1829610 | 0 | EPSS Ckt | N | 2023
35020 | LOS PADRES | PASO ROBLES | CHOLAME-1101 | 182561101 | FUSE | 6217 | 2023-05-04 | 2036 | 20230504 | 2219 | 2105110 | 103 | Distribution Circuit | 3rd Party | Other | 5 | 515 | 35.8433 | -120.3805 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0068495 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1840956 | 0 | EPSS Ckt | N | 2023
35086 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | SWITCH | 2755 | 2023-05-25 | 1602 | 20230525 | 1724 | 2121425 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 3198 | 35.4053 | -120.2577 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0075673 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1845945 | 0 | EPSS Ckt | N | 2023
35090 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7385 | 2023-05-26 | 909 | 20230526 | 1106 | 2121988 | 117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1287 | 35.4325 | -120.4912 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0075905 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Force Out | 0 | No | No | No | 1846114 | 0 | EPSS Ckt | N | 2023
35096 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 7057 | 2023-05-27 | 1242 | 20230527 | 1622 | 2122700 | 220 | Distribution Circuit | Animal | Squirrel | 4 | 880 | 35.4527 | -120.5049 | No | Clear;32-90 F | Fuse | Burned Open | 23-0076346 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Three Phase Fault | 0 | No | No | No | 1846352 | 0 | EPSS Ckt | N | 2023
35116 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | TRANSFORMER | 415561721879 | 2023-06-02 | 1124 | 20230602 | 1435 | 2127369 | 191 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 191 | 35.9242 | -120.4989 | No | Clear;32-90 F |  |  | 23-0078387 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | None | 0 | No | No | No | 1847597 | 0 | EPSS Ckt | N | 2023
35196 | LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 1863 | 2023-06-26 | 1538 | 20230626 | 2123 | 2146296 | 345 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 34 | 10153 | 34.5514 | -119.9703 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0085841 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Ground | 0 | No | No | No | 1853297 | 1 | EPSS Ckt | N | 2023
35287 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 2023-07-19 | 23 | 20230719 | 1310 | 2167359 | 767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 408 | 92616 | 35.4109 | -120.5655 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0093986 | OH | Sus | 31656143 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1858624 | 0 | EPSS Ckt | Y | 2023 | C GRD
35332 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 2023-07-28 | 848 | 20230728 | 905 | s1861224 | 17 | Distribution Circuit | Company Initiated | Personnel- company | 16 | 272 | 35.4345 | -120.2869 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0093280 | OH | Sus | 31622825 | SOUTH BAY AND CENTRAL COAST | JUL | None | 0 | No | No | No | 1861224 | 0 | EPSS Ckt | N | 2023 | SGF
35349 | LOS PADRES | PASO ROBLES | ATASCADERO-1103 | 182541103 | TRANSFORMER | 512775066160 | 2023-08-01 | 2243 | 20230802 | 1825 | 2180020 | 1182 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1182 | 35.2922 | -120.4217 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0099370 | OH | Sus | 35474136 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Ground | 0 | No | No | No | 1862249 | 0 | EPSS Ckt | N | 2023
35385 | LOS PADRES | SANTA MARIA | ZACA-1102 | 182681102 | FUSE | 6917 | 2023-08-12 | 906 | 20230812 | 1158 | 2189060 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2236 | 34.7327 | -119.9963 | No | Clear;32-90 F | Other | Malfunctioning | 23-0103573 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | None | 0 | No | No | No | 1865160 | 0 | EPSS Ckt | N | 2023
35478 | LOS PADRES | SANTA MARIA | SISQUOC-1102 | 182811102 | TRANSFORMER | 513542557915 | 2023-09-05 | 627 | 20230905 | 1623 | 2209663 | 596 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 596 | 35.0714 | -120.1618 | No | Fog;32-90 F | Pole-Wood | Deteriorated | 23-0112430 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871184 | 0 | EPSS Ckt | N | 2023
35483 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 30415 | 2023-09-05 | 1950 | 20230905 | 2203 | 2210407 | 133 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 133 | 35.4215 | -120.4655 | No | Clear;32-90 F | Secondary | Broken | 23-0112820 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1871399 | 0 | EPSS Ckt | N | 2023
35673 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512635669683 | 2023-10-28 | 1115 | 20231028 | 1452 | 2254198 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 868 | 35.3899 | -120.472 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885850 | 0 | EPSS Ckt | N | 2023
35673 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512635669683 | 2023-10-28 | 1115 | 20231028 | 1452 | 2254198 | 217 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 868 | 35.3899 | -120.472 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0133538 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Line to Ground | 0 | No | No | No | 1885850 | 0 | EPSS Ckt | N | 2023
35732 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 2023-11-14 | 1059 | 20231114 | 1409 | 2269025 | 190 | Distribution Circuit | Animal | Bird found | 148 | 28120 | 35.8461 | -120.3793 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0138815 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890482 | 0 | EPSS Ckt | Y | 2023 | A & B
35741 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 796386 | 2023-11-15 | 1547 | 20231115 | 1744 | 2270103 | 117 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 148 | 17316 | 35.8461 | -120.3793 | No | Overcast;32-90 F |  |  | 23-0139546 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1890868 | 0 | EPSS Ckt | Y | 2023 | B- C & INST OC
35762 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 2023-11-18 | 511 | 20231118 | 1051 | 2272035 | 340 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 19040 | 35.4345 | -120.2869 | No | Partly Cloudy-Fog;32-90 F |  |  | 23-0140753 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1891467 | 0 | EPSS Ckt | Y | 2023 | SGF DCD
35814 | LOS PADRES | SANTA MARIA | SANTA YNEZ-1101 | 182721101 | FUSE | 7459 | 2023-11-30 | 927 | 20231130 | 1229 | 2280646 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 182 | 34.547 | -119.8929 | No | Partly Cloudy;32-90 F |  |  | 23-0144248 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Ground | 0 | No | No | No | 1894029 | 1 | EPSS Ckt | N | 2023
36192 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | TRANSFORMER | 512458070610 | 2024-02-06 | 2159 | 20240207 | 205 | 2365907 | 246 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 492 | 35.4135 | -120.5306 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0023917 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1913281 | 0 | EPSS Ckt | N | 2024
36300 | LOS PADRES | PASO ROBLES | SAN MIGUEL-1106 | 182661106 | FUSE | 5707 | 2024-03-02 | 1146 | 20240302 | 1640 | 2394867 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1470 | 35.9307 | -120.6774 | No | Clear;32-90 F |  |  | 24-0036987 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Line to Line | 0 | No | No | No | 1921942 | 0 | EPSS Ckt | N | 2024
36338 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 2024-03-13 | 1350 | 20240313 | 1537 | 2403645 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 9900 | 35.3806 | -120.4438 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0041562 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAR | Force Out | 0 | No | No | No | 1924727 | 0 | EPSS Ckt | N | 2024 | NONE
36572 | LOS PADRES | PASO ROBLES | CHOLAME-2102 | 182562102 | RECLOSER | 867686 | 2024-05-22 | 1737 | 20240522 | 2004 | 2465360 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 8232 | 35.4345 | -120.2869 | No | Clear;32-90 F |  |  | 24-0068960 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Line | 0 | No | No | No | 1943559 | 0 | EPSS Ckt | Y | 2024 | B & C PHSE
36883 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 2024-08-03 | 1307 | 20240803 | 1725 | 2533699 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 34056 | 35.3806 | -120.4438 | No | Clear;32-90 F |  |  | 24-0095422 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | AUG | Line to Line | 0 | No | No | No | 1961749 | 0 | EPSS Ckt | Y | 2024 | A B INST OC
37075 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 2024-09-14 | 631 | 20240914 | 902 | 2567971 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 411 | 27465 | 35.4109 | -120.5655 | No | Clear;32-90 F |  |  | 24-0110975 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1972058 | 0 | EPSS Ckt | Y | 2024 | B C
37141 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 2024-09-27 | 647 | 20240927 | 1051 | 2579073 | 244 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 32208 | 35.3806 | -120.4438 | No | Clear;32-90 F |  |  | 24-0116322 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Line | 0 | No | No | No | 1975762 | 0 | EPSS Ckt | Y | 2024 | A B INST
37148 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | JUMPER | OJ 1 SPAN N/OF CGC # 512669771808 | 2024-09-29 | 1100 | 20240929 | 1353 | 2580613 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 173 | 35.4524 | -120.4641 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0117037 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Force Out | 0 | No | No | No | 1976320 | 0 | EPSS Ckt | N | 2024
37366 | LOS PADRES | PASO ROBLES | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 2024-11-25 | 1125 | 20241125 | 1919 | 2637639 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 8532 | 35.3953 | -120.5192 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0140032 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | Line to Line | 0 | No | No | No | 1992793 | 0 | EPSS Ckt | N | 2024
37713 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 2023-02-19 | 1759 | 20230219 | 1900 | 1988992 | 61 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 244 | 37.5977 | -121.6341 | Yes | Clear;32-90 F |  |  | 23-0030580 | OH | Sus | 0 | BAY AREA | FEB | Line to Line | 0 | No | No | No | 1814331 | 0 | EPSS Ckt | N | 2023
37740 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 73969 | 2023-02-24 | 1524 | 20230225 | 1540 | 2008151 | 1456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2912 | 37.5778 | -121.586 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035120 | OH | Sus | 0 | BAY AREA | FEB | Line to Ground | 0 | No | Yes | No | 1817983 | 0 | EPSS Ckt | N | 2023
37767 | MISSION | MISSION | VASCO-1102 | 13751102 | OTHER | J71114 TWD T7488 | 2023-03-07 | 1837 | 20230308 | 228 | 2025975 | 471 | Distribution Circuit | Equipment Failure/Involved | Underground | 9 | 4239 | 37.584 | -121.693 | No | Clear;32-90F | Transformer (UG) | Broken | 23-0041188 | UG | Sus | 35430857 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1822712 | 0 | EPSS Ckt | N | 2023
37782 | MISSION | MISSION | VASCO-1102 | 13751102 | OTHER | J71114 TWD T7488 | 2023-03-12 | 1425 | 20230312 | 1445 | 2033367 | 20 | Distribution Circuit | 3rd Party | Customer Equipment | 13 | 204 | 37.584 | -121.693 | No | Overcast-Fog;32-90 F | Transformer (UG) | Normal | 23-0043738 | UG | Sus | 0 | BAY AREA | MAR | Force Out | 0 | No | No | No | 1824255 | 0 | EPSS Ckt | N | 2023
37840 | MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 13908 | 2023-03-14 | 1349 | 20230317 | 1221 | 2044470 | 4232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 38088 | 37.8131 | -121.7954 | Yes | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0045808 | OH | Sus | 0 | BAY AREA | MAR | Multi-Fault | 0 | No | Yes | No | 1825730 | 0 | EPSS Ckt | N | 2023
37949 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 2023-04-05 | 1234 | 20230405 | 1727 | 2080841 | 293 | Distribution Circuit | 3rd Party | Other | 1 | 293 | 37.5786 | -121.5877 | No | Clear;32-90 F | Fuse | Normal | 23-0057687 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1833559 | 0 | EPSS Ckt | N | 2023
38001 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 14877 | 2023-04-29 | 941 | 20230429 | 2045 | 2100001 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2656 | 37.564 | -121.683 | No | Clear;32-90 F | Jumper | Burned Open | 23-0066323 | OH | Sus | 45745135 | BAY AREA | APR | Line to Ground | 0 | No | No | No | 1839544 | 0 | EPSS Ckt | N | 2023
38482 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 2023-11-15 | 1731 | 20231116 | 135 | 2270341 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1936 | 37.5977 | -121.6341 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0139660 | OH | Sus | 46059257 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1890923 | 0 | EPSS Ckt | N | 2023
38856 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 13026 | 2024-04-24 | 943 | 20240424 | 1120 | 2438037 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 291 | 37.5951 | -121.6317 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0058391 | OH | Sus | 0 | BAY AREA | APR | Force Out | 0 | No | No | No | 1936079 | 0 | EPSS Ckt | N | 2024
38858 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10225 | 2024-04-25 | 1230 | 20240425 | 1720 | 2438663 | 290 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 20 | 3800 | 37.579 | -121.6832 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 24-0058937 | UG | Sus | 31692106 | BAY AREA | APR | Force Out | 0 | No | No | No | 1936445 | 0 | EPSS Ckt | N | 2024
39450 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 2024-10-17 | 2120 | 20241019 | 1540 | 2598023 | 2540 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2540 | 37.5786 | -121.5877 | Yes | Clear;32-90 F |  |  | 24-0123917 | OH | Sus | 8216649 | BAY AREA | OCT | Force Out | 0 | No | No | No | 1981582 | 0 | EPSS Ckt | N | 2024
39503 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 8917 | 2024-11-04 | 1316 | 20241104 | 1643 | 2613453 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 5382 | 37.5848 | -121.6 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0131538 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986330 | 0 | EPSS Ckt | N | 2024
39514 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10633 | 2024-11-05 | 1926 | 20241106 | 1721 | 2615013 | 1315 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1315 | 37.5786 | -121.5877 | Yes | Clear;32-90 F |  |  | 24-0131971 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1986808 | 0 | EPSS Ckt | N | 2024
39522 | MISSION | MISSION | CAYETANO-2109 | 14422109 | FUSE | 72173 | 2024-11-05 | 2026 | 20241107 | 927 | 2617261 | 2221 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 31094 | 37.8155 | -121.7953 | Yes | Clear;32-90 F |  |  | 24-0131842 | OH | Sus | 0 | BAY AREA | NOV | Force Out | 0 | No | No | No | 1987331 | 0 | EPSS Ckt | N | 2024
39609 | MISSION | MISSION | VASCO-1102 | 13751102 | FUSE | 10882 | 2024-11-30 | 1920 | 20241130 | 2216 | 2640922 | 176 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 352 | 37.5977 | -121.6341 | No | Clear;32-90 F |  |  | 24-0141467 | OH | Sus | 0 | BAY AREA | NOV | Line to Line | 0 | No | No | No | 1993445 | 0 | EPSS Ckt | N | 2024
39772 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 7511 | 2023-01-04 | 1921 | 20230106 | 1715 | 1917589 | 2754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33048 | 38.468 | -122.2295 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007087 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797381 | 0 | EPSS Ckt | N | 2023
39821 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 639467 | 2023-01-06 | 1350 | 20230106 | 1604 | 1925272 | 134 | Distribution Circuit | Animal | Other | 16 | 2144 | 38.6258 | -122.2907 | No | Clear;32-90F | Cutout- fuse holder | Normal | 23-0008479 | OH | Sus | 0 | NORTH COAST | JAN | Line to Line | 0 | No | No | No | 1798411 | 0 | EPSS Ckt | N | 2023
39822 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | TRANSFORMER | 219640030135 | 2023-01-06 | 1454 | 20230107 | 1437 | 1925170 | 1423 | Transformer only | Environmental/External | Water | 16 | 22768 | 38.4945 | -122.1273 | No | Clear;32-90 F | Transformer | Broken | 23-0008545 | OH | Sus | 0 | NORTH COAST | JAN | Line to Ground | 0 | No | No | No | 1798471 | 0 | EPSS Ckt | N | 2023
39930 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 256640 | 2023-01-10 | 2021 | 20230110 | 2156 | 1946476 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 3230 | 38.6063 | -122.2807 | Yes | Clear;32-90F |  |  | 23-0012992 | OH | Sus | 0 | NORTH COAST | JAN | Open Circuit | 0 | No | No | No | 1802552 | 0 | EPSS Ckt | N | 2023 | NA
39999 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN LD SIDE OF 2663 | 2023-01-19 | 1226 | 20230120 | 120 | 1962136 | 774 | Distribution Circuit | Equipment Failure/Involved | Overhead | 739 | 19211 | 38.6101 | -122.4578 | No | Clear;32-90 F | Jumper | Broken- wire on ground | 23-0018970 | OH | Sus | 31634836 | NORTH COAST | JAN | Line to Ground | 0 | No | Yes | Yes | 1806814 | 0 | EPSS Ckt | N | 2023
40026 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | SWITCH | 1812 | 2023-01-29 | 1632 | 20230129 | 2055 | 1971052 | 263 | Distribution Circuit | Equipment Failure/Involved | Underground | 256 | 46413 | 38.508 | -122.1959 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0022665 | UG | Sus | 0 | NORTH COAST | JAN | None | 0 | No | No | No | 1808944 | 0 | EPSS Ckt | N | 2023
40087 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | OTHER | GENERATOR AT 761725 | 2023-02-13 | 939 | 20230214 | 129 | 1983468 | 950 | Distribution Circuit | Company Initiated | Return Circuit Normal | 256 | 161816 | 38.5112 | -122.1822 | No | Clear;32-90 F | Conductor- Underground | Normal | 23-0022665 | UG | Sus | 35423905 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1812755 | 0 | EPSS Ckt | N | 2023
40115 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 4645 | 2023-02-18 | 639 | 20230218 | 1056 | 1988059 | 257 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4112 | 38.6009 | -122.3702 | No | Clear;32-90 F |  |  | 23-0030460 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1814194 | 0 | EPSS Ckt | N | 2023
40181 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 4307 | 2023-02-23 | 2139 | 20230226 | 2311 | 2008517 | 4412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 44120 | 38.5922 | -122.4463 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035258 | OH | Sus | 0 | NORTH COAST | FEB | Multi-Fault | 0 | No | Yes | No | 1818096 | 0 | EPSS Ckt | N | 2023
40193 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN W/O 2843 | 2023-02-24 | 109 | 20230228 | 1727 | 2001496 | 6738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 1154646 | 38.4822 | -122.1627 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033560 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1816592 | 0 | EPSS Ckt | N | 2023
40213 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218722232954 | 2023-02-25 | 2057 | 20230227 | 1428 | 2010402 | 2491 | Transformer only | Environmental/External | Ice or snow | 3 | 7473 | 38.5707 | -122.448 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0035859 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818681 | 0 | EPSS Ckt | N | 2023
40235 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218724633103 | 2023-02-27 | 1919 | 20230228 | 1225 | 2013646 | 1026 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2052 | 38.5744 | -122.447 | Yes | Clear;32-90F | Transformer (OH) | Broken | 23-0036919 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1819464 | 0 | EPSS Ckt | N | 2023
40243 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | SWITCH | 761 | 2023-02-28 | 1447 | 20230228 | 1627 | 2015937 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 6500 | 38.5927 | -122.4486 | Yes | Clear;32-90F | Conductor- Overhead | Deteriorated | 23-0037502 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | No | No | 1819872 | 0 | EPSS Ckt | N | 2023
40383 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 65454 | 2023-03-14 | 1429 | 20230315 | 1321 | 2040459 | 1372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 181104 | 38.4488 | -122.1954 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045335 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | Yes | No | 1825329 | 0 | EPSS Ckt | N | 2023 | B AND GRD
40387 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 639467 | 2023-03-14 | 1533 | 20230315 | 1922 | 2044873 | 1669 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 26704 | 38.6258 | -122.2907 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045920 | OH | Sus | 0 | NORTH COAST | MAR | Multi-Fault | 0 | No | Yes | No | 1825843 | 0 | EPSS Ckt | N | 2023
40540 | NORTH BAY | SILVERADO | SILVERADO-2105 | 43432105 | SWITCH | 3245 | 2023-03-30 | 2131 | 20230331 | 219 | 2074841 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 58752 | 38.7041 | -122.4208 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055254 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1832047 | 0 | EPSS Ckt | N | 2023
40540 | NORTH BAY | SILVERADO | SILVERADO-2105 | 43432105 | SWITCH | 3245 | 2023-03-30 | 2131 | 20230331 | 219 | 2074841 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 58752 | 38.7041 | -122.4208 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0055254 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1832047 | 0 | EPSS Ckt | N | 2023
40551 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 7339 | 2023-04-02 | 2017 | 20230402 | 2245 | 2077655 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 444 | 38.698 | -122.4042 | No | Clear;32-90 F |  |  | 23-0056088 | OH | Sus | 0 | NORTH COAST | APR | Line to Line | 0 | No | No | No | 1832680 | 0 | EPSS Ckt | N | 2023
40571 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2023-04-08 | 451 | 20230408 | 1917 | 2083014 | 866 | Distribution Circuit | 3rd Party | Vehicle | 346 | 210092 | 38.6152 | -122.4293 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0058729 | OH | Sus | 31641664 | NORTH COAST | APR | Three Phase Fault | 0 | No | Yes | No | 1834168 | 0 | EPSS Ckt | N | 2023 | A/B/C & GRD TARGETS
40592 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 2843 | 2023-04-15 | 617 | 20230415 | 901 | 2089044 | 164 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 35 | 5798 | 38.4825 | -122.1594 | No | Clear;32-90 F |  |  | 23-0061320 | OH | Sus | 0 | NORTH COAST | APR | Line to Ground | 0 | No | No | No | 1835996 | 1 | EPSS Ckt | N | 2023
40623 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 1780 | 2023-04-26 | 1403 | 20230426 | 1424 | 2097655 | 21 | Distribution Circuit | Vegetation | Tree - branch fell on line | 197 | 3851 | 38.5061 | -122.1872 | No | Clear;32-90 F | Recloser | Normal | 23-0065071 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1838771 | 0 | EPSS Ckt | N | 2023 | NONE
40669 | NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | TRANSFORMER | T5363 | 2023-05-08 | 2030 | 20230509 | 303 | 2108170 | 393 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 10 | 3354 | 38.4422 | -122.3047 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0069736 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1841802 | 0 | EPSS Ckt | N | 2023
40676 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 5769 | 2023-05-11 | 1928 | 20230512 | 127 | 2110683 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 359 | 38.5983 | -122.4578 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0071132 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1842664 | 0 | EPSS Ckt | N | 2023
40689 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2023-05-16 | 950 | 20230516 | 1103 | 2113905 | 73 | Distribution Circuit | Equipment Failure/Involved | Overhead | 278 | 20294 | 38.5063 | -122.202 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0072231 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1843594 | 0 | EPSS Ckt | N | 2023 | N/A
40733 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218723535275 | 2023-06-02 | 1031 | 20230602 | 1545 | 2127333 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 314 | 38.6339 | -122.4472 | No | Clear;32-90 F | Transformer | Leaking | 23-0078240 | OH | Sus | 0 | NORTH COAST | JUN | Line to Ground | 0 | No | No | No | 1847565 | 0 | EPSS Ckt | N | 2023
40777 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 2023-06-17 | 529 | 20230617 | 1121 | 2139142 | 352 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 134 | 32997 | 38.573 | -122.2439 | No | Clear;32-90 F |  |  | 23-0083325 | OH | Sus | 0 | NORTH COAST | JUN | Line to Line | 0 | No | No | No | 1851248 | 0 | EPSS Ckt | Y | 2023 | B & C PHSE
40795 | NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | TRANSFORMER | 219160527970 | 2023-06-19 | 2007 | 20230620 | 800 | 2140755 | 713 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 713 | 38.4342 | -122.294 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0083728 | OH | Sus | 0 | NORTH COAST | JUN | Line to Ground | 0 | No | Yes | No | 1851692 | 0 | EPSS Ckt | N | 2023
40810 | NORTH BAY | NORTH BAY | STAFFORD-1101 | 43201101 | FUSE | 6141 | 2023-06-25 | 858 | 20230625 | 1404 | 2145218 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 13770 | 38.1233 | -122.5961 | No | Overcast;32-90 F |  |  | 23-0085435 | OH | Sus | 0 | NORTH COAST | JUN | Line to Line | 0 | No | No | No | 1852984 | 0 | EPSS Ckt | N | 2023
40816 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218693534735 | 2023-06-27 | 2257 | 20230627 | 2338 | 2147373 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 38.6199 | -122.4561 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0086339 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1853576 | 0 | EPSS Ckt | N | 2023
40860 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 9671 | 2023-07-07 | 1910 | 20230708 | 618 | 2156568 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3340 | 38.4818 | -122.1586 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090019 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1855767 | 0 | EPSS Ckt | N | 2023
40877 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218708533131 | 2023-07-13 | 2230 | 20230714 | 432 | 2162062 | 362 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 724 | 38.5755 | -122.4528 | No | Clear;32-90 F | Insulator | Broken | 23-0092090 | OH | Sus | 0 | NORTH COAST | JUL | Force Out | 0 | No | No | No | 1857280 | 0 | EPSS Ckt | N | 2023
40884 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2023-07-16 | 1530 | 20230717 | 420 | 2164380 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 58718 | 38.4456 | -122.196 | No | Partly Cloudy;Above 90 | Conductor- Overhead | Broken- wire on ground | 23-0092844 | OH | Sus | 31655763 | NORTH COAST | JUL | Multi-Fault | 0 | Yes | Yes | No | 1857877 | 0 | EPSS Ckt | Y | 2023 | B PHASE & GRD
40889 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2023-07-19 | 546 | 20230719 | 751 | 2167394 | 125 | Distribution Circuit | Animal | Bird found | 278 | 34750 | 38.5063 | -122.202 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0093997 | OH | Sus | 0 | NORTH COAST | JUL | Line to Line | 0 | No | No | No | 1858634 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
40933 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 4431 | 2023-08-01 | 814 | 20230801 | 1033 | 2179401 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1096 | 38.6012 | -122.4624 | No | Partly Cloudy;32-90 F |  |  | 23-0099023 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1862113 | 0 | EPSS Ckt | N | 2023
40967 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 5301 | 2023-08-08 | 1420 | 20230808 | 1441 | 2185908 | 21 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 21 | 38.6176 | -122.4258 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0101843 | OH | Sus | 0 | NORTH COAST | AUG | Force Out | 0 | No | No | No | 1864076 | 0 | EPSS Ckt | N | 2023
40970 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | TRANSFORMER | 219640030135 | 2023-08-09 | 1406 | 20230809 | 2332 | 2186812 | 566 | Transformer only | Vegetation | Tree - branch fell on line | 16 | 9056 | 38.4945 | -122.1273 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0102377 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1864411 | 0 | EPSS Ckt | N | 2023
40976 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 666 | 2023-08-10 | 1059 | 20230811 | 1910 | 2187716 | 1931 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1200 | 548440 | 38.5091 | -122.2125 | No | Clear;32-90 F |  |  | 23-0102654 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1864665 | 0 | EPSS Ckt | Y | 2023 | C PH/GRD
40993 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2023-08-15 | 741 | 20230815 | 1228 | 2191280 | 287 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 505 | 144935 | 38.4456 | -122.196 | No | Clear;32-90 F |  |  | 23-0104376 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1865759 | 0 | EPSS Ckt | Y | 2023 | B PH & C PH
41000 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 4369 | 2023-08-16 | 649 | 20230816 | 848 | 2192384 | 119 | Distribution Circuit | Company Initiated | Improper Construction | 9 | 1071 | 38.467 | -122.228 | No | Clear;32-90 F | Jumper | Normal | 23-0104951 | OH | Sus | 0 | NORTH COAST | AUG | Open Circuit | 0 | No | No | No | 1866158 | 0 | EPSS Ckt | N | 2023
41070 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2023-09-01 | 1402 | 20230902 | 1718 | 2208106 | 913 | Distribution Circuit | Equipment Failure/Involved | Underground | 277 | 122013 | 38.5063 | -122.202 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 23-0111888 | UG | Sus | 35486224 | NORTH COAST | SEP | Force Out | 0 | No | No | No | 1870847 | 0 | EPSS Ckt | Y | 2023 | NONE
41111 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218812234632 | 2023-09-14 | 2056 | 20230914 | 2346 | 2219192 | 170 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 170 | 38.6163 | -122.417 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0116903 | OH | Sus | 0 | NORTH COAST | SEP | Force Out | 0 | No | No | No | 1874125 | 0 | EPSS Ckt | N | 2023
41118 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2023-09-17 | 907 | 20230917 | 1155 | 2220973 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 206 | 34608 | 38.5063 | -122.202 | No | Partly Cloudy;32-90 F |  |  | 23-0117538 | OH | Sus | 0 | NORTH COAST | SEP | Line to Ground | 0 | No | No | No | 1874624 | 0 | EPSS Ckt | Y | 2023 | B/GRD
41145 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2023-09-27 | 643 | 20230927 | 1154 | 2228199 | 296 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 505 | 128216 | 38.4456 | -122.196 | No | Clear;32-90 F |  |  | 23-0121273 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1877114 | 0 | EPSS Ckt | Y | 2023 | B & C
41189 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218685533044 | 2023-10-07 | 1000 | 20231007 | 1012 | 2237497 | 12 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 24 | 38.5733 | -122.4614 | No | Clear;32-90 F | Secondary | Broken | 23-0125708 | OH | Sus | 0 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1880191 | 0 | EPSS Ckt | N | 2023
41194 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 65454 | 2023-10-08 | 652 | 20231008 | 1043 | 2238119 | 231 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 30723 | 38.4488 | -122.1954 | No | Clear;32-90 F |  |  | 23-0125836 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1880297 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
41226 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2023-10-17 | 702 | 20231017 | 1611 | 2244946 | 549 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 504 | 145126 | 38.4456 | -122.196 | No | Clear;32-90 F |  |  | 23-0128952 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1882632 | 0 | EPSS Ckt | Y | 2023 | B/C PHASE
41244 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2023-10-22 | 818 | 20231022 | 1213 | 2248796 | 235 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 346 | 70216 | 38.6152 | -122.4293 | No | Overcast-Fog;32-90 F |  |  | 23-0131004 | OH | Sus | 0 | NORTH COAST | OCT | Line to Ground | 0 | No | No | No | 1883972 | 0 | EPSS Ckt | Y | 2023 | SGF
41260 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2023-10-27 | 2010 | 20231027 | 2250 | 2253736 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 276 | 44160 | 38.5063 | -122.202 | No | Clear;32-90 F |  |  | 23-0133441 | OH | Sus | 0 | NORTH COAST | OCT | None | 0 | No | No | No | 1885724 | 0 | EPSS Ckt | Y | 2023 | none
41274 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 65454 | 2023-10-30 | 2336 | 20231031 | 919 | 2256244 | 583 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 133 | 77421 | 38.4488 | -122.1954 | No | Partly Cloudy;32-90 F |  |  | 23-0134188 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1886368 | 0 | EPSS Ckt | Y | 2023 | B & C TARGETS- ABOVE MTT
41332 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 4569 | 2023-11-20 | 821 | 20231120 | 1800 | 2273937 | 579 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1158 | 38.61 | -122.4306 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0141244 | OH | Sus | 0 | NORTH COAST | NOV | Open Circuit | 0 | No | Yes | No | 1891898 | 0 | EPSS Ckt | N | 2023
41468 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 87875 | 2023-12-21 | 1410 | 20231221 | 1739 | 2297783 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 418 | 38.4708 | -122.2338 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0148488 | OH | Sus | 0 | NORTH COAST | DEC | Force Out | 0 | No | No | No | 1899483 | 0 | EPSS Ckt | N | 2023
41779 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN BET 7867 AND 76977 | 2024-02-04 | 1912 | 20240205 | 1216 | 2352125 | 1024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 127042 | 38.4527 | -122.2044 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021205 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | Yes | 1911033 | 0 | EPSS Ckt | N | 2024
41809 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 7511 | 2024-02-05 | 1235 | 20240207 | 2048 | 2359648 | 3373 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 40476 | 38.468 | -122.2295 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024506 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | Yes | No | 1913604 | 0 | EPSS Ckt | N | 2024
41857 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 2843 | 2024-02-07 | 1423 | 20240207 | 2253 | 2367669 | 510 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 27540 | 38.4825 | -122.1594 | No | Clear;32-90 F |  |  | 24-0024724 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1913766 | 0 | EPSS Ckt | N | 2024
41877 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 639467 | 2024-02-08 | 1900 | 20240208 | 1945 | 2370900 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 720 | 38.6258 | -122.2907 | No | Partly Cloudy;32-90 F |  |  | 24-0026565 | OH | Sus | 0 | NORTH COAST | FEB | Line to Line | 0 | No | No | No | 1915284 | 0 | EPSS Ckt | N | 2024
41892 | NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | JUMPER | WIRE DOWN @ CGC 219117027925 SOURCE SIDE | 2024-02-09 | 1559 | 20240210 | 1440 | 2372101 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12386 | 38.435 | -122.3089 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027166 | OH | Sus | 0 | NORTH COAST | FEB | Force Out | 0 | No | Yes | No | 1915687 | 0 | EPSS Ckt | N | 2024
41936 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-02-17 | 1720 | 20240218 | 1129 | 2379122 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 163531 | 38.6152 | -122.4293 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0030262 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1917544 | 0 | EPSS Ckt | N | 2024 | ABC TIME
41967 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2024-02-20 | 647 | 20240221 | 1208 | 2382431 | 1684 | Distribution Circuit | Vegetation | Tree - branch fell on line | 504 | 254435 | 38.4456 | -122.196 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 24-0031168 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1918266 | 0 | EPSS Ckt | N | 2024 | B- GRD TGT
41996 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | TRANSFORMER | 219196134355 | 2024-02-23 | 1027 | 20240223 | 1234 | 2386165 | 127 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 508 | 38.6094 | -122.2821 | No | Partly Cloudy;32-90 F | Fuse | Burned Open | 24-0033213 | OH | Sus | 0 | NORTH COAST | FEB | Line to Ground | 0 | No | No | No | 1919597 | 0 | EPSS Ckt | N | 2024
42031 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 5365 | 2024-03-01 | 2003 | 20240302 | 1300 | 2394628 | 1017 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 28 | 28476 | 38.6008 | -122.4605 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0036895 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1921885 | 0 | EPSS Ckt | N | 2024
42067 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 5859 | 2024-03-08 | 1615 | 20240308 | 1902 | 2400380 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 835 | 38.6172 | -122.4171 | No | Clear;32-90 F |  |  | 24-0040007 | OH | Sus | 0 | NORTH COAST | MAR | Line to Line | 0 | No | No | No | 1923626 | 0 | EPSS Ckt | N | 2024
42135 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 2691 | 2024-03-30 | 1158 | 20240330 | 1544 | 2419025 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3842 | 38.4468 | -122.1918 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0048761 | OH | Sus | 0 | NORTH COAST | MAR | Force Out | 0 | No | No | No | 1929606 | 0 | EPSS Ckt | N | 2024
42190 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 4369 | 2024-04-18 | 820 | 20240418 | 1025 | 2433978 | 125 | Distribution Circuit | Animal | Squirrel | 10 | 1250 | 38.467 | -122.228 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0056298 | OH | Sus | 0 | NORTH COAST | APR | Line to Line | 0 | No | No | No | 1934736 | 0 | EPSS Ckt | N | 2024
42202 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 1985 | 2024-04-24 | 1613 | 20240424 | 1648 | 2438370 | 35 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 630 | 38.483 | -122.1492 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0058640 | OH | Sus | 0 | NORTH COAST | APR | Force Out | 0 | No | No | No | 1936181 | 0 | EPSS Ckt | N | 2024
42236 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2024-05-04 | 654 | 20240504 | 852 | 2445543 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 281 | 33158 | 38.5063 | -122.202 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Insulator | Normal | 24-0061987 | OH | Sus | 0 | NORTH COAST | MAY | Line to Ground | 0 | No | No | No | 1938845 | 0 | EPSS Ckt | N | 2024 | B & GRD
42258 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 181979 | 2024-05-09 | 719 | 20240509 | 1247 | 2449425 | 328 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 984 | 38.6482 | -122.4699 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0064170 | OH | Sus | 0 | NORTH COAST | MAY | Force Out | 0 | No | No | No | 1940397 | 0 | EPSS Ckt | N | 2024
42317 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-05-30 | 409 | 20240530 | 527 | 2470513 | 78 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 26988 | 38.6152 | -122.4293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071191 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | No | No | No | 1945086 | 0 | EPSS Ckt | Y | 2024 | A-B INST
42320 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-05-30 | 1024 | 20240530 | 1908 | 2470792 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 120392 | 38.6152 | -122.4293 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0071335 | OH | Sus | 0 | NORTH COAST | MAY | Line to Line | 0 | Yes | No | No | 1945249 | 0 | EPSS Ckt | Y | 2024 | A-B- INST TGTS
42423 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218690733294 | 2024-06-20 | 2132 | 20240620 | 2154 | 2491085 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 88 | 38.5799 | -122.4592 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0078836 | OH | Sus | 0 | NORTH COAST | JUN | Force Out | 0 | No | No | No | 1950667 | 0 | EPSS Ckt | N | 2024
42506 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | FUSE | 6849 | 2024-07-06 | 1956 | 20240706 | 2141 | 2508328 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 220 | 12595 | 38.5725 | -122.4562 | No | Clear;Above 90 |  |  | 24-0084730 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | No | No | 1954632 | 1 | EPSS Ckt | Y | 2024
42509 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 959428 | 2024-07-07 | 1451 | 20240708 | 116 | 2509023 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 29216 | 38.5712 | -122.4534 | No | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 24-0084884 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | Yes | No | 1954759 | 0 | EPSS Ckt | Y | 2024 | C
42527 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 3055 | 2024-07-11 | 933 | 20240711 | 1929 | 2513555 | 596 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1204 | 106256 | 38.4475 | -122.1948 | No | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on object | 24-0086608 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | Yes | Yes | 1955899 | 0 | EPSS Ckt | N | 2024
42587 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 959428 | 2024-07-28 | 1907 | 20240729 | 551 | 2528780 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 41404 | 38.5712 | -122.4534 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0092919 | OH | Sus | 0 | NORTH COAST | JUL | Line to Ground | 0 | No | Yes | No | 1960118 | 0 | EPSS Ckt | Y | 2024 | C GRD
42633 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 2024-08-07 | 1432 | 20240807 | 1610 | 2536883 | 98 | Distribution Circuit | Animal | Other | 136 | 13328 | 38.573 | -122.2439 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0096878 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1962760 | 0 | EPSS Ckt | Y | 2024 | A & B
42636 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 7641 | 2024-08-07 | 1628 | 20240807 | 1702 | 2536986 | 34 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 1768 | 38.6059 | -122.2797 | No | Clear;Above 90 |  |  | 24-0096950 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1962783 | 0 | EPSS Ckt | N | 2024
42641 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 2024-08-08 | 726 | 20240808 | 1039 | 2537349 | 193 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 124 | 15881 | 38.573 | -122.2439 | No | Clear;32-90 F |  |  | 24-0097089 | OH | Sus | 0 | NORTH COAST | AUG | None | 0 | No | No | No | 1962864 | 0 | EPSS Ckt | Y | 2024 | A & C PHASE INST
42645 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 639467 | 2024-08-08 | 1647 | 20240808 | 1654 | 2538160 | 7 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 112 | 38.6258 | -122.2907 | No | Clear;Above 90 |  |  | 24-0097420 | OH | Sus | 0 | NORTH COAST | AUG | Line to Line | 0 | No | No | No | 1963068 | 0 | EPSS Ckt | N | 2024
42714 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | JUMPER | OPEN FLYERS 1 POLE E/OF CGC: 219418530690 | 2024-08-28 | 1632 | 20240828 | 1753 | 2554177 | 81 | Distribution Circuit | Animal | Other | 5 | 405 | 38.509 | -122.2022 | No | Clear;32-90 F | Jumper | Normal | 24-0104353 | OH | Sus | 0 | NORTH COAST | AUG | None | 0 | No | No | No | 1967930 | 0 | EPSS Ckt | N | 2024
42746 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-09-10 | 908 | 20240910 | 1143 | 2564426 | 155 | Distribution Circuit | Equipment Failure/Involved | Underground | 347 | 53785 | 38.6152 | -122.4293 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0109090 | UG | Sus | 0 | NORTH COAST | SEP | Three Phase Fault | 0 | No | No | No | 1970958 | 0 | EPSS Ckt | Y | 2024 | A B C
42754 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2024-09-11 | 627 | 20240911 | 1450 | 2565034 | 503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 504 | 202418 | 38.4456 | -122.196 | No | Clear;32-90 F |  |  | 24-0109447 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1971109 | 0 | EPSS Ckt | Y | 2024 | LR 718 = AB / LR 37384 = BC
42766 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-09-12 | 1900 | 20240912 | 2222 | 2566927 | 202 | Distribution Circuit | Animal | Bird found | 347 | 70094 | 38.6152 | -122.4293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0110516 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1971733 | 0 | EPSS Ckt | Y | 2024 | A/C PHASE
42788 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2024-09-19 | 1347 | 20240919 | 1630 | 2572620 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 504 | 82152 | 38.4456 | -122.196 | No | Clear;32-90 F |  |  | 24-0113131 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1973583 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
42794 | NORTH BAY | SILVERADO | PUEBLO-1105 | 43291105 | TRANSFORMER | 219156027955 | 2024-09-21 | 1909 | 20240922 | 459 | 2574234 | 590 | Transformer only | Unknown Cause | Patrol - not conducted | 2 | 1180 | 38.434 | -122.2955 | No | Clear;32-90 F |  |  | 24-0114071 | OH | Sus | 31709490 | NORTH COAST | SEP | None | 0 | No | No | No | 1974136 | 0 | EPSS Ckt | N | 2024
42820 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | TRANSFORMER | 219360729233 | 2024-09-26 | 855 | 20240926 | 1113 | 2578219 | 138 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 276 | 38.4692 | -122.2243 | No | Clear;32-90 F | Fuse | Burned Open | 24-0115863 | OH | Sus | 0 | NORTH COAST | SEP | Line to Ground | 0 | No | No | No | 1975561 | 0 | EPSS Ckt | N | 2024
42826 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218865033017 | 2024-09-27 | 2003 | 20240927 | 2103 | 2579707 | 60 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 60 | 38.5728 | -122.3976 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0116833 | OH | Sus | 35584207 | NORTH COAST | SEP | Force Out | 0 | No | No | No | 1976033 | 0 | EPSS Ckt | N | 2024
42832 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-09-28 | 1933 | 20240929 | 1231 | 2580322 | 1018 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 347 | 353246 | 38.6152 | -122.4293 | No | Clear;32-90 F |  |  | 24-0116962 | OH | Sus | 0 | NORTH COAST | SEP | Line to Line | 0 | No | No | No | 1976249 | 0 | EPSS Ckt | Y | 2024 | B- C- 50 INST
42840 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218723933138 | 2024-09-30 | 2035 | 20240930 | 2133 | 2581760 | 58 | Transformer only | Equipment Failure/Involved | Overhead | 6 | 348 | 38.5754 | -122.4472 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0117540 | OH | Sus | 0 | NORTH COAST | SEP | Force Out | 0 | No | No | No | 1976674 | 0 | EPSS Ckt | N | 2024
42850 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 959428 | 2024-10-02 | 1833 | 20241002 | 1851 | 2584052 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 220 | 3960 | 38.5712 | -122.4534 | No | Clear;Above 90 | Recloser | Normal | 24-0118616 | OH | Sus | 0 | NORTH COAST | OCT | None | 0 | No | No | No | 1977396 | 0 | EPSS Ckt | Y | 2024 | INST
42872 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | TRANSFORMER | 219444528440 | 2024-10-06 | 1341 | 20241007 | 1123 | 2587393 | 1302 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1302 | 38.4469 | -122.1947 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0119953 | OH | Sus | 0 | NORTH COAST | OCT | Line to Ground | 0 | No | No | No | 1978204 | 0 | EPSS Ckt | N | 2024
42887 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-10-07 | 1931 | 20241008 | 1012 | 2588916 | 881 | Distribution Circuit | Company Initiated | Coordination failure | 347 | 305707 | 38.6152 | -122.4293 | No | Clear;32-90 F | Recloser | Normal | 24-0120436 | OH | Sus | 0 | NORTH COAST | OCT | Line to Ground | 0 | No | No | No | 1978636 | 0 | EPSS Ckt | Y | 2024 | DCD
42894 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 666 | 2024-10-09 | 654 | 20241009 | 1220 | 2590204 | 326 | Distribution Circuit | Company Initiated | Personnel- company | 1200 | 200474 | 38.5091 | -122.2125 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0121000 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1979022 | 0 | EPSS Ckt | Y | 2024 | B & C
42944 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2024-10-17 | 1832 | 20241019 | 1510 | 2597722 | 2678 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 229 | 613262 | 38.4456 | -122.196 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0123825 | OH | Sus | 8216649 | NORTH COAST | OCT | Force Out | 0 | No | No | No | 1981485 | 0 | EPSS Ckt | N | 2024 | NONE
42992 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 65454 | 2024-10-29 | 710 | 20241029 | 721 | 2606807 | 11 | Distribution Circuit | Company Initiated | Coordination failure | 61 | 671 | 38.4488 | -122.1954 | No | Clear;32-90 F | Recloser | Normal | 24-0128829 | OH | Sus | 0 | NORTH COAST | OCT | Line to Line | 0 | No | No | No | 1984307 | 0 | EPSS Ckt | Y | 2024 | B-C- ABOVE MTT
43009 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-11-03 | 1051 | 20241103 | 1613 | 2612399 | 322 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 347 | 111734 | 38.6152 | -122.4293 | No | Clear;32-90 F |  |  | 24-0131117 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | Yes | No | No | 1985988 | 0 | EPSS Ckt | Y | 2024 | BC I OC TGT
43011 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 106272 | 2024-11-04 | 641 | 20241104 | 1246 | 2612909 | 365 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 143 | 52195 | 38.617 | -122.4242 | No | Clear;32-90 F |  |  | 24-0131237 | OH | Sus | 31716621 | NORTH COAST | NOV | None | 0 | No | No | No | 1986075 | 0 | EPSS Ckt | Y | 2024 | A & B INST
43030 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 959428 | 2024-11-05 | 1934 | 20241107 | 1729 | 2614954 | 2755 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 269 | 609344 | 38.5712 | -122.4534 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131264 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986791 | 0 | EPSS Ckt | N | 2024 | N/A
43031 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-11-05 | 1934 | 20241107 | 1740 | 2614957 | 2766 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 347 | 959802 | 38.6152 | -122.4293 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131264 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986792 | 0 | EPSS Ckt | N | 2024 | N/A
43032 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 106272 | 2024-11-05 | 1934 | 20241107 | 1748 | 2614960 | 2774 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 143 | 396682 | 38.617 | -122.4242 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131264 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986795 | 0 | EPSS Ckt | N | 2024 | N/A
43036 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | OCB | 1101/2 | 2024-11-05 | 1936 | 20241107 | 1041 | 2614776 | 2345 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 4690 | 38.5093 | -122.2147 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986726 | 0 | EPSS Ckt | N | 2024 | n/a
43037 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 654 | 2024-11-05 | 1936 | 20241107 | 1118 | 2614782 | 2382 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 21 | 50022 | 38.5112 | -122.2134 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986731 | 0 | EPSS Ckt | N | 2024 | NONE
43038 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 909026 | 2024-11-05 | 1936 | 20241107 | 1131 | 2614792 | 2395 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 42 | 100590 | 38.5296 | -122.2242 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986733 | 0 | EPSS Ckt | N | 2024 | NONE
43039 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 2024-11-05 | 1936 | 20241107 | 1143 | 2614796 | 2407 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 91 | 219037 | 38.573 | -122.2439 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986735 | 0 | EPSS Ckt | N | 2024 | NONE
43040 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 256640 | 2024-11-05 | 1936 | 20241107 | 1203 | 2614800 | 2427 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 36 | 87372 | 38.6063 | -122.2807 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986738 | 0 | EPSS Ckt | N | 2024 | NONE
43042 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 666 | 2024-11-05 | 1936 | 20241107 | 1446 | 2614811 | 2590 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 84 | 217560 | 38.5091 | -122.2125 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986745 | 0 | EPSS Ckt | N | 2024 | NONE
43043 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 52910 | 2024-11-05 | 1936 | 20241107 | 1450 | 2614823 | 2594 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 281 | 728914 | 38.5063 | -122.202 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986747 | 0 | EPSS Ckt | N | 2024 | NONE
43044 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 93384 | 2024-11-05 | 1936 | 20241107 | 1454 | 2614834 | 2598 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 147 | 381906 | 38.4785 | -122.188 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986749 | 0 | EPSS Ckt | N | 2024 | NONE
43045 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 1780 | 2024-11-05 | 1936 | 20241107 | 1504 | 2614838 | 2608 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 54 | 140832 | 38.5063 | -122.1872 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986750 | 0 | EPSS Ckt | N | 2024 | NONE
43046 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 65454 | 2024-11-05 | 1936 | 20241107 | 1509 | 2614842 | 2613 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 61 | 159393 | 38.4488 | -122.1954 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986752 | 0 | EPSS Ckt | N | 2024 | NONE
43048 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 2024-11-05 | 1936 | 20241107 | 1519 | 2614849 | 2623 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 229 | 600667 | 38.4456 | -122.196 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131804 | OH | Sus | 0 | NORTH COAST | NOV | Force Out | 0 | No | No | No | 1986756 | 0 | EPSS Ckt | N | 2024 | NONE
43097 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | RECLOSER | 666 | 2024-11-09 | 619 | 20241109 | 1542 | 2619440 | 563 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1205 | 360155 | 38.5091 | -122.2125 | No | Partly Cloudy;32-90 F |  |  | 24-0133761 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | No | No | 1987989 | 0 | EPSS Ckt | Y | 2024 | A/C INST OC
43103 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-11-11 | 700 | 20241111 | 729 | 2620475 | 29 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 347 | 10063 | 38.6152 | -122.4293 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0134023 | OH | Sus | 0 | NORTH COAST | NOV | Line to Line | 0 | No | No | No | 1988303 | 0 | EPSS Ckt | N | 2024 | B-C INST
43248 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | TRANSFORMER | 218791534780 | 2024-12-05 | 1053 | 20241205 | 1602 | 2644964 | 309 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 309 | 38.6205 | -122.424 | No | Clear;32-90 F |  |  | 24-0143085 | OH | Sus | 0 | NORTH COAST | DEC | None | 0 | No | No | No | 1994878 | 0 | EPSS Ckt | N | 2024
43251 | NORTH BAY | NORTH BAY | STAFFORD-1101 | 43201101 | TRANSFORMER | 313994559820 | 2024-12-06 | 2029 | 20241207 | 57 | 2646218 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 10 | 2680 | 38.1245 | -122.5891 | No | Clear;32-90 F | Secondary | Broken | 24-0143491 | OH | Sus | 0 | NORTH COAST | DEC | Force Out | 0 | No | No | No | 1995220 | 0 | EPSS Ckt | N | 2024
43286 | NORTH BAY | SILVERADO | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 2024-12-13 | 2354 | 20241214 | 1227 | 2652645 | 753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 347 | 176801 | 38.6152 | -122.4293 | No | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145004 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | Yes | No | 1997309 | 0 | EPSS Ckt | N | 2024 | B & TIME
43302 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 2843 | 2024-12-14 | 652 | 20241214 | 954 | 2653754 | 182 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 46 | 8372 | 38.4825 | -122.1594 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145266 | OH | Sus | 0 | NORTH COAST | DEC | Line to Ground | 0 | No | No | No | 1997576 | 0 | EPSS Ckt | N | 2024
43423 | NORTH BAY | SILVERADO | MONTICELLO-1101 | 43051101 | FUSE | 9361 | 2024-12-20 | 127 | 20241220 | 1148 | 2666327 | 621 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 5 | 2945 | 38.4693 | -122.1424 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0147183 | OH | Sus | 0 | NORTH COAST | DEC | Line to Line | 0 | No | No | No | 1999922 | 0 | EPSS Ckt | N | 2024
43466 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 310456 | 2023-01-03 | 1132 | 20230103 | 1339 | 1911411 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 2413 | 39.8583 | -121.66 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0005145 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1795691 | 0 | EPSS Ckt | N | 2023 | NONE
43478 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 2023-01-04 | 1955 | 20230105 | 1050 | 1917891 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 904 | 263416 | 40.351 | -121.7811 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 23-0006523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1796821 | 0 | EPSS Ckt | N | 2023 | A B- GRD
43479 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | FUSE | 9301 | 2023-01-04 | 1955 | 20230106 | 1203 | 1919571 | 2408 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53711 | 40.3447 | -121.761 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | Yes | No | 1797105 | 0 | EPSS Ckt | N | 2023
43481 | NORTH VALLEY | PARADISE | PARADISE-1103 | 102831103 | FUSE | 499325 | 2023-01-04 | 2003 | 20230105 | 1430 | 1922042 | 1107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 27675 | 39.7459 | -121.644 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0007348 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1797608 | 0 | EPSS Ckt | N | 2023
43486 | NORTH VALLEY | CHICO | BUTTE 1105 | 103081105 | FUSE | 2511 | 2023-01-04 | 2011 | 20230107 | 1027 | 1918070 | 3736 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7472 | 39.7857 | -121.6586 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797706 | 0 | EPSS Ckt | N | 2023
43489 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | OCB | 1102/2 | 2023-01-04 | 2017 | 20230107 | 1613 | 1918492 | 4076 | Distribution Circuit | Vegetation | Tree - fell into line | 724 | 1347530 | 39.8716 | -121.6114 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006819 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | Yes | No | 1797121 | 0 | EPSS Ckt | N | 2023 | NA
43499 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-01-04 | 2032 | 20230106 | 1852 | s1796878 | 2780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 510970 | 39.8787 | -121.6118 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006490 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1796878 | 0 | EPSS Ckt | N | 2023 | A PHASE - TIME OC - SGF
43502 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | JUMPER | OJ'S 6 LD SIDE OF 310456 | 2023-01-04 | 2042 | 20230105 | 2042 | 1922267 | 1440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 5760 | 39.8583 | -121.6676 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007441 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1797679 | 0 | EPSS Ckt | N | 2023
43529 | NORTH VALLEY | PARADISE | ORO FINO 1101 | 103031101 | OCB | 1101/2 | 2023-01-04 | 2236 | 20230105 | 1835 | 1919508 | 1199 | Distribution Circuit | Vegetation | Tree - fell into line | 1700 | 1964849 | 39.8716 | -121.6113 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0006798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797099 | 0 | EPSS Ckt | N | 2023 | C GRD INST
43533 | NORTH VALLEY | PARADISE | BIG BEND 1101 | 103751101 | FUSE | 17253 | 2023-01-04 | 2245 | 20230107 | 1327 | 1919520 | 3762 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 41382 | 39.7192 | -121.4875 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007562 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1797775 | 0 | EPSS Ckt | N | 2023
43562 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | FUSE | 799 | 2023-01-05 | 952 | 20230105 | 1036 | 1921550 | 44 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 616 | 39.5898 | -121.2768 | Yes | Clear;32-90 F |  |  | 23-0007225 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797499 | 0 | EPSS Ckt | N | 2023
43565 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2443 | 2023-01-05 | 1245 | 20230106 | 1532 | 1922270 | 1607 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 14463 | 40.5975 | -122.5436 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007442 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | Yes | No | 1797680 | 0 | EPSS Ckt | N | 2023
43581 | NORTH VALLEY | CHICO | NOTRE DAME 1104 | 102041104 | RECLOSER | 310456 | 2023-01-05 | 2124 | 20230106 | 1504 | 1923910 | 1060 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 20140 | 39.8583 | -121.66 | Yes | Clear;32-90 F |  |  | 23-0008442 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798388 | 0 | EPSS Ckt | N | 2023 | A PHASE PROTECTION TRIP
43625 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 16617 | 2023-01-08 | 151 | 20230108 | 1045 | 1933178 | 534 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1602 | 39.8797 | -121.6625 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010031 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1799876 | 0 | EPSS Ckt | N | 2023
43633 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | FUSE | 696787 | 2023-01-08 | 253 | 20230110 | 1707 | 1933946 | 3734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 7468 | 39.5513 | -121.3419 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1800113 | 0 | EPSS Ckt | N | 2023
43644 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | JUMPER | WIRE DOWN | 2023-01-08 | 812 | 20230109 | 1223 | 1932893 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16307 | 39.7998 | -121.655 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0009940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Open Circuit | 0 | No | No | No | 1799790 | 0 | EPSS Ckt | N | 2023
43669 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRANSFORMER | 220970777314 | 2023-01-10 | 253 | 20230110 | 1945 | 1946171 | 1012 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 4048 | 39.7889 | -121.6567 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802458 | 0 | EPSS Ckt | N | 2023
43673 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | RECLOSER | 2511 | 2023-01-10 | 430 | 20230110 | 1801 | 1942126 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 70691 | 39.7857 | -121.6586 | Yes | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011867 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1801634 | 0 | EPSS Ckt | N | 2023 | A & GRD
43681 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 2023-01-10 | 1119 | 20230111 | 1126 | 1944782 | 1447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 748 | 871441 | 40.351 | -121.7811 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802039 | 0 | EPSS Ckt | N | 2023 | A PHASE GRD
43689 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 38698 | 2023-01-10 | 1951 | 20230111 | 1254 | 1946446 | 1023 | Distribution Circuit | Environmental/External | Ice or snow | 313 | 115479 | 40.0372 | -121.6183 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Together | 23-0012975 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802538 | 0 | EPSS Ckt | N | 2023 | A & C TGT'S
43698 | NORTH VALLEY | SHASTA | JESSUP 1101 | 103441101 | FUSE | 10205 | 2023-01-11 | 1955 | 20230112 | 434 | 1949016 | 519 | Distribution Circuit | Equipment Failure/Involved | Underground | 5 | 2595 | 40.4782 | -122.4643 | No | Clear;32-90F | Elbow | Failed/Faulted | 23-0014214 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1803566 | 0 | EPSS Ckt | N | 2023
43708 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | FUSE | 2243 | 2023-01-14 | 348 | 20230114 | 1839 | 1952763 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 50380 | 40.886 | -122.3867 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1804679 | 0 | EPSS Ckt | N | 2023
43711 | NORTH VALLEY | SHASTA | FRENCH GULCH 1101 | 103381101 | TRIP-SAVER | 2905 | 2023-01-14 | 755 | 20230114 | 2300 | 1953067 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13370 | 40.7197 | -122.6293 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1804876 | 0 | EPSS Ckt | N | 2023 | A & C
43713 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 2023-01-14 | 801 | 20230114 | 1234 | 1953151 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 45181 | 40.6166 | -122.4958 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0015891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804726 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
43769 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | OTHER | WIRE DOWN HOT | 2023-01-18 | 2140 | 20230119 | 1808 | 1961535 | 1228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 541 | 24346 | 39.5463 | -121.2833 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0018628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1806684 | 0 | EPSS Ckt | N | 2023
43772 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-01-19 | 846 | 20230119 | 1606 | 1961900 | 440 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 7 | 3080 | 40.6669 | -122.6336 | No | Clear;32-90F | Conductor- Overhead | Contaminated | 23-0018706 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806750 | 0 | EPSS Ckt | N | 2023 | NA
43776 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-01-20 | 811 | 20230120 | 1539 | 1962997 | 448 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 7 | 3136 | 40.6669 | -122.6336 | No | Clear;32-90F | Circuit Breaker | Normal | 23-0019240 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1806983 | 0 | EPSS Ckt | N | 2023 | NA
43787 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 195987 | 2023-01-21 | 1240 | 20230121 | 1300 | 1964049 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 40 | 39.7915 | -121.5059 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019729 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807202 | 0 | EPSS Ckt | N | 2023
43789 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | RECLOSER | 859138 | 2023-01-22 | 535 | 20230122 | 707 | 1964461 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 385 | 35396 | 39.5749 | -121.3055 | No | Clear;32-90 F | Recloser | Malfunctioning | 23-0019820 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1807279 | 0 | EPSS Ckt | N | 2023 | NONE
43790 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-01-22 | 803 | 20230122 | 1626 | 1964501 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3521 | 40.6669 | -122.6336 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0019828 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807285 | 0 | EPSS Ckt | N | 2023 | NONE
43792 | NORTH VALLEY | PARADISE | BUCKS CREEK-1103 | 102211103 | RECLOSER | BUCKS CREEK TPG LR | 2023-01-22 | 1221 | 20230123 | 1053 | 1964715 | 1352 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 333 | 429088 | 39.9115 | -121.3268 | No | Clear;Below 32 F |  |  | 23-0019868 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1807312 | 0 | EPSS Ckt | N | 2023 | NONE
43795 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-01-23 | 816 | 20230123 | 1519 | 1965434 | 423 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 7 | 2961 | 40.6669 | -122.6336 | No | Clear;32-90F | Other | Normal | 23-0020047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807464 | 0 | EPSS Ckt | N | 2023 | NONE
43802 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-01-24 | 803 | 20230124 | 1139 | 1966553 | 216 | Distribution Circuit | Company Initiated | Other Circuits | 7 | 1512 | 40.6669 | -122.6336 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020564 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807720 | 0 | EPSS Ckt | N | 2023 | NONE
43805 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | JUMPER | OJ'S 2 SS/OF CGC 119098355035 | 2023-01-25 | 709 | 20230125 | 1620 | 1967546 | 551 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1 | 551 | 40.8442 | -122.3259 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0021022 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1807988 | 0 | EPSS Ckt | N | 2023
43831 | NORTH VALLEY | SHASTA | PIT NO 5 1101 | 101321101 | RECLOSER | 1658 | 2023-01-29 | 1509 | 20230130 | 259 | 1971015 | 710 | Distribution Circuit | 3rd Party | Customer Equipment | 135 | 29793 | 40.9921 | -121.9718 | No | Clear;32-90 F | Recloser | Normal | 23-0022739 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1808938 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
43834 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-01-29 | 2313 | 20230130 | 1707 | 1971276 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 144802 | 39.7407 | -121.4962 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0022788 | OH | Sus | 31635982 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1808989 | 0 | EPSS Ckt | N | 2023 | A & GRD
43837 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 417066 | 2023-01-30 | 753 | 20230130 | 804 | 1971418 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 17 | 187 | 40.6627 | -122.4938 | No | Clear;32-90F |  |  | 23-0022824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1809027 | 0 | EPSS Ckt | N | 2023 | A & C
43843 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-01-30 | 1842 | 20230131 | 1120 | 1972260 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 17475 | 39.7407 | -121.4962 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0023196 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1809272 | 0 | EPSS Ckt | N | 2023 | NONE
43899 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 908917 | 2023-02-10 | 821 | 20230210 | 1101 | 1981479 | 160 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 160 | 39.7273 | -121.4831 | No | Clear;32-90F | Jumper | Broken | 23-0027397 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1812052 | 0 | EPSS Ckt | N | 2023
43959 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | TRANSFORMER | 118925856594 | 2023-02-20 | 1544 | 20230220 | 2328 | 1989561 | 464 | Transformer only | Equipment Failure/Involved | Electrical Overload | 3 | 1392 | 40.8861 | -122.3896 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0030718 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1814494 | 0 | EPSS Ckt | N | 2023
43999 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 17257 | 2023-02-22 | 1232 | 20230222 | 1905 | 1997582 | 393 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 393 | 39.7256 | -121.511 | No | Strong Winds; | Conductor- Overhead | Normal | 23-0032343 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815848 | 0 | EPSS Ckt | N | 2023
44020 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-02-24 | 8 | 20230224 | 52 | 2001144 | 44 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 115 | 4849 | 40.9921 | -121.9718 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0033514 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816546 | 0 | EPSS Ckt | Y | 2023 | A B
44025 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 2023-02-24 | 105 | 20230227 | 1911 | 2001523 | 5054 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 1560301 | 40.8524 | -122.3324 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816582 | 0 | EPSS Ckt | N | 2023 | A- GRD- SGF
44029 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 16385 | 2023-02-24 | 152 | 20230226 | 1843 | 2009209 | 3891 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15564 | 39.8792 | -121.6919 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035443 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818291 | 0 | EPSS Ckt | N | 2023
44031 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 308298 | 2023-02-24 | 156 | 20230226 | 1326 | 2001705 | 3570 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 103530 | 39.8338 | -121.6933 | Yes | Partly Cloudy-Rain-Strong Winds;32-90 F |  |  | 23-0033584 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816620 | 0 | EPSS Ckt | N | 2023 | A & B
44033 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | JUMPER | OJ @ CGC 220908680248 | 2023-02-24 | 158 | 20230226 | 1901 | 2009379 | 3903 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19515 | 39.8695 | -121.6769 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0035492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818339 | 0 | EPSS Ckt | N | 2023
44036 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 9731 | 2023-02-24 | 245 | 20230225 | 1844 | 2006509 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 33586 | 39.8725 | -121.6799 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0034446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1817299 | 0 | EPSS Ckt | N | 2023
44039 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | JUMPER | OJ 1 SS OF 4817 | 2023-02-24 | 306 | 20230226 | 1841 | 2009204 | 3815 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 34317 | 39.8803 | -121.6817 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035441 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1818289 | 0 | EPSS Ckt | N | 2023
44042 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-02-24 | 335 | 20230224 | 350 | 2002236 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 115 | 1709 | 40.9921 | -121.9718 | Yes | Clear;Below 32 F |  |  | 23-0033514 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816648 | 0 | EPSS Ckt | Y | 2023 | A B
44044 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1384 | 2023-02-24 | 400 | 20230226 | 1755 | 2002417 | 3715 | Distribution Circuit | Vegetation | Tree - bark fell into line | 400 | 769600 | 40.8937 | -122.382 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0033624 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816662 | 0 | EPSS Ckt | N | 2023 | A GRD
44052 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | JUMPER | OJ'S 1 SS OF 94725 | 2023-02-24 | 430 | 20230226 | 1552 | 2010042 | 3562 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3562 | 39.8312 | -121.6955 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0035721 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1818560 | 0 | EPSS Ckt | N | 2023
44054 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 26501 | 2023-02-24 | 436 | 20230226 | 1310 | 2005424 | 3394 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50910 | 39.8441 | -121.6946 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034128 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817063 | 0 | EPSS Ckt | N | 2023
44058 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | FUSE | 10781 | 2023-02-24 | 451 | 20230224 | 1055 | 2002623 | 364 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 20384 | 40.6152 | -122.4317 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0033994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1816966 | 0 | EPSS Ckt | N | 2023
44067 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | JUMPER | OJ'S @ HARDTAP TWD 6049 | 2023-02-24 | 524 | 20230225 | 1815 | 2008333 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2211 | 39.8455 | -121.6958 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1818029 | 0 | EPSS Ckt | N | 2023
44069 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | OTHER | WIRE DOWN 10 SP SS OF LR 2028 | 2023-02-24 | 528 | 20230225 | 1137 | 2002898 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 193071 | 39.825 | -121.7074 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | Yes | 1816933 | 0 | EPSS Ckt | N | 2023
44086 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 2023-02-24 | 620 | 20230224 | 1945 | 2003403 | 805 | Distribution Circuit | Equipment Failure/Involved | Overhead | 372 | 297770 | 40.5176 | -122.5057 | Yes | Overcast-Fog;32-90 F | Crossarm- Wood | Broken | 23-0033719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816754 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
44087 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 66791 | 2023-02-24 | 621 | 20230226 | 1732 | 2009987 | 3551 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 56816 | 39.8509 | -121.6636 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0035702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818542 | 0 | EPSS Ckt | N | 2023
44089 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | OCB | 1101/2 | 2023-02-24 | 634 | 20230301 | 935 | 2003356 | 5078 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3763 | 3797490 | 39.8716 | -121.6113 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken | 23-0033742 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1816770 | 0 | EPSS Ckt | N | 2023 | NONE
44094 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 2023-02-24 | 705 | 20230225 | 1715 | 2003640 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 98908 | 40.7197 | -122.6293 | Yes | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818162 | 1 | EPSS Ckt | N | 2023
44096 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | FUSE | 2469 | 2023-02-24 | 724 | 20230224 | 1439 | 2003277 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10440 | 40.593 | -122.4887 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034256 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1817148 | 0 | EPSS Ckt | N | 2023
44108 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-02-24 | 830 | 20230225 | 1028 | 2004254 | 1537 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 215983 | 39.7407 | -121.4962 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816836 | 0 | EPSS Ckt | N | 2023 | GRD- SGF TARGET
44116 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRIP-SAVER | 1243 | 2023-02-24 | 922 | 20230226 | 1512 | 2004703 | 3230 | Distribution Circuit | Environmental/External | Ice or snow | 55 | 177650 | 39.7896 | -121.6561 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034368 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817238 | 0 | EPSS Ckt | N | 2023 | N/A
44135 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 1731 | 2023-02-24 | 1612 | 20230225 | 1742 | 2006205 | 1530 | Distribution Circuit | Environmental/External | Ice or snow | 36 | 55080 | 39.7304 | -121.5313 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1818007 | 0 | EPSS Ckt | N | 2023
44144 | NORTH VALLEY | SHASTA | ROUND MOUNTAIN-1101 | 109001101 | FUSE | 1639 | 2023-02-24 | 1930 | 20230225 | 1254 | 2006909 | 1044 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 36 | 10928 | 40.7533 | -122.0237 | Yes | Partly Cloudy-Snow;Below 32 F |  |  | 23-0034942 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817807 | 0 | Non-EPSS | N | 2023
44148 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | JUMPER | OJ'S 2 SPAN SS OF CGC# 221046478133 | 2023-02-24 | 2026 | 20230228 | 1200 | 2009933 | 5254 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9574 | 39.8105 | -121.6271 | Yes | Overcast;32-90 F | Pole-Wood | Broken | 23-0035686 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818529 | 0 | EPSS Ckt | N | 2023
44167 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 55791 | 2023-02-25 | 1130 | 20230225 | 1215 | 2008406 | 45 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 135 | 39.7208 | -121.5234 | Yes | Clear;32-90 F |  |  | 23-0035203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1818054 | 0 | EPSS Ckt | N | 2023
44168 | NORTH VALLEY | SHASTA | ROUND MOUNTAIN-1101 | 109001101 | FUSE | 3887 | 2023-02-25 | 1145 | 20230225 | 1209 | 2008364 | 24 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 288 | 40.7524 | -122.0349 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0035189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818040 | 0 | Non-EPSS | N | 2023
44172 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 96271 | 2023-02-25 | 1253 | 20230226 | 755 | 2008267 | 1142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3426 | 39.7237 | -121.5775 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0035248 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1818090 | 0 | EPSS Ckt | N | 2023
44178 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | FUSE | 2443 | 2023-02-25 | 1645 | 20230225 | 1736 | 2008765 | 51 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 340 | 40.5975 | -122.5436 | Yes | Clear;32-90 F |  |  | 23-0035411 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818254 | 1 | EPSS Ckt | N | 2023
44192 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 2525 | 2023-02-26 | 1225 | 20230227 | 1805 | 2012371 | 1780 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26700 | 39.8617 | -121.6583 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0036439 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819074 | 0 | EPSS Ckt | N | 2023
44193 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 16617 | 2023-02-26 | 1231 | 20230227 | 1754 | 2013068 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5289 | 39.8797 | -121.6625 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036626 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819196 | 0 | EPSS Ckt | N | 2023
44195 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 310456 | 2023-02-26 | 1235 | 20230227 | 1756 | 2013216 | 1761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 33459 | 39.8583 | -121.66 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0036670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819234 | 0 | EPSS Ckt | N | 2023 | N/A
44196 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | TRANSFORMER | 220649080475 | 2023-02-26 | 1239 | 20230227 | 456 | 2009880 | 977 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 977 | 39.8753 | -121.7707 | Yes | Clear;32-90F | Transformer (OH) | Arcing | 23-0035725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818564 | 0 | EPSS Ckt | N | 2023
44231 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | JUMPER | OJ'S 1 POLE N/OF SBCO 94725 | 2023-02-27 | 849 | 20230227 | 1251 | 2011289 | 242 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 484 | 39.8322 | -121.6953 | Yes | Overcast-Drizzle;32-90 F | Pole-Wood | Deteriorated | 23-0036102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1818884 | 0 | EPSS Ckt | N | 2023
44235 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | TRANSFORMER | 220775882696 | 2023-02-27 | 955 | 20230227 | 1332 | 2011470 | 217 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 217 | 39.9365 | -121.7242 | Yes | Clear;32-90 F | Transformer | Broken | 23-0036239 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818957 | 0 | EPSS Ckt | N | 2023
44243 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | FUSE | 685 | 2023-02-27 | 1126 | 20230227 | 1600 | 2011973 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2740 | 39.9377 | -121.724 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036472 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819090 | 0 | EPSS Ckt | N | 2023
44260 | NORTH VALLEY | PARADISE | PARADISE-1105 | 102831105 | FUSE | 17343 | 2023-02-27 | 2038 | 20230228 | 1016 | 2013828 | 818 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 73620 | 39.8286 | -121.6212 | Yes | Overcast-Drizzle;32-90 F |  |  | 23-0037223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819678 | 0 | EPSS Ckt | N | 2023
44281 | NORTH VALLEY | PARADISE | PARADISE-1105 | 102831105 | FUSE | 17343 | 2023-02-28 | 1033 | 20230228 | 1143 | 2014888 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 6300 | 39.8286 | -121.6212 | Yes | Clear;32-90 F |  |  | 23-0037331 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | No | No | 1819744 | 0 | EPSS Ckt | N | 2023
44288 | NORTH VALLEY | PARADISE | PARADISE-1105 | 102831105 | FUSE | 17343 | 2023-02-28 | 1239 | 20230301 | 757 | 2015539 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 12948 | 39.8286 | -121.6212 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Together | 23-0037444 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819832 | 0 | EPSS Ckt | N | 2023
44291 | NORTH VALLEY | OROVILLE | CHALLENGE-1102 | 103201102 | RECLOSER | LR1101/2 | 2023-02-28 | 1330 | 20230302 | 1514 | 2014466 | 2984 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 495029 | 39.575 | -121.3064 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037471 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819850 | 0 | EPSS Ckt | N | 2023 | B- C- TIMED OC
44295 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | FUSE | 1403 | 2023-02-28 | 1726 | 20230301 | 1020 | 2016040 | 1014 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8112 | 39.8688 | -121.6111 | Yes | Clear;32-90F |  |  | 23-0038077 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820342 | 0 | EPSS Ckt | N | 2023
44321 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | TRANSFORMER | 220864079150 | 2023-03-02 | 1753 | 20230303 | 221 | 2020357 | 508 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 508 | 39.8389 | -121.6934 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0039019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821014 | 0 | EPSS Ckt | N | 2023
44329 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | FUSE | 417795 | 2023-03-03 | 1848 | 20230303 | 2340 | 2021628 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 876 | 39.7429 | -121.6754 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039670 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821431 | 0 | EPSS Ckt | N | 2023
44346 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-03-05 | 244 | 20230305 | 255 | 2023153 | 11 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 347 | 3817 | 39.8787 | -121.6118 | No | Overcast-Drizzle;32-90 F |  |  | 23-0040202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | No | No | 1821950 | 0 | EPSS Ckt | N | 2023 | A B C
44347 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-03-05 | 310 | 20230305 | 1237 | 2023162 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 349 | 188325 | 39.8787 | -121.6118 | No | Overcast-Snow-Strong Winds;32-90 F | Crossarm- Wood | Broken | 23-0040205 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821953 | 0 | EPSS Ckt | N | 2023 | A C
44348 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | FUSE | 6385 | 2023-03-05 | 542 | 20230305 | 849 | 2023245 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 2992 | 39.7404 | -121.6784 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0040230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821979 | 0 | EPSS Ckt | N | 2023
44348 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | FUSE | 6385 | 2023-03-05 | 542 | 20230305 | 849 | 2023245 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 2992 | 39.7404 | -121.6784 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 23-0040230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821979 | 0 | EPSS Ckt | N | 2023
44375 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-03-08 | 306 | 20230308 | 314 | 2026179 | 8 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 347 | 2776 | 39.8787 | -121.6118 | No | Overcast-Rain;32-90 F |  |  | 23-0041453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822783 | 0 | EPSS Ckt | N | 2023 | B C
44393 | NORTH VALLEY | SHASTA | OREGON TRAIL-1102 | 103521102 | FUSE | 3177 | 2023-03-09 | 1846 | 20230310 | 1632 | -2029160 | 1306 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 58770 | 40.6666 | -122.4016 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042682 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823490 | 0 | EPSS Ckt | N | 2023
44396 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 2023-03-09 | 1858 | 20230310 | 2023 | 2028764 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 111586 | 40.7197 | -122.6293 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042505 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823328 | 1 | EPSS Ckt | N | 2023 | A PHASE GRD
44401 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 871830 | 2023-03-09 | 1917 | 20230309 | 1940 | 2028963 | 23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 75 | 1725 | 40.8473 | -122.3309 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0042470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823295 | 0 | EPSS Ckt | N | 2023 | B & C
44404 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | FUSE | 2413 | 2023-03-09 | 1952 | 20230310 | 1645 | 2029121 | 1253 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 8771 | 40.658 | -122.4214 | Yes | Clear;32-90F |  |  | 23-0042897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823649 | 0 | EPSS Ckt | N | 2023
44424 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | FUSE | 3175 | 2023-03-10 | 708 | 20230310 | 1645 | 2030401 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 28850 | 40.664 | -122.4009 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042827 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | Yes | 1823605 | 0 | EPSS Ckt | N | 2023
44428 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2443 | 2023-03-10 | 1325 | 20230310 | 1340 | 2031077 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 150 | 40.5975 | -122.5436 | No | Partly Cloudy;32-90 F |  |  | 23-0043113 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1823741 | 0 | EPSS Ckt | N | 2023
44429 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 2023-03-10 | 1659 | 20230312 | 1949 | 2031443 | 3050 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 198295 | 40.8524 | -122.3324 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823808 | 0 | EPSS Ckt | N | 2023 | A & C
44430 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1378 | 2023-03-10 | 1702 | 20230311 | 1737 | 2031466 | 1209 | Distribution Circuit | Environmental/External | Ice or snow | 216 | 194087 | 40.8489 | -122.3313 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043223 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823815 | 0 | EPSS Ckt | N | 2023 | SGF ONLY
44439 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | TRANSFORMER | 221114580025 | 2023-03-11 | 1403 | 20230312 | 1039 | 2032481 | 1236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5840 | 39.8629 | -121.604 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0043508 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824053 | 0 | EPSS Ckt | N | 2023
44440 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | TRANSFORMER | 119035255586 | 2023-03-11 | 1433 | 20230311 | 1600 | 2032508 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 87 | 40.8586 | -122.3499 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0043509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824054 | 0 | EPSS Ckt | N | 2023
44454 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 2023-03-13 | 1123 | 20230313 | 1750 | 2034371 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 26703 | 40.7197 | -122.6293 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0044136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824534 | 0 | EPSS Ckt | N | 2023 | #2 AND #3
44462 | NORTH VALLEY | SHASTA | CEDAR CREEK-1101 | 103321101 | TRANSFORMER | 119911651760 | 2023-03-14 | 856 | 20230314 | 1932 | 2035388 | 636 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1908 | 40.7545 | -122.033 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0045096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825156 | 0 | EPSS Ckt | N | 2023
44519 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | JUMPER | OJ'S FEEDING CGC 118706445662 | 2023-03-17 | 1840 | 20230317 | 2108 | 2050668 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 148 | 40.5858 | -122.4663 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0047743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826984 | 0 | EPSS Ckt | N | 2023
44526 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-03-18 | 943 | 20230318 | 1325 | 2051001 | 222 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 1332 | 39.7407 | -121.4962 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0048241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1827493 | 0 | EPSS Ckt | N | 2023 | NONE
44540 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-03-20 | 2220 | 20230320 | 2233 | 2053491 | 13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 1950 | 39.7407 | -121.4962 | No | Clear;32-90 F | Insulator | Broken | 23-0049027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1828003 | 0 | EPSS Ckt | N | 2023 | NONE
44544 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | TRANSFORMER | 100000076234 | 2023-03-21 | 933 | 20230321 | 1122 | 2053829 | 109 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 109 | 39.7413 | -121.5192 | Yes | Overcast;32-90 F |  |  | 23-0049317 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1828124 | 0 | EPSS Ckt | N | 2023
44554 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | RECLOSER | 1454 | 2023-03-21 | 2213 | 20230322 | 149 | 2061198 | 216 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3672 | 40.3595 | -122.8928 | Yes | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0049897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1828889 | 0 | EPSS Ckt | N | 2023 | NONE
44595 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | RECLOSER | 384582 | 2023-03-28 | 727 | 20230330 | 2112 | 2069589 | 3645 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14820 | 40.3606 | -122.8896 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0053263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1830991 | 0 | EPSS Ckt | N | 2023 | A & C TGT
44633 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-03-29 | 943 | 20230329 | 1246 | 2072642 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 183 | 40.9921 | -121.9718 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 23-0054150 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831543 | 0 | EPSS Ckt | N | 2023 | NONE
44640 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | OCB | 1101/2 | 2023-03-29 | 1117 | 20230329 | 1245 | 2072881 | 88 | Distribution Circuit | Vegetation | Tree - fell into line | 1908 | 167904 | 39.8716 | -121.6113 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0054323 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831614 | 0 | EPSS Ckt | N | 2023 | A & B PHASE- TIME OC
44684 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 26501 | 2023-04-03 | 1523 | 20230404 | 139 | 2078670 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 28336 | 39.8441 | -121.6946 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0056475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1832916 | 0 | EPSS Ckt | N | 2023
44694 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-04-05 | 1127 | 20230405 | 1246 | s1833497 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 395 | 40.6175 | -122.4626 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0057318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1833497 | 0 | EPSS Ckt | N | 2023 | NONE
44712 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-04-08 | 1305 | 20230408 | 1518 | 2083265 | 133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 349 | 22957 | 39.8787 | -121.6118 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0058782 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834238 | 0 | EPSS Ckt | N | 2023 | B-C-TIME
44735 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 2023-04-11 | 2338 | 20230412 | 1940 | 2086081 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 157724 | 40.6166 | -122.4958 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0059843 | OH | Sus | 45726954 | NORTH VALLEY AND SIERRA | APR | Three Phase Fault | 0 | No | Yes | No | 1835006 | 0 | EPSS Ckt | N | 2023 | A- B- C
44763 | NORTH VALLEY | GLENN | ELK CREEK-1101 | 102781101 | FUSE | 841 | 2023-04-17 | 1838 | 20230418 | 650 | 2090845 | 732 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 10063 | 39.2511 | -122.4726 | No | Clear;32-90 F | Other | Broken | 23-0061836 | OH | Sus | 31642497 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1836514 | 1 | EPSS Ckt | N | 2023
44787 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2435 | 2023-04-21 | 1844 | 20230422 | 422 | 2094204 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4046 | 40.6041 | -122.5021 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0063645 | OH | Sus | 45738579 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837613 | 0 | EPSS Ckt | N | 2023
44832 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 2023-04-28 | 1953 | 20230428 | 2048 | 2099713 | 55 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 3685 | 40.8524 | -122.3324 | No | Clear;32-90 F | Insulator | Broken | 23-0066173 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839382 | 0 | EPSS Ckt | N | 2023 | NON
44838 | NORTH VALLEY | GLENN | ELK CREEK-1101 | 102781101 | FUSE | 4065 | 2023-04-29 | 1846 | 20230430 | 1013 | 2100189 | 927 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 2 | 1855 | 39.3657 | -122.6206 | No | Clear;32-90 F |  |  | 23-0066329 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839549 | 1 | EPSS Ckt | N | 2023
44841 | NORTH VALLEY | OROVILLE | WYANDOTTE-1107 | 102911107 | TRANSFORMER | 221854267053 | 2023-04-30 | 1007 | 20230430 | 1013 | 2100482 | 6 | Transformer only | 3rd Party | Fire- house or bldg. | 1 | 6 | 39.5057 | -121.3442 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066406 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839634 | 0 | EPSS Ckt | N | 2023
44855 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-05-01 | 1607 | 20230502 | 236 | 2101856 | 629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3774 | 39.7407 | -121.4962 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0066755 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1839954 | 0 | EPSS Ckt | N | 2023 | NONE
44930 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 160063 | 2023-05-18 | 1012 | 20230518 | 1155 | 2115965 | 101 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 313 | 31613 | 40.0066 | -121.6331 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1844218 | 0 | EPSS Ckt | N | 2023
44974 | NORTH VALLEY | SHASTA | JESSUP-1101 | 103441101 | TRANSFORMER | 118622741831 | 2023-05-25 | 1509 | 20230525 | 1603 | 2121345 | 54 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 54 | 40.4803 | -122.4962 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0075704 | OH | Sus | 45774969 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1845954 | 0 | EPSS Ckt | N | 2023
44984 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 417066 | 2023-05-25 | 2035 | 20230526 | 939 | 2121622 | 784 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 13328 | 40.6627 | -122.4938 | No | Lightning-Partly Cloudy;32-90 F |  |  | 23-0075759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1845991 | 0 | EPSS Ckt | Y | 2023 | AB
45026 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118648545510 | 2023-05-27 | 1626 | 20230528 | 230 | 2122815 | 604 | Transformer only | Environmental/External | Lightning | 1 | 604 | 40.5814 | -122.4877 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0076361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1846363 | 0 | EPSS Ckt | N | 2023
45027 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | FUSE | 177893 | 2023-05-27 | 1632 | 20230527 | 1918 | 2122776 | 166 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1660 | 40.5802 | -122.491 | No | Partly Cloudy;32-90 F |  |  | 23-0076359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1846361 | 0 | EPSS Ckt | N | 2023
45028 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | TRANSFORMER | 118787747413 | 2023-05-27 | 1652 | 20230527 | 2325 | 2122789 | 393 | Transformer only | Environmental/External | Lightning | 1 | 393 | 40.6338 | -122.4378 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846356 | 0 | EPSS Ckt | N | 2023
45030 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118638245486 | 2023-05-27 | 2004 | 20230528 | 305 | 2122822 | 421 | Transformer only | Environmental/External | Lightning | 1 | 421 | 40.5808 | -122.4916 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0076363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1846365 | 0 | EPSS Ckt | N | 2023
45041 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | TRANSFORMER | 118928956315 | 2023-05-29 | 948 | 20230529 | 1115 | 2123399 | 87 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 348 | 40.8786 | -122.3884 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0076550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846512 | 0 | EPSS Ckt | N | 2023
45064 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 2023-06-02 | 440 | 20230602 | 638 | 2127038 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 16284 | 39.839 | -121.7019 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0078063 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1847416 | 0 | EPSS Ckt | N | 2023 | NONE
45094 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 871830 | 2023-06-05 | 2027 | 20230606 | 57 | 2129994 | 270 | Distribution Circuit | Environmental/External | Lightning | 75 | 20250 | 40.8473 | -122.3309 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0079131 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1848139 | 0 | EPSS Ckt | Y | 2023 | B & C
45107 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 908917 | 2023-06-06 | 1703 | 20230606 | 1803 | 2131255 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 60 | 39.7273 | -121.4831 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0079493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1848484 | 0 | EPSS Ckt | N | 2023
45109 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | TRANSFORMER | 220832078975 | 2023-06-06 | 1801 | 20230607 | 12 | 2131204 | 371 | Transformer only | Environmental/External | Lightning | 1 | 371 | 39.8331 | -121.7043 | No | Overcast;32-90 F | Transformer (OH) | Burned/flashed | 23-0079569 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848486 | 0 | EPSS Ckt | N | 2023
45132 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118677745173 | 2023-06-08 | 1911 | 20230609 | 321 | 2133076 | 490 | Transformer only | Environmental/External | Lightning | 1 | 490 | 40.5723 | -122.4771 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080580 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849189 | 0 | EPSS Ckt | N | 2023
45134 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118685545166 | 2023-06-08 | 1936 | 20230609 | 356 | 2133059 | 500 | Transformer only | Environmental/External | Lightning | 2 | 1000 | 40.5721 | -122.4744 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080556 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849164 | 0 | EPSS Ckt | N | 2023
45135 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | TRANSFORMER | 118643943663 | 2023-06-08 | 1954 | 20230609 | 610 | 2133084 | 616 | Transformer only | Environmental/External | Lightning | 1 | 616 | 40.5311 | -122.4889 | No | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0080551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849157 | 0 | EPSS Ckt | N | 2023
45150 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118687045186 | 2023-06-11 | 916 | 20230611 | 1622 | 2134571 | 426 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 426 | 40.5726 | -122.4739 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0081266 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849711 | 0 | EPSS Ckt | N | 2023
45160 | NORTH VALLEY | SHASTA | CEDAR CREEK-1101 | 103321101 | FUSE | 1639 | 2023-06-11 | 1903 | 20230611 | 2114 | 2134789 | 131 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 4716 | 40.7533 | -122.0237 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0081354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849767 | 0 | EPSS Ckt | N | 2023
45185 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 2023-06-12 | 2151 | 20230613 | 1443 | 2135699 | 1012 | Distribution Circuit | Environmental/External | Lightning | 138 | 101687 | 39.839 | -121.7019 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1850084 | 0 | EPSS Ckt | Y | 2023 | A- B- GRD
45200 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | SWITCH | 69455 | 2023-06-14 | 1817 | 20230615 | 201 | 2137249 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 145696 | 39.9788 | -121.6395 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0082476 | OH | Sus | 31652358 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850689 | 0 | EPSS Ckt | N | 2023
45205 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | JUMPER | OJ @ MTR 1008055197 | 2023-06-15 | 1654 | 20230616 | 40 | 2137906 | 466 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 2330 | 40.005 | -122.4533 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 23-0082887 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850902 | 0 | EPSS Ckt | N | 2023
45221 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | JUMPER | 17159 HIGH SIDE JUMPERS | 2023-06-18 | 1514 | 20230618 | 1556 | 2139811 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 42 | 39.8715 | -121.6158 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0083503 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851449 | 0 | EPSS Ckt | N | 2023
45250 | NORTH VALLEY | GLENN | ELK CREEK-1101 | 102781101 | TRANSFORMER | 218335969961 | 2023-06-23 | 1718 | 20230623 | 1753 | 2144349 | 35 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 35 | 39.5853 | -122.5895 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0085222 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852760 | 0 | EPSS Ckt | N | 2023
45262 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | JUMPER | OPEN JUMPERS 1 SPAN S/S OF CGC 119786250804 | 2023-06-26 | 1250 | 20230626 | 1939 | 2146143 | 409 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1227 | 40.7269 | -122.0783 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Burned/flashed | 23-0085671 | OH | Sus | 31653631 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853226 | 0 | EPSS Ckt | N | 2023
45266 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1378 | 2023-06-26 | 2057 | 20230627 | 1214 | 2146447 | 917 | Distribution Circuit | Environmental/External | Lightning | 382 | 130725 | 40.8489 | -122.3313 | No | Overcast-Lightning;32-90 F | Conductor- Overhead | Normal | 23-0085844 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1853300 | 0 | EPSS Ckt | Y | 2023 | B- C & GRD
45272 | NORTH VALLEY | SHASTA | CEDAR CREEK-1101 | 103321101 | FUSE | 6349 | 2023-06-27 | 754 | 20230627 | 1111 | 2146667 | 197 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 591 | 40.7496 | -122.04 | No | Clear;32-90 F |  |  | 23-0086040 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1853477 | 0 | EPSS Ckt | N | 2023
45285 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | FUSE | 7835 | 2023-06-29 | 1329 | 20230629 | 1632 | 2148981 | 183 | Distribution Circuit | 3rd Party | Vehicle | 4 | 732 | 40.7117 | -122.0876 | No | Clear;Above 90 | Conductor- Overhead | Burned/flashed | 23-0087171 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854098 | 0 | EPSS Ckt | N | 2023
45339 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | FUSE | 850235 | 2023-07-07 | 2113 | 20230707 | 2300 | 2156719 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 535 | 40.3466 | -121.7486 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0090032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855780 | 0 | EPSS Ckt | N | 2023
45346 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | SWITCH | 800623 | 2023-07-09 | 1010 | 20230709 | 1305 | 2157608 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 700 | 40.6653 | -122.6361 | No | Clear;32-90 F | Other | Broken | 23-0090202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855945 | 0 | EPSS Ckt | N | 2023
45347 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | TRANSFORMER | 118614943227 | 2023-07-09 | 1523 | 20230709 | 2141 | 2157741 | 378 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 756 | 40.5188 | -122.4994 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0090250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1855978 | 0 | EPSS Ckt | N | 2023
45349 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 1731 | 2023-07-10 | 1937 | 20230711 | 304 | 2158958 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 2518 | 39.7304 | -121.5313 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0090627 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856251 | 0 | EPSS Ckt | N | 2023
45361 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | SWITCH | 1721 | 2023-07-13 | 1136 | 20230713 | 1425 | 2161642 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 22139 | 39.764 | -121.5211 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0091780 | OH | Sus | 45885405 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1857167 | 0 | EPSS Ckt | N | 2023
45398 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 65932 | 2023-07-19 | 1451 | 20230719 | 1638 | 2168301 | 107 | Distribution Circuit | Vegetation | Tree - fell into line | 1094 | 116539 | 39.8705 | -121.6503 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0094302 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1858888 | 0 | EPSS Ckt | Y | 2023 | A & C
45409 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | FUSE | 6659 | 2023-07-20 | 1519 | 20230720 | 1635 | 2169153 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 912 | 40.7484 | -122.2451 | No | Clear;Above 90 | Crossarm- Wood | Deteriorated | 23-0094829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859151 | 0 | EPSS Ckt | N | 2023
45416 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | SWITCH | 2407BP | 2023-07-21 | 955 | 20230721 | 1318 | 2169794 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 316 | 64148 | 39.9508 | -121.6509 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0095130 | OH | Sus | 45895631 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859391 | 0 | EPSS Ckt | N | 2023
45441 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | FUSE | 3341 | 2023-07-24 | 1740 | 20230724 | 2142 | 2172835 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 18150 | 40.7465 | -122.2412 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0096203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860123 | 0 | EPSS Ckt | N | 2023
45455 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | JUMPER | OJ'S 2 W/OF CGC 221044073508 | 2023-07-26 | 905 | 20230726 | 1218 | 2174195 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 193 | 39.6849 | -121.6315 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0096925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860609 | 0 | EPSS Ckt | N | 2023
45475 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRANSFORMER | 220966277631 | 2023-07-29 | 812 | 20230729 | 1242 | 2176965 | 270 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 270 | 39.7979 | -121.6578 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0098282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861416 | 0 | EPSS Ckt | N | 2023
45476 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | TRANSFORMER | 119339050453 | 2023-07-29 | 955 | 20230729 | 2120 | 2177049 | 685 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 3425 | 40.7178 | -122.239 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0098301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861458 | 0 | EPSS Ckt | N | 2023
45486 | NORTH VALLEY | SHASTA | JESSUP-1101 | 103441101 | TRANSFORMER | 118634542000 | 2023-07-30 | 1503 | 20230731 | 206 | 2177788 | 663 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 663 | 40.4851 | -122.492 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0098481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861620 | 0 | EPSS Ckt | N | 2023
45490 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 1462 | 2023-08-01 | 704 | 20230801 | 916 | 2179145 | 132 | Distribution Circuit | Animal | Other | 27 | 3564 | 40.6671 | -122.6332 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0098949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1861962 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
45491 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2909 | 2023-08-01 | 947 | 20230801 | 1425 | 2179628 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 278 | 40.6586 | -122.6235 | No | Partly Cloudy;Above 90 |  |  | 23-0099191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1862177 | 0 | EPSS Ckt | N | 2023
45500 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-08-02 | 1018 | 20230802 | 1239 | 2180480 | 141 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 7614 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0099525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862447 | 0 | EPSS Ckt | Y | 2023 | DCD
45511 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-08-03 | 1048 | 20230803 | 1406 | 2181494 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 10692 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0100057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1862779 | 0 | EPSS Ckt | Y | 2023 | DCD
45518 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 2023-08-04 | 1617 | 20230804 | 2003 | 2182653 | 226 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 70 | 15820 | 40.7197 | -122.6293 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0100775 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1863163 | 0 | EPSS Ckt | N | 2023 | NONE
45520 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-08-05 | 626 | 20230805 | 1823 | 2182844 | 717 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 115 | 39960 | 40.9921 | -121.9718 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0100840 | OH | Sus | 31661928 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1863223 | 0 | EPSS Ckt | Y | 2023 | A-C
45531 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 65932 | 2023-08-09 | 344 | 20230809 | 1615 | 2186226 | 751 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1093 | 109926 | 39.8705 | -121.6503 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0101980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1864140 | 0 | EPSS Ckt | Y | 2023 | B PHASE GRD
45533 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-08-09 | 1110 | 20230809 | 1247 | 2186634 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 5238 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0102136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864354 | 0 | EPSS Ckt | Y | 2023 | SGF/ DCD
45542 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-08-11 | 951 | 20230811 | 1256 | 2188513 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 9990 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0103212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864958 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
45544 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 65932 | 2023-08-11 | 2301 | 20230812 | 204 | 2188974 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 17934 | 39.8705 | -121.6503 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0103475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1865109 | 0 | EPSS Ckt | N | 2023 | NONE
45555 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-08-14 | 952 | 20230814 | 1127 | 2190279 | 95 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 5130 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0103941 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1865563 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD ALRAMED
45576 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 2023-08-16 | 1848 | 20230817 | 244 | 2193244 | 476 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 747 | 98798 | 40.351 | -121.7811 | No | Partly Cloudy;Above 90 |  |  | 23-0105296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1866338 | 0 | EPSS Ckt | Y | 2023 | A & B
45600 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 7101 | 2023-08-21 | 1010 | 20230821 | 1733 | 2197902 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 549 | 41602 | 40.6174 | -122.49 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0106981 | OH | Sus | 45935498 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867624 | 0 | EPSS Ckt | Y | 2023
45619 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-08-23 | 1454 | 20230823 | 1551 | 2200324 | 57 | Distribution Circuit | Animal | Squirrel | 114 | 6498 | 40.9921 | -121.9718 | No | Clear;32-90 F | Pothead(Riser Termination) | Burned/flashed | 23-0108226 | OH | Sus | 45938148 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1868379 | 0 | EPSS Ckt | Y | 2023 | B & GRD
45651 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2023-08-30 | 142 | 20230830 | 1834 | 2205491 | 1010 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 218 | 216883 | 39.7407 | -121.4962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110215 | OH | Sus | 8206198 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1870019 | 0 | EPSS Ckt | N | 2023 | NONE
45657 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 2023-08-30 | 200 | 20230830 | 1842 | 2205496 | 1002 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 192 | 192384 | 40.5176 | -122.5057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0110318 | OH | Sus | 8206198 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1870021 | 0 | EPSS Ckt | N | 2023 | NONE
45677 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2023-08-30 | 406 | 20230830 | 2010 | 2205568 | 964 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 1928 | 39.8995 | -122.6127 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0110298 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1870056 | 0 | EPSS Ckt | N | 2023 | NONE
45694 | NORTH VALLEY | SHASTA | CEDAR CREEK-1101 | 103321101 | FUSE | 6349 | 2023-08-31 | 801 | 20230831 | 931 | 2206658 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 270 | 40.7496 | -122.04 | No | Clear;32-90 F |  |  | 23-0111176 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1870508 | 0 | EPSS Ckt | N | 2023
45701 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2023-09-01 | 812 | 20230903 | 1057 | 2207593 | 3045 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 17649 | 40.6669 | -122.6336 | No | Overcast;32-90 F | Lightning Arrestor | Broken | 23-0111637 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870709 | 0 | EPSS Ckt | Y | 2023 | A PHASE GRD INST OC
45704 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118658045485 | 2023-09-01 | 1019 | 20230901 | 1305 | 2207750 | 166 | Transformer only | Environmental/External | Lightning | 2 | 332 | 40.5808 | -122.4844 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870812 | 0 | EPSS Ckt | N | 2023
45707 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | TRANSFORMER | 118655745446 | 2023-09-01 | 1225 | 20230901 | 1305 | 2207876 | 40 | Transformer only | Environmental/External | Lightning | 1 | 40 | 40.5796 | -122.4851 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0111837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870813 | 0 | EPSS Ckt | N | 2023
45711 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 417066 | 2023-09-01 | 1603 | 20230901 | 1804 | 2208033 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 19 | 2299 | 40.6627 | -122.4938 | No | Overcast-Rain-Lightning;32-90 F |  |  | 23-0111983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Three Phase Fault | 0 | No | No | No | 1870846 | 0 | EPSS Ckt | Y | 2023 | A B & C PHASE
45717 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | TRANSFORMER | 118659545857 | 2023-09-02 | 751 | 20230902 | 1251 | 2208485 | 300 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 2100 | 40.591 | -122.4839 | No | Clear;32-90 F | Secondary | Broken | 23-0112089 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1870943 | 0 | EPSS Ckt | N | 2023
45761 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-09-13 | 1132 | 20230913 | 1402 | 2217752 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 8100 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0116047 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1873721 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
45788 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-09-18 | 1254 | 20230918 | 1657 | 2221674 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 10962 | 40.6175 | -122.4626 | No | Partly Cloudy;32-90 F | Insulator | Failed/Faulted | 23-0117821 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874909 | 0 | EPSS Ckt | Y | 2023 | SGF TGT W/DCD ALARM
45793 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-09-19 | 1155 | 20230919 | 1353 | 2222483 | 118 | Distribution Circuit | Company Initiated | Coordination failure | 54 | 6372 | 40.6175 | -122.4626 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118198 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1875222 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
45794 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | TRANSFORMER | 220732981220 | 2023-09-19 | 1159 | 20230920 | 31 | 2222783 | 752 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 752 | 39.8957 | -121.7404 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0118437 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1875296 | 0 | EPSS Ckt | N | 2023
45801 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-09-20 | 1126 | 20230920 | 1206 | 2223351 | 40 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 2160 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0118727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1875572 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
45812 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2023-09-20 | 2320 | 20230921 | 1705 | 2223768 | 1065 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 2130 | 39.8995 | -122.6127 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875684 | 0 | EPSS Ckt | N | 2023 | NONE
45832 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 3361 | 2023-09-23 | 1457 | 20230924 | 154 | 2225506 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 7227 | 39.8802 | -121.6629 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0120068 | OH | Sus | 35490990 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876231 | 0 | EPSS Ckt | N | 2023
45874 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-09-29 | 1157 | 20230929 | 1403 | 2230442 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 6804 | 40.6175 | -122.4626 | No | Partly Cloudy;32-90 F |  |  | 23-0122577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877934 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD ALARM
45876 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | FUSE | 10779 | 2023-09-29 | 1322 | 20230929 | 1705 | 2230384 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1784 | 40.5153 | -122.5148 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0122572 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877929 | 0 | EPSS Ckt | N | 2023
45888 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 2097 | 2023-09-29 | 2211 | 20230930 | 242 | 2230861 | 271 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2710 | 39.8127 | -121.7121 | No | Overcast-Drizzle-Lightning;32-90 F |  |  | 23-0122806 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878041 | 0 | EPSS Ckt | N | 2023
45915 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRANSFORMER | 220896775716 | 2023-09-30 | 1504 | 20230930 | 1804 | 2231730 | 180 | Transformer only | Environmental/External | Lightning | 1 | 180 | 39.7454 | -121.6825 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123012 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878238 | 0 | EPSS Ckt | N | 2023
45915 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRANSFORMER | 220896775716 | 2023-09-30 | 1504 | 20230930 | 1804 | 2231730 | 180 | Transformer only | Environmental/External | Lightning | 1 | 180 | 39.7454 | -121.6825 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0123012 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878238 | 0 | EPSS Ckt | N | 2023
45929 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | TRANSFORMER | 221343175064 | 2023-10-01 | 1225 | 20231001 | 1630 | 2232175 | 245 | Transformer only | Environmental/External | Lightning | 1 | 245 | 39.7264 | -121.5241 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0123105 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1878345 | 0 | EPSS Ckt | N | 2023
45953 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2023-10-04 | 941 | 20231004 | 1641 | 2234473 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 44090 | 39.8787 | -121.6118 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0124282 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1879265 | 0 | EPSS Ckt | Y | 2023 | A- B- C- & 50 INST
45963 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2023-10-05 | 1939 | 20231005 | 1957 | 2236057 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 18 | 324 | 40.6175 | -122.4626 | No | Clear;32-90 F |  |  | 23-0125101 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1879720 | 0 | EPSS Ckt | Y | 2023 | NONE
45973 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 718316 | 2023-10-07 | 1423 | 20231007 | 1431 | 2237740 | 8 | Distribution Circuit | Company Initiated | Personnel- company | 10 | 80 | 40.884 | -122.3876 | No | Clear;32-90 F | Recloser | Normal | 23-0125761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1880231 | 0 | EPSS Ckt | Y | 2023 | B & C PHASE
45994 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | JUMPER | OJ'S FEEDING CGC 119356451544 | 2023-10-12 | 1054 | 20231012 | 1431 | 2241764 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1736 | 40.7478 | -122.2333 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0127464 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1881629 | 0 | EPSS Ckt | N | 2023
45996 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | TRANSFORMER | 119353550521 | 2023-10-12 | 1743 | 20231013 | 450 | 2242130 | 667 | Transformer only | Unknown Cause | Patrol - not conducted | 4 | 2668 | 40.7197 | -122.2339 | No | Clear;32-90 F |  |  | 23-0127750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1881717 | 0 | EPSS Ckt | N | 2023
46012 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | TRANSFORMER | 220776382876 | 2023-10-15 | 2015 | 20231016 | 300 | 2243976 | 405 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 810 | 39.9414 | -121.7241 | No | Partly Cloudy;32-90 F | Jumper | Burned Open | 23-0128468 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882304 | 0 | EPSS Ckt | N | 2023
46015 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | JUMPER | OJ SOURCE SIDE OF CGC# 118706445662 | 2023-10-16 | 912 | 20231016 | 937 | 2244250 | 25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 25 | 40.5858 | -122.4664 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Broken | 23-0128565 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882436 | 0 | EPSS Ckt | N | 2023
46029 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 308298 | 2023-10-20 | 1402 | 20231020 | 1433 | 2247744 | 31 | Distribution Circuit | Company Initiated | Personnel- company | 24 | 744 | 39.8338 | -121.6933 | No | Clear;32-90 F | Recloser | Normal | 23-0130704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1883696 | 0 | EPSS Ckt | Y | 2023 | B-C
46030 | NORTH VALLEY | PARADISE | PARADISE-1106 | 102831106 | FUSE | 840311 | 2023-10-20 | 1717 | 20231020 | 1836 | 2247842 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 211 | 39.7777 | -121.6221 | No | Clear;32-90 F |  |  | 23-0130799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1883718 | 1 | EPSS Ckt | N | 2023
46034 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118853624488 | 2023-10-23 | 818 | 20231023 | 1015 | 2249565 | 117 | Transformer only | 3rd Party | Other | 1 | 117 | 40.0046 | -122.4105 | No | Clear;32-90 F | Jumper |  | 23-0131269 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1884295 | 0 | EPSS Ckt | N | 2023
46054 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 718316 | 2023-10-25 | 1813 | 20231025 | 2200 | 2251865 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 400 | 36530 | 40.884 | -122.3876 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0132594 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1885038 | 0 | EPSS Ckt | Y | 2023 | B PHASE
46095 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | JUMPER | OJ'S 1 E/OF CGC 221301175025 | 2023-11-02 | 1000 | 20231102 | 1058 | 2258221 | 58 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 116 | 39.7252 | -121.5386 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0135097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887182 | 0 | EPSS Ckt | N | 2023
46101 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-11-04 | 804 | 20231104 | 2040 | 2259755 | 756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 33979 | 40.9921 | -121.9718 | No | Partly Cloudy;32-90 F | Other | Broken | 23-0135852 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1887696 | 0 | EPSS Ckt | Y | 2023 | A & GRD
46154 | NORTH VALLEY | SHASTA | JESSUP-1101 | 103441101 | TRANSFORMER | 118717341624 | 2023-11-12 | 1529 | 20231112 | 1639 | 2267269 | 70 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 70 | 40.4749 | -122.4621 | No | Partly Cloudy;32-90 F | Fuse | Broken | 23-0138218 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1889891 | 0 | EPSS Ckt | N | 2023
46183 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 17155 | 2023-11-17 | 1007 | 20231117 | 1128 | 2271491 | 81 | Distribution Circuit | Animal | Squirrel | 34 | 2754 | 39.6854 | -121.6242 | No | Partly Cloudy;32-90 F | Switch (UG) | Normal | 23-0140402 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891334 | 0 | EPSS Ckt | N | 2023
46195 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2023-11-18 | 1608 | 20231118 | 1620 | 2272870 | 12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 114 | 1368 | 40.9921 | -121.9718 | No | Overcast-Fog-Rain-Lightning;32-90 F |  |  | 23-0140929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1891606 | 0 | EPSS Ckt | Y | 2023 | A- C
46211 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2655 | 2023-11-18 | 2348 | 20231119 | 24 | 2273361 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 612 | 40.609 | -122.4965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0141042 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891711 | 0 | EPSS Ckt | N | 2023
46228 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118741724790 | 2023-11-21 | 7 | 20231121 | 232 | 2274702 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 145 | 40.0127 | -122.4505 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0141625 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1892047 | 0 | EPSS Ckt | N | 2023
46244 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | RECLOSER | 733624 | 2023-11-23 | 2206 | 20231123 | 2358 | 2276267 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 2933 | 39.5802 | -121.2944 | No | Clear;32-90 F |  |  | 23-0142577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1892509 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
46245 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | RECLOSER | 733624 | 2023-11-24 | 13 | 20231124 | 1332 | 2276296 | 799 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 6429 | 39.5802 | -121.2944 | No | Clear;32-90 F |  |  | 23-0142577 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1892513 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
46308 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | OTHER | SERVICE DIG IN AT T2214 | 2023-12-04 | 1231 | 20231204 | 2238 | s1895017 | 607 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 1 | 607 | 40.5734 | -122.4543 | No | Clear;32-90 F | Bushing | Broken | 23-0145267 | OH | Sus | 35515220 | NORTH VALLEY AND SIERRA | DEC | Open Circuit | 0 | No | No | No | 1895017 | 0 | EPSS Ckt | N | 2023
46320 | NORTH VALLEY | PARADISE | CRESTA 1101 | 102251101 | SWITCH | 4557 | 2023-12-06 | 1005 | 20231206 | 1522 | 2285112 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 317 | 39.8276 | -121.4222 | No | Partly Cloudy-Drizzle;32-90 F | Other | Broken | 23-0145830 | OH | Sus | 46079715 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895600 | 0 | EPSS Ckt | N | 2023
46353 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1588 | 2023-12-13 | 1148 | 20231213 | 1245 | 2291010 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 171 | 40.617 | -122.4963 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0147219 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897524 | 0 | EPSS Ckt | N | 2023 | N/A
46358 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | JUMPER | OJ'S 1 SPAN SOURCE SIDE OF CGC 118680645183 | 2023-12-13 | 1912 | 20231213 | 2220 | 2291348 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 188 | 40.5731 | -122.4765 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0147325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897602 | 0 | EPSS Ckt | N | 2023
46361 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | FUSE | 400251 | 2023-12-15 | 921 | 20231215 | 1135 | 2292408 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 134 | 39.7438 | -121.6746 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0147551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | None | 0 | No | No | No | 1898095 | 0 | EPSS Ckt | N | 2023
46362 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1378 | 2023-12-15 | 1219 | 20231215 | 1608 | 2292594 | 229 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 215 | 10358 | 40.8489 | -122.3313 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Together | 23-0147576 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1898176 | 0 | EPSS Ckt | N | 2023 | SGF
46403 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2909 | 2023-12-28 | 1334 | 20231228 | 1510 | 2301389 | 96 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 96 | 40.6586 | -122.6235 | No | Overcast-Fog;32-90 F | Insulator | Burned/flashed | 23-0149115 | OH | Sus | 31680486 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1900367 | 0 | EPSS Ckt | N | 2023
46470 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2024-01-13 | 1246 | 20240113 | 1641 | 2314683 | 235 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 26358 | 40.9921 | -121.9718 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0010470 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1903791 | 0 | EPSS Ckt | N | 2024 | A & B
46474 | NORTH VALLEY | SHASTA | CEDAR CREEK-1101 | 103321101 | OTHER | WIRE DOWN 1 SS OF CGC 119975552175 | 2024-01-13 | 1525 | 20240113 | 2138 | 2314936 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 34572 | 40.7666 | -122.0099 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0010532 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1903828 | 0 | EPSS Ckt | N | 2024
46476 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | FUSE | 16437 | 2024-01-13 | 1609 | 20240113 | 2002 | 2314877 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 466 | 39.9328 | -121.7284 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0010512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1903819 | 0 | EPSS Ckt | N | 2024
46533 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | TRANSFORMER | 220928080565 | 2024-01-26 | 1128 | 20240126 | 1201 | 2324842 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 66 | 39.878 | -121.6697 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0015563 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1906673 | 0 | EPSS Ckt | N | 2024
46541 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2735 | 2024-01-29 | 733 | 20240129 | 944 | 2326895 | 131 | Distribution Circuit | 3rd Party | Gun Shot | 1 | 131 | 40.6659 | -122.5009 | No | Clear;32-90 F | Fuse | Burned Open | 24-0016106 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1907151 | 0 | EPSS Ckt | N | 2024
46566 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | OCB | 1101/2 | 2024-02-01 | 47 | 20240201 | 158 | 2330716 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1904 | 135184 | 39.8716 | -121.6113 | No | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0017737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908135 | 0 | EPSS Ckt | N | 2024 | A-B & TIME
46571 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 1737 | 2024-02-01 | 302 | 20240201 | 515 | 2330758 | 133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 8778 | 39.7058 | -121.4747 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0017768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1908167 | 0 | EPSS Ckt | N | 2024
46666 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 2024-02-04 | 2004 | 20240208 | 1506 | 2353145 | 5462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 341855 | 39.839 | -121.7019 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021013 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1910835 | 0 | EPSS Ckt | N | 2024 | GRD & SGF
46685 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | OCB | 1102/2 | 2024-02-04 | 2038 | 20240207 | 1809 | 2354687 | 4171 | Distribution Circuit | Vegetation | Tree - fell into line | 1919 | 3549887 | 39.8716 | -121.6114 | Yes | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1910921 | 0 | EPSS Ckt | N | 2024 | NONE
46686 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | OTHER | WIRE DOWN SPAN LD SIDE OF 1409 | 2024-02-04 | 2040 | 20240207 | 1154 | 2356686 | 3794 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 444666 | 39.8391 | -121.6212 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021466 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911301 | 0 | EPSS Ckt | N | 2024
46707 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 1462 | 2024-02-04 | 2301 | 20240206 | 1229 | 2355577 | 2248 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 29912 | 40.6671 | -122.6332 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021258 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911089 | 0 | EPSS Ckt | N | 2024 | A-C PHASE- GRD
46745 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | TRANSFORMER | 118920156356 | 2024-02-05 | 1053 | 20240205 | 1943 | 2358995 | 530 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 2120 | 40.8797 | -122.3914 | No | Strong Winds-Clear;32-90 F |  |  | 24-0022382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1912034 | 0 | EPSS Ckt | N | 2024
46773 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | FUSE | 55791 | 2024-02-06 | 1520 | 20240206 | 1616 | 2365555 | 56 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 168 | 39.7208 | -121.5234 | No | Partly Cloudy;32-90 F |  |  | 24-0023722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1913115 | 0 | EPSS Ckt | N | 2024
46852 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | TRANSFORMER | 118929957693 | 2024-02-19 | 905 | 20240219 | 1156 | 2380564 | 171 | Transformer only | Vegetation | Tree - fell into line | 5 | 855 | 40.9163 | -122.3883 | No | Overcast-Fog-Rain;32-90 F | Cutout- fuse holder | Broken | 24-0030743 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917956 | 0 | EPSS Ckt | N | 2024
46858 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | FUSE | 6155 | 2024-02-19 | 1225 | 20240219 | 1354 | 2381105 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2759 | 40.6172 | -122.4288 | No | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0030879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918053 | 0 | EPSS Ckt | N | 2024
46867 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 1917 | 2024-02-19 | 1529 | 20240219 | 1949 | 2381738 | 260 | Distribution Circuit | Environmental/External | Lightning | 77 | 4896 | 39.8719 | -121.6791 | No | Overcast-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030978 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918121 | 0 | EPSS Ckt | N | 2024
46873 | NORTH VALLEY | OROVILLE | WYANDOTTE-1103 | 102911103 | FUSE | 219237 | 2024-02-20 | 622 | 20240220 | 1050 | 2382413 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 1072 | 39.5763 | -121.3023 | No | Clear;32-90 F |  |  | 24-0031475 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918438 | 0 | EPSS Ckt | N | 2024
47006 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | FUSE | 1671 | 2024-03-02 | 1405 | 20240304 | 1548 | 2395038 | 2983 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 69629 | 40.3889 | -123.0589 | No | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921950 | 0 | EPSS Ckt | N | 2024
47021 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 2024-03-04 | 2112 | 20240305 | 1356 | 2397198 | 1004 | Distribution Circuit | Equipment Failure/Involved | Overhead | 750 | 578676 | 40.351 | -121.7811 | No | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0037839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1922425 | 0 | EPSS Ckt | N | 2024 | A-B-GRD
47043 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | FUSE | 17343 | 2024-03-09 | 623 | 20240309 | 839 | 2400571 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 11968 | 39.8286 | -121.6212 | No | Partly Cloudy;32-90 F |  |  | 24-0040062 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1923684 | 0 | EPSS Ckt | N | 2024
47056 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | RECLOSER | 98896 | 2024-03-11 | 2343 | 20240312 | 331 | 2402278 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 10646 | 40.3607 | -122.9513 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0040694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924212 | 0 | EPSS Ckt | N | 2024 | NONE
47067 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | TRANSFORMER | 120083035765 | 2024-03-13 | 1650 | 20240313 | 1745 | 2403815 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 40.3151 | -121.9719 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0041700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1924764 | 0 | EPSS Ckt | N | 2024
47073 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 38698 | 2024-03-14 | 1053 | 20240314 | 1808 | 2404844 | 435 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 59367 | 40.0372 | -121.6183 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042015 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925082 | 0 | EPSS Ckt | N | 2024 | A AND C
47115 | NORTH VALLEY | OROVILLE | WYANDOTTE-1103 | 102911103 | TRANSFORMER | 221991269759 | 2024-03-20 | 1206 | 20240320 | 1319 | 2410315 | 73 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 146 | 39.58 | -121.2949 | No | Clear;32-90 F |  |  | 24-0044671 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1926969 | 0 | EPSS Ckt | N | 2024
47116 | NORTH VALLEY | OROVILLE | WYANDOTTE-1103 | 102911103 | TRANSFORMER | 221991269759 | 2024-03-20 | 1605 | 20240320 | 2052 | 2410580 | 287 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 574 | 39.58 | -121.2949 | No | Clear;32-90 F | Fuse | Normal | 24-0044911 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927049 | 0 | EPSS Ckt | N | 2024
47126 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 7285 | 2024-03-22 | 927 | 20240322 | 1057 | 2411804 | 90 | Distribution Circuit | 3rd Party | Vehicle | 36 | 3240 | 40.5995 | -122.4921 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Together | 24-0045573 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927480 | 0 | EPSS Ckt | N | 2024
47128 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | TRANSFORMER | 220649080475 | 2024-03-22 | 1035 | 20240322 | 1533 | 2411939 | 298 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 298 | 39.8753 | -121.7707 | No | Partly Cloudy-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927490 | 0 | EPSS Ckt | N | 2024
47179 | NORTH VALLEY | GLENN | ELK CREEK-1101 | 102781101 | FUSE | 4065 | 2024-03-28 | 1542 | 20240328 | 1821 | 2417554 | 159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 477 | 39.3657 | -122.6206 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0048114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929197 | 0 | EPSS Ckt | N | 2024
47184 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | TRANSFORMER | 119350350401 | 2024-03-30 | 843 | 20240330 | 1428 | 2418894 | 345 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 345 | 40.7163 | -122.235 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0048719 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1929591 | 0 | EPSS Ckt | N | 2024
47207 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | TRANSFORMER | 100000013186 | 2024-04-03 | 1617 | 20240403 | 1647 | 2421960 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 60 | 39.8475 | -121.6722 | No | Overcast;32-90 F | Transformer (OH) | Deteriorated | 24-0050352 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930657 | 0 | EPSS Ckt | N | 2024
47247 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | SWITCH | 1905 | 2024-04-10 | 919 | 20240410 | 1527 | 2427714 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 36064 | 39.8732 | -121.6583 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0051305 | OH | Sus | 35541680 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1932460 | 0 | EPSS Ckt | N | 2024
47261 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1614 | 2024-04-14 | 557 | 20240417 | 1556 | s1933595 | 4919 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4919 | 40.9971 | -121.9666 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0054627 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1933595 | 0 | EPSS Ckt | N | 2024 | A & GRD
47269 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | SWITCH | 3339 | 2024-04-15 | 859 | 20240415 | 1013 | 2431595 | 74 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 6586 | 40.7349 | -122.2403 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0054787 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1933654 | 0 | EPSS Ckt | N | 2024
47295 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | FUSE | 26501 | 2024-04-20 | 1416 | 20240420 | 2233 | 2435567 | 497 | Distribution Circuit | 3rd Party | Customer Equipment | 46 | 22862 | 39.8441 | -121.6946 | No | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 24-0057189 | OH | Sus | 31691312 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | No | 1935224 | 0 | EPSS Ckt | N | 2024
47313 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | TRANSFORMER | 220869379949 | 2024-04-24 | 1512 | 20240424 | 1553 | 2438320 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 123 | 39.8612 | -121.6907 | No | Clear;32-90 F | Secondary | Broken | 24-0058609 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1936171 | 0 | EPSS Ckt | N | 2024
47339 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1892 | 2024-05-01 | 446 | 20240501 | 706 | 2443056 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 420 | 40.7018 | -122.6403 | No | Clear;32-90 F | Capacitor | Burned/flashed | 24-0060687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1937825 | 0 | EPSS Ckt | N | 2024 | B- C- SGF
47385 | NORTH VALLEY | PARADISE | PARADISE-1103 | 102831103 | TRANSFORMER | 220980074445 | 2024-05-04 | 1837 | 20240505 | 951 | 2446118 | 914 | Transformer only | Environmental/External | Lightning | 2 | 1828 | 39.71 | -121.6529 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0062247 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1939021 | 0 | EPSS Ckt | N | 2024
47410 | NORTH VALLEY | SHASTA | RISING RIVER-1101 | 103551101 | JUMPER | OJS @ CGC 121602649278 | 2024-05-08 | 157 | 20240508 | 241 | 2448325 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 44 | 40.6843 | -121.4232 | No | Clear;Below 32 F | Service conductor | Bent or Twisted | 24-0063376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1939853 | 0 | EPSS Ckt | N | 2024
47421 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2024-05-10 | 1127 | 20240510 | 1354 | 2450835 | 69 | Distribution Circuit | 3rd Party | Customer Equipment | 349 | 32457 | 39.8787 | -121.6118 | No | Clear;32-90 F | Other | Malfunctioning | 24-0064694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1940714 | 0 | EPSS Ckt | N | 2024 | A- B- SGF- GRD INST
47517 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | FUSE | 17849 | 2024-05-27 | 638 | 20240527 | 845 | 2468119 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 254 | 39.8759 | -121.6121 | No | Clear;32-90 F |  |  | 24-0070185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944358 | 0 | EPSS Ckt | N | 2024
47522 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | SWITCH | 94725 | 2024-05-28 | 913 | 20240528 | 1100 | 2468642 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 107 | 39.8304 | -121.6956 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0070378 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1944543 | 0 | EPSS Ckt | N | 2024
47539 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | FUSE | 9577 | 2024-05-31 | 803 | 20240531 | 809 | 2471501 | 6 | Distribution Circuit | 3rd Party | Other | 1 | 6 | 40.6979 | -122.6395 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0071729 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1945438 | 0 | EPSS Ckt | N | 2024
47568 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | TRANSFORMER | 221442074535 | 2024-06-05 | 1159 | 20240605 | 1820 | 2476263 | 381 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 381 | 39.7126 | -121.4886 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0073708 | OH | Sus | 31696057 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946882 | 0 | EPSS Ckt | N | 2024
47569 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 417066 | 2024-06-05 | 1206 | 20240605 | 1536 | 2476308 | 210 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 3570 | 40.6627 | -122.4938 | No | Clear;32-90 F |  |  | 24-0073644 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1946856 | 0 | EPSS Ckt | Y | 2024 | NA
47583 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | FUSE | 4281 | 2024-06-08 | 1153 | 20240608 | 2125 | 2480074 | 572 | Distribution Circuit | 3rd Party | Vehicle | 96 | 11016 | 40.0156 | -122.4333 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0074961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947726 | 0 | EPSS Ckt | N | 2024
47632 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | SWITCH | 730057 | 2024-06-15 | 2327 | 20240616 | 24 | 2486820 | 57 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 8 | 456 | 39.549 | -121.3486 | No | Clear;32-90 F | Insulator | Broken | 24-0077426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1949599 | 0 | EPSS Ckt | N | 2024
47634 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | RECLOSER | 1466 | 2024-06-16 | 1725 | 20240617 | 1558 | 2487135 | 1353 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 478 | 65334 | 40.7125 | -122.2531 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0077508 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 131448 | No | No | No | 1949661 | 0 | EPSS Ckt | N | 2024 | NONE
47641 | NORTH VALLEY | GLENN | ELK CREEK-1101 | 102781101 | FUSE | 841 | 2024-06-17 | 1326 | 20240621 | 1638 | 2489585 | 5952 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 107136 | 39.2511 | -122.4726 | No | Clear;32-90 F | Pole-Wood | Burned/flashed | 24-0077735 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1950294 | 0 | EPSS Ckt | N | 2024
47664 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | JUMPER | OJ 1 SPAN SS OF CGC 220973377485 | 2024-06-20 | 906 | 20240620 | 1025 | 2490596 | 79 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1027 | 39.7933 | -121.6551 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken | 24-0078579 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950550 | 0 | EPSS Ckt | N | 2024
47679 | NORTH VALLEY | PARADISE | ORO FINO-1101 | 103031101 | FUSE | 26787 | 2024-06-22 | 955 | 20240622 | 1455 | 2492413 | 300 | Distribution Circuit | Animal | Other | 10 | 3000 | 39.8655 | -121.6083 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0079380 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1951035 | 0 | EPSS Ckt | N | 2024
47689 | NORTH VALLEY | LAS PLUMAS | BUCKS CREEK-1103 | 102211103 | SWITCH | 855133 | 2024-06-24 | 1040 | 20240624 | 1133 | 2493694 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 333 | 17649 | 39.9111 | -121.327 | No | Clear;32-90 F | Jumper | Deteriorated | 24-0079704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1951385 | 0 | EPSS Ckt | N | 2024
47712 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118798224467 | 2024-06-28 | 929 | 20240628 | 957 | 2498432 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 40.004 | -122.4302 | No | Clear;32-90 F | Fuse | Broken | 24-0081713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952777 | 0 | EPSS Ckt | N | 2024
47713 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118729724481 | 2024-06-28 | 1026 | 20240628 | 1044 | 2498441 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 36 | 40.0042 | -122.4547 | No | Clear;32-90 F | Fuse | Broken | 24-0081714 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952778 | 0 | EPSS Ckt | N | 2024
47714 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118719424508 | 2024-06-28 | 1056 | 20240628 | 1248 | 2498549 | 112 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 336 | 40.005 | -122.4584 | No | Clear;32-90 F | Fuse | Broken | 24-0081759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952812 | 0 | EPSS Ckt | N | 2024
47717 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | FUSE | 52521 | 2024-06-29 | 957 | 20240629 | 1200 | 2499223 | 123 | Distribution Circuit | Animal | Other | 2 | 246 | 39.8529 | -121.6628 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0082030 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1952971 | 0 | EPSS Ckt | N | 2024
47731 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118808325011 | 2024-07-01 | 1324 | 20240701 | 1353 | 2500865 | 29 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 87 | 40.0189 | -122.4267 | No | Clear;Above 90 | Secondary | Broken | 24-0082537 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953352 | 0 | EPSS Ckt | N | 2024
47735 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | RECLOSER | 180398 | 2024-07-02 | 29 | 20240702 | 1852 | 2501429 | 1103 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 14339 | 39.7338 | -121.4964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953439 | 0 | EPSS Ckt | N | 2024 | NONE
47736 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | RECLOSER | 641808 | 2024-07-02 | 29 | 20240702 | 1859 | 2501451 | 1110 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 182 | 200019 | 39.7407 | -121.4962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953442 | 0 | EPSS Ckt | N | 2024 | NONE
47738 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | SWITCH | 669889 | 2024-07-02 | 29 | 20240702 | 2112 | 2502810 | 1243 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 117 | 145431 | 39.7332 | -121.495 | No | Clear-Strong Winds;32-90 F | Insulator | Broken | 24-0082476 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953682 | 0 | EPSS Ckt | N | 2024
47748 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2024-07-02 | 503 | 20240702 | 1857 | 2501537 | 834 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 1668 | 39.8995 | -122.6127 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953474 | 0 | EPSS Ckt | N | 2024 | NA
47751 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 2024-07-02 | 920 | 20240702 | 1203 | 2501723 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 749 | 108518 | 40.351 | -121.7811 | No | Clear-Heat Wave;32-90 F |  |  | 24-0082878 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1953548 | 0 | EPSS Ckt | Y | 2024 | B PHASE GRD- INST OC
47768 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2024-07-03 | 7 | 20240703 | 1710 | 2503355 | 1023 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 2046 | 39.8995 | -122.6127 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083224 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953805 | 0 | EPSS Ckt | N | 2024 | NONE
47772 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | RECLOSER | 180398 | 2024-07-03 | 103 | 20240703 | 1646 | 2503364 | 943 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 159 | 149009 | 39.7338 | -121.4964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083220 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953810 | 0 | EPSS Ckt | N | 2024 | NONE
47773 | NORTH VALLEY | PARADISE | CLARK ROAD-1102 | 103091102 | RECLOSER | 641808 | 2024-07-03 | 103 | 20240703 | 1648 | 2503377 | 945 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 153 | 144585 | 39.7407 | -121.4962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083220 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953817 | 0 | EPSS Ckt | N | 2024 | NONE
47785 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | RECLOSER | 98896 | 2024-07-04 | 1810 | 20240704 | 2156 | 2505365 | 226 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 47 | 10591 | 40.3607 | -122.9513 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084094 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1954179 | 0 | EPSS Ckt | Y | 2024 | A & C
47790 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | FUSE | 787 | 2024-07-04 | 2127 | 20240704 | 2331 | 2505517 | 124 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 372 | 39.5498 | -121.3448 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0084127 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954209 | 0 | EPSS Ckt | N | 2024
47795 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | TRANSFORMER | 118647444165 | 2024-07-05 | 732 | 20240705 | 1017 | 2505741 | 165 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 330 | 40.5445 | -122.4878 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0084219 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1954281 | 0 | EPSS Ckt | N | 2024
47825 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | RECLOSER | 1466 | 2024-07-07 | 2311 | 20240708 | 916 | 2509607 | 605 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 478 | 289190 | 40.7125 | -122.2531 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0085023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | Yes | No | 1954873 | 0 | EPSS Ckt | Y | 2024 | A & C
47839 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | RECLOSER | 65932 | 2024-07-09 | 925 | 20240709 | 1050 | 2511375 | 85 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1078 | 60214 | 39.8705 | -121.6503 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0085545 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1955283 | 0 | EPSS Ckt | Y | 2024 | A & C
47849 | NORTH VALLEY | SHASTA | GIRVAN-1102 | 103401102 | JUMPER | OJ'S 2 POLES N/OF CGC 118719045683 | 2024-07-10 | 747 | 20240710 | 949 | 2512131 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 122 | 40.587 | -122.4625 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0085940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1955492 | 0 | EPSS Ckt | N | 2024
47877 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118710524587 | 2024-07-13 | 823 | 20240713 | 1127 | 2515835 | 184 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 184 | 40.0071 | -122.4617 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0087484 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956429 | 0 | EPSS Ckt | N | 2024
47878 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118732724679 | 2024-07-13 | 903 | 20240713 | 1135 | 2515838 | 152 | Transformer only | Company Initiated | Construction Activity/equip- company | 2 | 304 | 40.0097 | -122.4536 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0087485 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956431 | 0 | EPSS Ckt | N | 2024
47881 | NORTH VALLEY | TEHEMA | CORNING-1101 | 103331101 | TRANSFORMER | 118770524765 | 2024-07-14 | 838 | 20240714 | 1004 | 2516553 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 86 | 40.0121 | -122.4403 | No | Overcast;32-90 F | Transformer (OH) | Normal | 24-0087697 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956606 | 0 | EPSS Ckt | N | 2024
47892 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | FUSE | 908917 | 2024-07-15 | 1109 | 20240715 | 1241 | 2517348 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 92 | 39.7273 | -121.4831 | No | Clear;32-90 F | Other | Broken | 24-0087930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1956891 | 0 | EPSS Ckt | N | 2024
47910 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | TRANSFORMER | 221047178061 | 2024-07-19 | 2053 | 20240720 | 1245 | 2521479 | 952 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1904 | 39.8088 | -121.6278 | No | Clear;Above 90 | Secondary | Broken | 24-0089955 | OH | Sus | 46282480 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958042 | 0 | EPSS Ckt | N | 2024
47919 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2024-07-21 | 1106 | 20240722 | 12 | 2522403 | 786 | Distribution Circuit | 3rd Party | Vehicle | 348 | 154294 | 39.8787 | -121.6118 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0090164 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958236 | 0 | EPSS Ckt | Y | 2024 | B & C PHASE
47920 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | TRANSFORMER | 119339550798 | 2024-07-21 | 1320 | 20240722 | 215 | 2522469 | 770 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2098 | 40.7273 | -122.2391 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0090191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1958257 | 0 | EPSS Ckt | N | 2024
47969 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 2024-07-25 | 1652 | 20240813 | 1055 | 2526894 | 27003 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1098 | 58070 | 39.872 | -121.612 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0092156 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 7017018 | No | Yes | No | 1959543 | 0 | EPSS Ckt | N | 2024 | NONE
47970 | NORTH VALLEY | CHICO | ORO FINO-1102 | 103031102 | TRANSFORMER | 220894780720 | 2024-07-25 | 1652 | 20240725 | 1658 | 2528686 | 6 | Transformer only | Environmental/External | Fire- Forest/Grass | 1 | 6 | 39.8825 | -121.6813 | No | Clear;32-90 F | Transformer (OH) | Burned/flashed | 24-0092869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1960097 | 0 | EPSS Ckt | N | 2024
47999 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | COHASSET TEMP GEN LR | 2024-07-31 | 1207 | 20240731 | 1809 | 2531240 | 362 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 178 | 64420 | 39.9267 | -121.7318 | No | Clear;32-90 F |  |  | 24-0091680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Three Phase Fault | 0 | No | No | No | 1961077 | 0 | EPSS Ckt | N | 2024 | A B C
48026 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | COHASSET TEMP GEN LR | 2024-08-05 | 1825 | 20240805 | 1915 | 2535302 | 50 | Distribution Circuit | Company Initiated | Return Circuit Normal | 235 | 4800 | 39.9267 | -121.7318 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0091680 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962156 | 0 | EPSS Ckt | N | 2024 | NONE
48058 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | FUSE | 26487 | 2024-08-10 | 938 | 20240810 | 1047 | 2539266 | 69 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 414 | 39.9402 | -121.7238 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0097971 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963431 | 0 | EPSS Ckt | N | 2024
48061 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1590 | 2024-08-10 | 1638 | 20240810 | 1939 | 2539526 | 181 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 54 | 9774 | 40.6175 | -122.4626 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0098023 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1963477 | 0 | EPSS Ckt | N | 2024 | NONE
48065 | NORTH VALLEY | SHASTA | OREGON TRAIL-1103 | 103521103 | TRANSFORMER | 100000032123 | 2024-08-11 | 1506 | 20240811 | 1936 | 2539815 | 270 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 270 | 40.6117 | -122.428 | No | Clear;Above 90 |  |  | 24-0098095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1963563 | 0 | EPSS Ckt | N | 2024
48180 | NORTH VALLEY | TEHEMA | RAWSON-1103 | 103531103 | FUSE | 4273 | 2024-08-27 | 1926 | 20240828 | 1237 | 2553202 | 1031 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1031 | 40.2157 | -122.1104 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0103785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1967599 | 0 | EPSS Ckt | N | 2024
48205 | NORTH VALLEY | LAS PLUMAS | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103/2 | 2024-08-31 | 1755 | 20240902 | 2042 | 2556641 | 2030 | Distribution Circuit | Equipment Failure/Involved | Underground | 337 | 649502 | 39.9117 | -121.3266 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0105621 | UG | Sus | 46307585 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1968672 | 0 | EPSS Ckt | Y | 2024 | B & GRD
48230 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2024-09-05 | 850 | 20240905 | 1134 | 2560061 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 348 | 57072 | 39.8787 | -121.6118 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0107092 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969656 | 0 | EPSS Ckt | N | 2024 | NONE
48232 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRIP-SAVER | 1243 | 2024-09-05 | 948 | 20240905 | 1235 | 2560165 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 9185 | 39.7896 | -121.6561 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0107167 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969723 | 0 | EPSS Ckt | N | 2024 | NONE
48263 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 1462 | 2024-09-11 | 1343 | 20240911 | 1705 | 2565605 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 5454 | 40.6672 | -122.6333 | No | Clear;32-90 F | Crossarm- Wood | Burned/flashed | 24-0109749 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1971358 | 0 | EPSS Ckt | N | 2024 | NA
48270 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | TRANSFORMER | 118705445789 | 2024-09-12 | 125 | 20240912 | 634 | 2566102 | 309 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 309 | 40.5892 | -122.4673 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0109999 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1971462 | 0 | EPSS Ckt | N | 2024
48274 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1464 | 2024-09-12 | 931 | 20240912 | 1144 | 2566445 | 133 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 9727 | 40.7131 | -122.6353 | No | Clear;32-90 F |  |  | 24-0110154 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1971632 | 0 | EPSS Ckt | Y | 2024 | A AND C
48288 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1892 | 2024-09-15 | 1612 | 20240915 | 1738 | 2568925 | 86 | Distribution Circuit | Environmental/External | Lightning | 3 | 258 | 40.7018 | -122.6403 | No | Overcast;32-90 F | Capacitor | Burned/flashed | 24-0111202 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1972279 | 0 | EPSS Ckt | Y | 2024 | GRD & INST OC
48394 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | JUMPER | OJ'S @ CGC 220865779950 TWD EAST | 2024-09-25 | 2228 | 20240926 | 328 | 2577856 | 300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1200 | 39.8612 | -121.692 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0115722 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975384 | 0 | EPSS Ckt | N | 2024
48427 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | JUMPER | OJ 2 SPANS SS OF CGC# 119318750197 | 2024-09-29 | 1110 | 20240929 | 1418 | 2580640 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 564 | 40.7115 | -122.2481 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0117051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976332 | 0 | EPSS Ckt | N | 2024
48428 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | JUMPER | OJ 5 SPANS S/OF CGC# 221341377010 | 2024-09-29 | 1117 | 20240929 | 1347 | 2580642 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 300 | 39.7791 | -121.5217 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0117053 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976334 | 0 | EPSS Ckt | N | 2024
48437 | NORTH VALLEY | PARADISE | CRESTA PH-1101 | 102251101 | RECLOSER | 546650 | 2024-09-30 | 438 | 20240930 | 1826 | 2580922 | 828 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 6820 | 39.8308 | -121.4091 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117068 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976410 | 0 | EPSS Ckt | N | 2024 | NONE
48438 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2024-09-30 | 440 | 20240930 | 1904 | 2580923 | 850 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 229 | 191750 | 39.7407 | -121.4962 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0117077 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976411 | 0 | EPSS Ckt | N | 2024 | NONE
48460 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 2024-09-30 | 818 | 20240930 | 1432 | 2581087 | 374 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 67 | 25058 | 40.8524 | -122.3324 | No | Clear;32-90 F | Recloser | Normal | 24-0117070 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976487 | 0 | EPSS Ckt | N | 2024 | NA
48463 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | RECLOSER | 1466 | 2024-09-30 | 818 | 20240930 | 1730 | 2581168 | 552 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 472 | 260544 | 40.7125 | -122.2531 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117078 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976520 | 0 | EPSS Ckt | N | 2024 | NONE
48469 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 2024-09-30 | 927 | 20240930 | 1738 | 2581284 | 491 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 194 | 95254 | 40.5176 | -122.5057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976576 | 0 | EPSS Ckt | N | 2024 | NONE
48473 | NORTH VALLEY | SHASTA | JESSUP-1101 | 103441101 | SWITCH | CUS48 | 2024-09-30 | 927 | 20240930 | 1032 | 2581414 | 65 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 65 | 40.4653 | -122.4806 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117090 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1976605 | 0 | EPSS Ckt | N | 2024
48492 | NORTH VALLEY | SHASTA | JESSUP-1101 | 103441101 | TRANSFORMER | 118717241959 | 2024-10-03 | 2040 | 20241003 | 2120 | 2585219 | 40 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 40 | 40.4841 | -122.4623 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0119240 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1977700 | 0 | EPSS Ckt | N | 2024
48556 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | OCB | 1102/2 | 2024-10-17 | 1257 | 20241018 | 1019 | 2597167 | 1282 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 5128 | 40.6868 | -122.6405 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981331 | 0 | EPSS Ckt | N | 2024 | NONE
48557 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 1462 | 2024-10-17 | 1257 | 20241018 | 1024 | 2597296 | 1287 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 27 | 34749 | 40.6672 | -122.6333 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981362 | 0 | EPSS Ckt | N | 2024 | NONE
48558 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 2024-10-17 | 1257 | 20241018 | 1023 | 2597301 | 1286 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 9002 | 40.6669 | -122.6336 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981364 | 0 | EPSS Ckt | N | 2024 | NONE
48568 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | OCB | 1101/2 | 2024-10-17 | 1259 | 20241018 | 1004 | 2597174 | 1265 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 176 | 222640 | 40.6869 | -122.6405 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981336 | 0 | EPSS Ckt | N | 2024 | NONE
48569 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1892 | 2024-10-17 | 1300 | 20241018 | 1009 | 2597261 | 1269 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 3807 | 40.7018 | -122.6403 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981354 | 0 | EPSS Ckt | N | 2024 | NONE
48570 | NORTH VALLEY | SHASTA | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1464 | 2024-10-17 | 1300 | 20241018 | 1011 | 2597279 | 1271 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 75 | 95325 | 40.7131 | -122.6353 | Yes | Clear-Rain;32-90 F | Conductor- Overhead | Normal | 24-0123737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981358 | 0 | EPSS Ckt | N | 2024 | NONE
48572 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 1588 | 2024-10-17 | 1303 | 20241019 | 939 | 2597183 | 2669 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 316 | 799390 | 40.617 | -122.4963 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981334 | 0 | EPSS Ckt | N | 2024 | NONE
48574 | NORTH VALLEY | SHASTA | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 2024-10-17 | 1304 | 20241019 | 936 | 2597173 | 2672 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 322 | 845865 | 40.5176 | -122.5057 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123776 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981332 | 0 | EPSS Ckt | N | 2024 | NONE
48580 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | FUSE | 2735 | 2024-10-17 | 1309 | 20241019 | 1125 | 2597374 | 2776 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2776 | 40.6659 | -122.5009 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981392 | 0 | EPSS Ckt | N | 2024
48582 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | RECLOSER | 417066 | 2024-10-17 | 1310 | 20241019 | 947 | 2597360 | 2677 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 16 | 42832 | 40.6627 | -122.4938 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981387 | 0 | EPSS Ckt | N | 2024 | NONE
48583 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | SWITCH | 711465 | 2024-10-17 | 1310 | 20241019 | 1124 | 2597371 | 2774 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2774 | 40.6619 | -122.4865 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123780 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981391 | 0 | EPSS Ckt | N | 2024
48598 | NORTH VALLEY | SHASTA | STILLWATER-1102 | 103561102 | RECLOSER | 1466 | 2024-10-17 | 1327 | 20241019 | 1234 | 2597264 | 2827 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 751 | 2114707 | 40.7125 | -122.2531 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123851 | OH | Sus | 8216649 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981355 | 0 | EPSS Ckt | N | 2024 | NONE
48607 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2024-10-17 | 1410 | 20241019 | 1543 | 2597391 | 2973 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 5946 | 39.8995 | -122.6127 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981398 | 0 | EPSS Ckt | N | 2024 | NONE
48614 | NORTH VALLEY | TEHEMA | WILDWOOD-1101 | 103611101 | FUSE | 1671 | 2024-10-17 | 1612 | 20241017 | 1752 | 2597472 | 100 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 38 | 3800 | 40.3889 | -123.0589 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981421 | 0 | EPSS Ckt | N | 2024
48624 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 180398 | 2024-10-18 | 1950 | 20241019 | 1845 | 2598988 | 1375 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 38 | 52250 | 39.7338 | -121.4964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981855 | 0 | EPSS Ckt | N | 2024 | NONE
48625 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2024-10-18 | 1950 | 20241019 | 1828 | 2598991 | 1358 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 156 | 211848 | 39.7407 | -121.4962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981858 | 0 | EPSS Ckt | N | 2024 | NONE
48627 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2024-10-18 | 1952 | 20241019 | 1722 | 2598989 | 1288 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 858 | 1021165 | 39.8787 | -121.6118 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123967 | OH | Sus | 8216649 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981856 | 0 | EPSS Ckt | N | 2024 | NONE
48628 | NORTH VALLEY | PARADISE | CRESTA PH-1101 | 102251101 | RECLOSER | 103126 | 2024-10-18 | 1953 | 20241019 | 1417 | 2598992 | 1104 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 8832 | 39.8253 | -121.4098 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981859 | 0 | EPSS Ckt | N | 2024 | NONE
48629 | NORTH VALLEY | PARADISE | CRESTA PH-1101 | 102251101 | RECLOSER | 546650 | 2024-10-18 | 1953 | 20241019 | 1421 | 2598994 | 1108 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1108 | 39.8308 | -121.4091 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124056 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981861 | 0 | EPSS Ckt | N | 2024 | NONE
48630 | NORTH VALLEY | LAS PLUMAS | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103/2 | 2024-10-18 | 1955 | 20241019 | 1653 | 2598995 | 1258 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 1258 | 39.9117 | -121.3266 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981862 | 0 | EPSS Ckt | N | 2024 | N/A
48668 | NORTH VALLEY | SHASTA | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 2024-10-24 | 1548 | 20241024 | 1615 | s1999148 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 67 | 1809 | 40.8524 | -122.3324 | No | Clear;32-90 F | Recloser | Normal | 24-0120584 | OH | Sus | 31700868 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1999148 | 0 | EPSS Ckt | Y | 2024 | NONE RPTD ON SWLOG
48680 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | JUMPER | OJ IN SPAN SS OF CGC 100000046930 | 2024-10-26 | 1331 | 20241026 | 1557 | 2604910 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1022 | 39.7879 | -121.5267 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0128194 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983799 | 0 | EPSS Ckt | N | 2024
48738 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 180398 | 2024-11-04 | 441 | 20241104 | 1021 | 2612813 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 33578 | 39.7338 | -121.4964 | No | Clear;32-90 F | Conductor- Overhead | Together | 24-0131225 | OH | Sus | 46378735 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986060 | 0 | EPSS Ckt | Y | 2024 | B & C- INST OC
48771 | NORTH VALLEY | TEHEMA | CORNING-1102 | 103331102 | RECLOSER | 493022 | 2024-11-06 | 535 | 20241107 | 1213 | 2615609 | 1838 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 3676 | 39.8995 | -122.6127 | No | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131748 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986954 | 0 | EPSS Ckt | N | 2024 | NONE
48774 | NORTH VALLEY | LAS PLUMAS | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103/2 | 2024-11-06 | 701 | 20241107 | 740 | 2615705 | 1479 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 4437 | 39.9117 | -121.3266 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131735 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986969 | 0 | EPSS Ckt | N | 2024 | NONE
48776 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 180398 | 2024-11-06 | 704 | 20241107 | 1239 | 2615735 | 1775 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 200 | 355000 | 39.7338 | -121.4964 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131728 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986977 | 0 | EPSS Ckt | N | 2024 | NONE
48777 | NORTH VALLEY | PARADISE | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 2024-11-06 | 704 | 20241107 | 1237 | 2615742 | 1773 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 156 | 276588 | 39.7407 | -121.4962 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131728 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986981 | 0 | EPSS Ckt | N | 2024 | NONE
48780 | NORTH VALLEY | PARADISE | CRESTA PH-1101 | 102251101 | RECLOSER | 546650 | 2024-11-06 | 704 | 20241107 | 944 | 2615706 | 1600 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 14336 | 39.8308 | -121.4091 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131741 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986970 | 0 | EPSS Ckt | N | 2024 | NONE
48860 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2931 | 2024-11-19 | 2338 | 20241120 | 125 | 2629952 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 428 | 40.6547 | -122.6661 | No | Clear;32-90 F |  |  | 24-0137410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991151 | 0 | EPSS Ckt | N | 2024
48865 | NORTH VALLEY | SHASTA | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 2024-11-20 | 754 | 20241123 | 1756 | 2630210 | 2996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 300867 | 40.9921 | -121.9718 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Multi-Fault | 0 | No | Yes | No | 1991201 | 0 | EPSS Ckt | N | 2024 | A- B- GRD
48869 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2931 | 2024-11-20 | 1054 | 20241122 | 2030 | 2630677 | 3109 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 12436 | 40.6547 | -122.6661 | No | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken | 24-0137732 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1991418 | 0 | EPSS Ckt | N | 2024
48873 | NORTH VALLEY | SHASTA | ROUND MOUNTAIN-1101 | 109001101 | FUSE | 6449 | 2024-11-20 | 1409 | 20241120 | 1640 | 2631321 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 1510 | 40.8446 | -121.9225 | No | Overcast-Fog-Snow;32-90 F |  |  | 24-0138000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991573 | 0 | Non-EPSS | N | 2024
48901 | NORTH VALLEY | CHICO | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 2024-11-21 | 1049 | 20241121 | 2104 | 2632615 | 608 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 15996 | 39.839 | -121.7019 | No | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 24-0138340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1991811 | 0 | EPSS Ckt | N | 2024 | NONE
48908 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | TRANSFORMER | 118363348007 | 2024-11-22 | 442 | 20241122 | 2000 | 2633964 | 918 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 918 | 40.6495 | -122.5909 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0138823 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992044 | 0 | EPSS Ckt | N | 2024
48929 | NORTH VALLEY | CHICO | BUTTE-1105 | 103081105 | TRIP-SAVER | 1243 | 2024-11-22 | 2158 | 20241123 | 1245 | 2635610 | 887 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 48785 | 39.7896 | -121.6561 | No | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken | 24-0139354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992363 | 0 | EPSS Ckt | N | 2024 | TRIP
48948 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2931 | 2024-11-25 | 918 | 20241126 | 1431 | 2637443 | 1753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7012 | 40.6547 | -122.6661 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken | 24-0140092 | OH | Sus | 46400129 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1992812 | 0 | EPSS Ckt | N | 2024
48986 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | SWITCH | 300961 | 2024-12-03 | 1235 | 20241203 | 1313 | 2642984 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 646 | 40.6628 | -122.4951 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0142159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994090 | 0 | EPSS Ckt | N | 2024
48997 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | JUMPER | OJ 1 E/OF CGC 118636246192 | 2024-12-04 | 1931 | 20241204 | 2250 | 2644264 | 199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 199 | 40.5999 | -122.4918 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0142730 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994537 | 0 | EPSS Ckt | N | 2024
49015 | NORTH VALLEY | PARADISE | ORO FINO-1102 | 103031102 | RECLOSER | 787504 | 2024-12-09 | 202 | 20241209 | 1135 | 2647193 | 573 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 348 | 199404 | 39.8787 | -121.6118 | No | Clear;32-90 F |  |  | 24-0143786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1995539 | 0 | EPSS Ckt | Y | 2024 | GRD OR SGF- INST OC
49048 | NORTH VALLEY | OROVILLE | KANAKA-1101 | 103221101 | TRANSFORMER | 100000083438 | 2024-12-13 | 1105 | 20241213 | 1620 | 2651788 | 315 | Transformer only | Vegetation | Tree - fell into line | 1 | 315 | 39.5538 | -121.335 | No | Overcast-Fog-Rain;32-90 F | Service conductor | Broken- wire on ground | 24-0144866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997169 | 0 | EPSS Ckt | N | 2024
49109 | NORTH VALLEY | SHASTA | FRENCH GULCH-1102 | 103381102 | FUSE | 2931 | 2024-12-14 | 1934 | 20241214 | 2156 | 2660525 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 568 | 40.6547 | -122.6661 | Yes | Clear-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0146072 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998414 | 1 | EPSS Ckt | N | 2024
49110 | NORTH VALLEY | SHASTA | KESWICK-1101 | 103451101 | TRANSFORMER | 118630946712 | 2024-12-15 | 143 | 20241215 | 953 | 2660806 | 490 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 490 | 40.6146 | -122.4942 | No | Partly Cloudy;32-90 F |  |  | 24-0146163 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998512 | 0 | EPSS Ckt | N | 2024
49139 | NORTH VALLEY | TEHEMA | VOLTA-1101 | 102541101 | TRANSFORMER | 120519535555 | 2024-12-19 | 1606 | 20241219 | 2000 | 2666199 | 234 | Transformer only | 3rd Party | Tree - cutting- 3rd party | 6 | 1404 | 40.31 | -121.8158 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0147169 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999900 | 0 | EPSS Ckt | N | 2024
49151 | NORTH VALLEY | SHASTA | OREGON TRAIL-1102 | 103521102 | FUSE | 3177 | 2024-12-21 | 1356 | 20241221 | 1849 | 2667442 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 13185 | 40.6666 | -122.4016 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0147335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 2000291 | 0 | EPSS Ckt | N | 2024
49154 | NORTH VALLEY | CHICO | SYCAMORE CREEK-1111 | 102971111 | FUSE | 683 | 2024-12-22 | 1347 | 20241222 | 1529 | 2667799 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 2448 | 39.9321 | -121.7291 | No | Overcast;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0147393 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 2000377 | 0 | EPSS Ckt | N | 2024
52685 | SACRAMENTO | COLUSA | ARBUCKLE 1104 | 62081104 | FUSE | 4607 | 2023-01-04 | 1549 | 20230105 | 1318 | 1914948 | 1289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 22354 | 38.9511 | -122.0885 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0006272 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1796577 | 1 | EPSS Ckt | N | 2023
53370 | SACRAMENTO | COLUSA | ARBUCKLE-1104 | 62081104 | JUMPER | OJ'S 1 POLE E/OF CGC 219724246429 | 2023-02-07 | 1449 | 20230207 | 1539 | 1979373 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 97 | 38.9421 | -122.0978 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0026334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1811344 | 0 | EPSS Ckt | N | 2023
53426 | SACRAMENTO | SOLANO | VACAVILLE-1108 | 63601108 | FUSE | 9167 | 2023-02-14 | 1128 | 20230214 | 1356 | 1984779 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 4736 | 38.4002 | -122.041 | No | Clear;32-90 F |  |  | 23-0028726 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1813192 | 0 | EPSS Ckt | N | 2023
53470 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | FUSE | 391 | 2023-02-21 | 642 | 20230221 | 815 | 1989734 | 93 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2232 | 38.2714 | -122.1672 | Yes | Clear;32-90F |  |  | 23-0030796 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1814555 | 0 | EPSS Ckt | N | 2023
53476 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | RECLOSER | 46012 | 2023-02-21 | 1344 | 20230222 | 317 | 1990991 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 280 | 168470 | 38.4836 | -122.0249 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031186 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1814876 | 0 | EPSS Ckt | N | 2023 | A GRD
53567 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 13372 | 2023-02-25 | 1544 | 20230226 | 1539 | 2008832 | 1435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 15785 | 38.7934 | -122.0621 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | Yes | 1818190 | 0 | EPSS Ckt | N | 2023 | NONE
53587 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | FUSE | 1271 | 2023-02-28 | 1254 | 20230303 | 1821 | 2018171 | 4647 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 195174 | 39.3812 | -121.1439 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038107 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820363 | 0 | EPSS Ckt | N | 2023
53602 | SACRAMENTO | SOLANO | VACAVILLE-1108 | 63601108 | TRANSFORMER | 219849827102 | 2023-03-01 | 1410 | 20230302 | 1442 | 2018427 | 1472 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2944 | 38.4108 | -122.054 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0038283 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820489 | 0 | EPSS Ckt | N | 2023
53890 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | FUSE | 6421 | 2023-03-30 | 1158 | 20230330 | 1414 | 2074381 | 136 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 136 | 38.471 | -122.0315 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0054982 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831956 | 0 | EPSS Ckt | N | 2023
53950 | SACRAMENTO | COLUSA | ARBUCKLE-1104 | 62081104 | FUSE | 14531 | 2023-04-09 | 706 | 20230409 | 1042 | 2083552 | 216 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 10 | 2160 | 38.952 | -122.0983 | No | Clear;32-90 F |  |  | 23-0058866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834315 | 0 | EPSS Ckt | N | 2023
53998 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | FUSE | 391 | 2023-04-14 | 617 | 20230414 | 805 | 2088244 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 2592 | 38.2714 | -122.1672 | No | Clear;32-90 F |  |  | 23-0060991 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1835717 | 0 | EPSS Ckt | N | 2023
54050 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 75395 | 2023-04-21 | 1629 | 20230421 | 2140 | 2094065 | 311 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 311 | 38.7766 | -122.172 | No | Clear;32-90 F |  |  | 23-0063663 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1837631 | 0 | EPSS Ckt | N | 2023
54114 | SACRAMENTO | COLUSA | ARBUCKLE-1104 | 62081104 | TRANSFORMER | 219753747086 | 2023-04-28 | 1104 | 20230428 | 1416 | 2099311 | 192 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 192 | 38.9592 | -122.0876 | No | Clear;32-90 F |  |  | 23-0066102 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1839345 | 0 | EPSS Ckt | N | 2023
54260 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | FUSE | 21101 | 2023-05-18 | 848 | 20230518 | 1511 | 2115551 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 383 | 38.501 | -122.0414 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072973 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844084 | 0 | EPSS Ckt | N | 2023
54276 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | TRANSFORMER | 219298844522 | 2023-05-19 | 1530 | 20230519 | 1830 | 2117225 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | 38.8895 | -122.2473 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844542 | 0 | EPSS Ckt | N | 2023
54376 | SACRAMENTO | COLUSA | ARBUCKLE-1104 | 62081104 | TRANSFORMER | 219719846854 | 2023-06-05 | 1101 | 20230605 | 1809 | 2129144 | 428 | Transformer only | Environmental/External | Flood/Erosion | 3 | 1284 | 38.953 | -122.0995 | No | Partly Cloudy;32-90 F | Transformer | Broken | 23-0078943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848051 | 0 | EPSS Ckt | N | 2023
54400 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | JUMPER | OJS 1 SS OF MTR# 1008919521 | 2023-06-08 | 2124 | 20230609 | 236 | 2133155 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 624 | 38.8867 | -122.2396 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0080553 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1849158 | 0 | EPSS Ckt | N | 2023
54403 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | RECLOSER | 669720 | 2023-06-09 | 9 | 20230609 | 1539 | 2133586 | 623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 12064 | 38.9509 | -122.0979 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0080604 | OH | Sus | 31651808 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1849390 | 0 | Non-EPSS | N | 2023 | SGF & INSTA
54452 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | TRANSFORMER | 219752246516 | 2023-06-17 | 845 | 20230617 | 918 | 2139205 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 33 | 38.9438 | -122.0881 | No | Clear;32-90 F | Secondary | Broken | 23-0083344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851287 | 0 | Non-EPSS | N | 2023
54489 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | FUSE | 12057 | 2023-06-24 | 1702 | 20230624 | 2049 | 2145025 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1589 | 38.2817 | -122.1272 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0085359 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852903 | 0 | EPSS Ckt | N | 2023
54812 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | FUSE | 12057 | 2023-08-07 | 1227 | 20230808 | 500 | 2184614 | 993 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 6951 | 38.2817 | -122.1272 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0101323 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1863742 | 0 | EPSS Ckt | N | 2023
54963 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | SWITCH | 745850 | 2023-08-30 | 416 | 20230830 | 1731 | 2205548 | 793 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 22 | 17169 | 38.7662 | -122.1746 | No | Clear;32-90 F |  |  | 23-0110053 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1870040 | 0 | EPSS Ckt | N | 2023
55036 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | OTHER | J38112 TWD T661986 | 2023-09-13 | 2312 | 20230914 | 128 | 2218353 | 136 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 136 | 38.281 | -122.1236 | No | Clear;32-90 F | Transformer (UG) | Leaking | 23-0116180 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873852 | 0 | EPSS Ckt | N | 2023
55049 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | RECLOSER | 5202 | 2023-09-16 | 831 | 20230916 | 1216 | 2220436 | 225 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 207 | 46575 | 39.3398 | -121.1945 | No | Clear;32-90 F |  |  | 23-0117401 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1874482 | 0 | EPSS Ckt | Y | 2023 | A GRD
55305 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | FUSE | 69097 | 2023-10-27 | 1153 | 20231027 | 1457 | 2253343 | 184 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 4 | 736 | 38.3085 | -122.1293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133238 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885646 | 0 | EPSS Ckt | N | 2023
55317 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 13372 | 2023-10-29 | 802 | 20231029 | 1342 | 2254681 | 340 | Distribution Circuit | Company Initiated | Other Circuits | 11 | 3740 | 38.7934 | -122.0621 | No | Clear;32-90 F |  |  | 23-0133662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885946 | 0 | EPSS Ckt | N | 2023 | N/A
55449 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | TRANSFORMER | 219725046395 | 2023-11-21 | 655 | 20231121 | 929 | 2274751 | 154 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 154 | 38.9407 | -122.0978 | No | Clear;32-90 F | Fuse | Broken | 23-0141738 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892148 | 0 | Non-EPSS | N | 2023
55467 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | RECLOSER | 69722 | 2023-11-24 | 450 | 20231124 | 1214 | 2276342 | 444 | Distribution Circuit | Animal | Other | 704 | 76140 | 39.3406 | -121.1949 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142586 | OH | Sus | 31677110 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1892520 | 0 | EPSS Ckt | Y | 2023 | B GRD
55479 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | RECLOSER | 1101/2 | 2023-11-25 | 428 | 20231125 | 727 | 2276825 | 179 | Distribution Circuit | Animal | Squirrel | 919 | 146871 | 39.3399 | -121.1959 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0142731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1892638 | 0 | EPSS Ckt | Y | 2023 | BC
55700 | SACRAMENTO | SOLANO | VACAVILLE-1108 | 63601108 | RECLOSER | 922767 | 2024-01-01 | 1514 | 20240102 | 1603 | 2304338 | 1489 | Distribution Circuit | Equipment Failure/Involved | Underground | 418 | 81730 | 38.3838 | -122.0312 | No | Clear;32-90 F | Bushing | Failed/Faulted | 24-0005807 | UG | Sus | 46124906 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1900910 | 0 | EPSS Ckt | N | 2024 | C
55859 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 1963 | 2024-02-02 | 1425 | 20240202 | 1523 | 2332571 | 58 | Distribution Circuit | 3rd Party | Gun Shot | 7 | 406 | 38.771 | -122.1691 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0018734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1908649 | 0 | EPSS Ckt | N | 2024
55998 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 1987 | 2024-02-04 | 1752 | 20240208 | 1120 | 2348995 | 5368 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 80520 | 38.8893 | -122.2389 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911980 | 0 | EPSS Ckt | N | 2024
56285 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 1987 | 2024-02-17 | 1806 | 20240218 | 1052 | 2379159 | 1006 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5025 | 38.8893 | -122.2389 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0030290 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917570 | 1 | EPSS Ckt | N | 2024
56357 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 936212 | 2024-02-25 | 617 | 20240225 | 1101 | 2387254 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 9580 | 38.8894 | -122.2394 | No | Clear;32-90 F | Recloser | Malfunctioning | 24-0033611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1919882 | 0 | EPSS Ckt | N | 2024 | A & C
56460 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | FUSE | 391 | 2024-03-13 | 708 | 20240313 | 931 | 2403172 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3575 | 38.2714 | -122.1672 | No | Clear;32-90 F |  |  | 24-0041376 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1924645 | 0 | EPSS Ckt | N | 2024
56485 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | FUSE | 391 | 2024-03-15 | 656 | 20240315 | 854 | 2405712 | 118 | Distribution Circuit | Animal | Bird found | 25 | 2950 | 38.2714 | -122.1672 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925435 | 0 | EPSS Ckt | N | 2024
56543 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 1963 | 2024-03-23 | 1448 | 20240323 | 1655 | 2412934 | 127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 889 | 38.771 | -122.1691 | No | Clear;32-90 F | Fuse | Burned Open | 24-0046062 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927769 | 0 | EPSS Ckt | N | 2024
56667 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | TRANSFORMER | 219964029885 | 2024-04-11 | 2210 | 20240411 | 2355 | 2429036 | 105 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 210 | 38.4877 | -122.0135 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0053829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1932914 | 0 | EPSS Ckt | N | 2024
56859 | SACRAMENTO | COLUSA | ARBUCKLE-1101 | 62081101 | FUSE | 540881 | 2024-05-08 | 1656 | 20240508 | 1800 | 2449163 | 64 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 64 | 38.9784 | -122.1338 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0063902 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940137 | 1 | EPSS Ckt | N | 2024
56873 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | TRANSFORMER | 219865030680 | 2024-05-09 | 1327 | 20240509 | 1508 | 2449912 | 101 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 101 | 38.5076 | -122.0475 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0064371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Open Circuit | 0 | No | No | No | 1940453 | 0 | EPSS Ckt | N | 2024
56924 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | RECLOSER | 69722 | 2024-05-15 | 2200 | 20240516 | 312 | 2460431 | 312 | Distribution Circuit | Animal | Squirrel | 706 | 162951 | 39.3406 | -121.1949 | No | Clear;32-90 F | Recloser | Burned/flashed | 24-0066617 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1942013 | 0 | EPSS Ckt | N | 2024 | A GRD
56991 | SACRAMENTO | YOLO | PUTAH CREEK-1103 | 63681103 | RECLOSER | 654021 | 2024-05-25 | 1050 | 20240525 | 1459 | 2467436 | 249 | Distribution Circuit | Company Initiated | Coordination failure | 16 | 3984 | 38.4828 | -122.0068 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0069987 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1944198 | 0 | EPSS Ckt | Y | 2024 | A / B
57168 | SACRAMENTO | YOLO | PUTAH CREEK-1103 | 63681103 | RECLOSER | 654021 | 2024-06-21 | 1219 | 20240621 | 1328 | 2491870 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1104 | 38.4828 | -122.0068 | No | Clear;32-90 F |  |  | 24-0079137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1950921 | 0 | EPSS Ckt | Y | 2024 | A GRD
57223 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | RECLOSER | 669720 | 2024-07-02 | 57 | 20240702 | 1323 | 2501455 | 746 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 9698 | 38.9509 | -122.0979 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953446 | 0 | Non-EPSS | N | 2024 | NONE
57225 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 13372 | 2024-07-02 | 100 | 20240702 | 1401 | 2501454 | 761 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 82 | 61906 | 38.7934 | -122.0621 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082338 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953445 | 0 | EPSS Ckt | N | 2024 | NONE
57226 | SACRAMENTO | COLUSA | ARBUCKLE-1101 | 62081101 | SWITCH | 932352 | 2024-07-02 | 109 | 20240702 | 1331 | 2501466 | 742 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 2226 | 38.9757 | -122.1365 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0082310 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953450 | 0 | EPSS Ckt | N | 2024
57230 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 75395 | 2024-07-02 | 234 | 20240702 | 406 | 2501493 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 92 | 38.7766 | -122.172 | No | Clear;32-90 F |  |  | 24-0082766 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953459 | 0 | EPSS Ckt | N | 2024
57256 | SACRAMENTO | COLUSA | ARBUCKLE-1101 | 62081101 | SWITCH | 932352 | 2024-07-03 | 111 | 20240703 | 1423 | 2503369 | 792 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 2376 | 38.9757 | -122.1365 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083249 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953814 | 0 | EPSS Ckt | N | 2024
57257 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | RECLOSER | 669720 | 2024-07-03 | 115 | 20240703 | 1420 | 2503372 | 785 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 10205 | 38.9509 | -122.0979 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0083253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1953816 | 0 | Non-EPSS | N | 2024 | N/A
57386 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 2189 | 2024-07-16 | 1548 | 20240716 | 1658 | 2518458 | 70 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 280 | 38.7915 | -122.044 | No | Clear;Above 90 |  |  | 24-0088631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957259 | 0 | EPSS Ckt | N | 2024
57471 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 2189 | 2024-07-26 | 1233 | 20240726 | 1352 | 2527587 | 79 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 316 | 38.7915 | -122.044 | No | Clear;Above 90 |  |  | 24-0092496 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1959806 | 0 | EPSS Ckt | N | 2024
57530 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 75395 | 2024-08-05 | 1359 | 20240805 | 1524 | 2535160 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 85 | 38.7766 | -122.172 | No | Clear;Above 90 |  |  | 24-0096028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1962136 | 0 | EPSS Ckt | N | 2024
57536 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 2189 | 2024-08-06 | 1037 | 20240806 | 1145 | 2535770 | 68 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 91 | 38.7915 | -122.044 | No | Clear;32-90 F |  |  | 24-0096319 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962391 | 1 | EPSS Ckt | N | 2024
57742 | SACRAMENTO | YOLO | PUTAH CREEK-1103 | 63681103 | RECLOSER | 654021 | 2024-09-08 | 741 | 20240908 | 1017 | 2562429 | 156 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 2496 | 38.4828 | -122.0068 | No | Clear;32-90 F |  |  | 24-0108334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1970348 | 0 | EPSS Ckt | Y | 2024 | a-b
57897 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | JUMPER | LINE AND BUCK 6 SPANS SS OF CGC 219634821930 | 2024-10-03 | 2109 | 20241004 | 256 | 2585250 | 347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 347 | 38.2705 | -122.1239 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0119246 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1977709 | 0 | EPSS Ckt | N | 2024
58008 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | RECLOSER | 669720 | 2024-10-17 | 1635 | 20241019 | 1153 | 2597511 | 2598 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 33774 | 38.9509 | -122.0979 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981430 | 0 | Non-EPSS | N | 2024 | NONE
58011 | SACRAMENTO | COLUSA | ARBUCKLE-1101 | 62081101 | FUSE | 283647 | 2024-10-17 | 1654 | 20241019 | 1202 | 2597547 | 2588 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 12940 | 38.983 | -122.1293 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123813 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981437 | 0 | EPSS Ckt | N | 2024
58012 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | SWITCH | 638434 | 2024-10-17 | 1713 | 20241019 | 1023 | 2597568 | 2470 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 12350 | 38.3015 | -122.1529 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981450 | 0 | EPSS Ckt | N | 2024
58014 | SACRAMENTO | YOLO | PUTAH CREEK-1103 | 63681103 | RECLOSER | 654021 | 2024-10-17 | 1717 | 20241019 | 1528 | 2597565 | 2771 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 57 | 157783 | 38.4828 | -122.0068 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981445 | 0 | EPSS Ckt | N | 2024 | NONE
58024 | SACRAMENTO | SOLANO | VACAVILLE-1108 | 63601108 | RECLOSER | 922767 | 2024-10-17 | 1722 | 20241019 | 1842 | 2597662 | 2960 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 150960 | 38.3838 | -122.0313 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123923 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981474 | 0 | EPSS Ckt | N | 2024 | NONE
58030 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 13372 | 2024-10-17 | 1733 | 20241019 | 1409 | 2597601 | 2676 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 21 | 55872 | 38.7934 | -122.0621 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981453 | 0 | EPSS Ckt | N | 2024 | NONE
58034 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | SWITCH | 787708 | 2024-10-17 | 1745 | 20241019 | 952 | 2597634 | 2407 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 35 | 84245 | 38.2709 | -122.1667 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0123774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981466 | 0 | EPSS Ckt | N | 2024
58084 | SACRAMENTO | SOLANO | JAMESON-1102 | 63801102 | OTHER | T261207 TWD T974368 | 2024-10-23 | 1435 | 20241023 | 1503 | 2602346 | 28 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3 | 84 | 38.2688 | -122.1658 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0106408 | OH | Sus | 35342147 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1983039 | 0 | EPSS Ckt | N | 2024
58192 | SACRAMENTO | SOLANO | VACAVILLE-1108 | 63601108 | RECLOSER | 922767 | 2024-11-05 | 1900 | 20241107 | 1442 | 2614746 | 2622 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 133722 | 38.3838 | -122.0313 | Yes | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Deteriorated | 24-0131775 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986715 | 0 | EPSS Ckt | N | 2024 | NONE
58194 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | RECLOSER | 13372 | 2024-11-05 | 1930 | 20241107 | 1259 | 2614756 | 2471 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 260 | 631207 | 38.7934 | -122.0621 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131739 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986717 | 0 | EPSS Ckt | N | 2024 | NONE
58199 | SACRAMENTO | YOLO | PUTAH CREEK-1102 | 63681102 | RECLOSER | 46012 | 2024-11-05 | 1935 | 20241107 | 1107 | 2614771 | 2372 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 275 | 642215 | 38.4836 | -122.0249 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131745 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986724 | 0 | EPSS Ckt | N | 2024 | NONE
58206 | SACRAMENTO | COLUSA | DUNNIGAN-1103 | 63811103 | FUSE | 4451 | 2024-11-05 | 2230 | 20241107 | 915 | 2615044 | 2078 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 24930 | 38.9394 | -122.1165 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0131796 | OH | Sus | 8216652 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1986821 | 0 | Non-EPSS | N | 2024
58330 | SACRAMENTO | YOLO | MADISON-2101 | 63172101 | FUSE | 1963 | 2024-11-21 | 2006 | 20241122 | 637 | 2633314 | 631 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4417 | 38.771 | -122.1691 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0138704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | Yes | No | 1991959 | 0 | EPSS Ckt | N | 2024
58540 | SACRAMENTO | MARYSVILLE | DOBBINS-1101 | 153741101 | TRANSFORMER | 222267561319 | 2024-12-16 | 857 | 20241216 | 1526 | 2662931 | 389 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 389 | 39.3476 | -121.1983 | No | Rain-Overcast;32-90 F | Transformer | Failed/Faulted | 24-0146603 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998986 | 0 | EPSS Ckt | N | 2024
58614 | SACRAMENTO | SOLANO | JAMESON-1105 | 63801105 | TRANSFORMER | 219635722680 | 2024-12-27 | 641 | 20241228 | 500 | 2670520 | 1339 | Transformer only | Vegetation | Tree - fell into line | 3 | 4017 | 38.2894 | -122.1281 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken | 24-0147918 | OH | Sus | 31720984 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 2001041 | 0 | EPSS Ckt | N | 2024
59699 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR332 | 2023-01-05 | 516 | 20230107 | 1005 | 1920637 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 264488 | 37.3494 | -121.6124 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006994 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Line to Ground | 0 | No | Yes | No | 1797296 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
59719 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 2023-01-07 | 1047 | 20230107 | 1301 | 1926407 | 134 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 9246 | 37.3568 | -121.5253 | Yes | Clear;32-90 F |  |  | 23-0008731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798614 | 0 | EPSS Ckt | N | 2023 | N/A
59719 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 2023-01-07 | 1047 | 20230107 | 1301 | 1926407 | 134 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 69 | 9246 | 37.3568 | -121.5253 | Yes | Clear;32-90 F |  |  | 23-0008731 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JAN | Force Out | 0 | No | No | No | 1798614 | 0 | EPSS Ckt | N | 2023 | N/A
60078 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 2023-02-24 | 649 | 20230226 | 1813 | 2003572 | 3564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 245916 | 37.3568 | -121.5253 | Yes | Clear;32-90 F | Insulator | Broken | 23-0033732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816763 | 0 | EPSS Ckt | N | 2023 | INST
60078 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | 853720 | 2023-02-24 | 649 | 20230226 | 1813 | 2003572 | 3564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 245916 | 37.3568 | -121.5253 | Yes | Clear;32-90 F | Insulator | Broken | 23-0033732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Line | 0 | No | No | No | 1816763 | 0 | EPSS Ckt | N | 2023 | INST
60081 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 92776 | 2023-02-24 | 1104 | 20230226 | 1640 | 2008822 | 3216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 35376 | 37.3709 | -121.6728 | Yes | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035408 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | Yes | No | 1818251 | 0 | EPSS Ckt | N | 2023
60643 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | RECLOSER | XR332 | 2023-06-27 | 1244 | 20230627 | 1904 | 2147065 | 380 | Distribution Circuit | 3rd Party | Other | 92 | 34912 | 37.3494 | -121.6124 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0086121 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUN | Line to Line | 0 | No | No | No | 1853500 | 0 | EPSS Ckt | Y | 2023 | A & C PH
60675 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 317129433087 | 2023-07-04 | 1156 | 20230704 | 1530 | 2154172 | 214 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 214 | 37.4064 | -121.4891 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 23-0088769 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Force Out | 0 | No | No | No | 1855173 | 0 | EPSS Ckt | N | 2023
60698 | SAN JOSE | SAN JOSE | HICKS-2105 | 83432105 | FUSE | 9707 | 2023-07-11 | 633 | 20230711 | 727 | 2159306 | 54 | Distribution Circuit | Animal | Bird found | 96 | 5184 | 37.2215 | -121.8512 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0090681 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | JUL | Line to Ground | 0 | No | No | No | 1856316 | 0 | Non-EPSS | N | 2023
60924 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | TRANSFORMER | 317163031705 | 2023-09-03 | 1405 | 20230903 | 2250 | 2209114 | 525 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1050 | 37.3689 | -121.4768 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0112249 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | SEP | Line to Ground | 0 | No | No | No | 1871054 | 0 | EPSS Ckt | N | 2023
61046 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15541 | 2023-10-10 | 1640 | 20231011 | 9 | 2240166 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 8980 | 37.3922 | -121.4894 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0126732 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | OCT | Force Out | 0 | No | No | No | 1881022 | 0 | EPSS Ckt | N | 2023
61644 | SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 25881 | 2024-02-18 | 1739 | 20240218 | 1925 | 2379881 | 106 | Distribution Circuit | Equipment Failure/Involved | Underground | 65 | 3146 | 37.2225 | -121.8498 | No | Overcast-Rain;32-90 F | Transformer (UG) | Deteriorated | 24-0030410 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Force Out | 0 | No | No | No | 1917740 | 0 | EPSS Ckt | N | 2024
61647 | SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 25881 | 2024-02-19 | 100 | 20240219 | 1051 | 2380247 | 591 | Distribution Circuit | Equipment Failure/Involved | Underground | 75 | 44325 | 37.2225 | -121.8498 | No | Overcast-Heavy Rain;32-90 F | Elbow | Failed/Faulted | 24-0030689 | UG | Sus | 0 | SOUTH BAY AND CENTRAL COAST | FEB | Line to Ground | 0 | No | No | No | 1917915 | 0 | EPSS Ckt | N | 2024
61848 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15541 | 2024-04-04 | 2333 | 20240406 | 1940 | 2424594 | 2647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 41440 | 37.3922 | -121.4894 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051545 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | Yes | No | 1931333 | 1 | EPSS Ckt | N | 2024
61849 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15555 | 2024-04-05 | 11 | 20240406 | 600 | 2423305 | 1789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 8945 | 37.3556 | -121.4714 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken | 24-0051537 | OH | Sus | 46221327 | SOUTH BAY AND CENTRAL COAST | APR | Line to Ground | 0 | No | No | No | 1931327 | 0 | EPSS Ckt | N | 2024
61868 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | SWITCH | 15537 | 2024-04-11 | 2122 | 20240411 | 2336 | 2429004 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 804 | 37.3884 | -121.4659 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 24-0053807 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1932891 | 0 | EPSS Ckt | N | 2024
61871 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | FUSE | 15539 | 2024-04-12 | 1631 | 20240412 | 1833 | 2429618 | 122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1342 | 37.3868 | -121.4664 | No | Overcast;32-90 F | Insulator | Broken | 24-0054195 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | APR | Force Out | 0 | No | No | No | 1933157 | 0 | EPSS Ckt | N | 2024
62025 | SAN JOSE | SAN JOSE | HICKS-2101 | 83432101 | FUSE | 100000103880 | 2024-05-27 | 2120 | 20240527 | 2254 | 2468429 | 94 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 2 | 180 | 37.221 | -121.845 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0070283 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | MAY | Line to Ground | 0 | No | No | No | 1944444 | 0 | EPSS Ckt | N | 2024
62795 | SAN JOSE | SAN JOSE | SWIFT-2110 | 83392110 | JUMPER | 712931 SB | 2024-11-06 | 19 | 20241107 | 1104 | 2617151 | 2085 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2085 | 37.392 | -121.4503 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0131792 | OH | Sus | 0 | SOUTH BAY AND CENTRAL COAST | NOV | None | 0 | No | No | No | 1987313 | 0 | EPSS Ckt | N | 2024
63105 | SIERRA | EL DORADO | PLACERVILLE 2106 | 153082106 | FUSE | 1491 | 2023-01-03 | 703 | 20230103 | 1042 | 1910995 | 219 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1021 | 38.7941 | -120.8199 | No | Clear;32-90 F |  |  | 23-0005051 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1795613 | 1 | EPSS Ckt | N | 2023
63153 | SIERRA | EL DORADO | APPLE HILL 1103 | 153661103 | OCB | 1103/2 | 2023-01-04 | 2050 | 20230105 | 1039 | 1918524 | 829 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1295 | 1073555 | 38.7393 | -120.6773 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006598 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Three Phase Fault | 0 | No | No | No | 1796899 | 0 | EPSS Ckt | N | 2023 | A+B+C
63157 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2027 | 2023-01-04 | 2140 | 20230105 | 1618 | 1919050 | 1118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 131924 | 38.6358 | -120.6358 | Yes | Clear;32-90 F |  |  | 23-0007679 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797871 | 0 | EPSS Ckt | N | 2023
63174 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 2023-01-05 | 232 | 20230105 | 2057 | 1920389 | 1105 | Distribution Circuit | Vegetation | Tree - fell into line | 4774 | 957238 | 38.7394 | -120.6774 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797252 | 0 | EPSS Ckt | N | 2023 | n/a
63175 | SIERRA | NEVADA | ALLEGHANY 1102 | 152101102 | RECLOSER | 1102/2 | 2023-01-05 | 307 | 20230105 | 900 | 1920470 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 164 | 57892 | 39.4655 | -120.8443 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797263 | 0 | EPSS Ckt | N | 2023 | A C
63175 | SIERRA | NEVADA | ALLEGHANY 1102 | 152101102 | RECLOSER | 1102/2 | 2023-01-05 | 307 | 20230105 | 900 | 1920470 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 164 | 57892 | 39.4655 | -120.8443 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006961 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797263 | 0 | EPSS Ckt | N | 2023 | A C
63176 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 2023-01-05 | 401 | 20230105 | 907 | 1920553 | 306 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 8874 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0007127 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797413 | 0 | EPSS Ckt | N | 2023
63189 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 836878 | 2023-01-05 | 1516 | 20230105 | 1534 | 1920596 | 18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3951 | 71118 | 38.7371 | -120.6759 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0007502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1797835 | 0 | EPSS Ckt | N | 2023
63190 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10291 | 2023-01-05 | 1534 | 20230105 | 1705 | 1923023 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 32 | 2912 | 38.6692 | -120.6696 | Yes | Clear;32-90 F |  |  | 23-0007664 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1797861 | 0 | EPSS Ckt | N | 2023
63191 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12121 | 2023-01-05 | 1553 | 20230105 | 1617 | 1923060 | 24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 288 | 38.6376 | -120.6493 | Yes | Clear;32-90 F |  |  | 23-0007705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1797889 | 0 | EPSS Ckt | N | 2023
63193 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1053 | 2023-01-05 | 1645 | 20230109 | 1725 | 1923703 | 5800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 298705 | 38.6534 | -120.6273 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0008009 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1798141 | 0 | EPSS Ckt | N | 2023
63202 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-01-06 | 710 | 20230106 | 1225 | 1924152 | 315 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1469 | 38.7941 | -120.8199 | No | Clear;32-90F |  |  | 23-0008210 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1798279 | 1 | EPSS Ckt | N | 2023
63215 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 89934 | 2023-01-07 | 1810 | 20230109 | 1658 | 1927476 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 1030 | 1197021 | 38.6491 | -120.6764 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1798815 | 0 | EPSS Ckt | N | 2023
63230 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 2023-01-07 | 2141 | 20230107 | 2220 | 1928136 | 39 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 1131 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0009230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799060 | 0 | EPSS Ckt | N | 2023
63231 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-01-07 | 2143 | 20230107 | 2336 | 1928139 | 113 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 105768 | 38.7391 | -120.6681 | Yes | Clear;32-90F |  |  | 23-0009146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799000 | 0 | EPSS Ckt | N | 2023 | B C
63266 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-01-08 | 37 | 20230108 | 1359 | s1813639 | 802 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 750672 | 38.7391 | -120.6681 | Yes | Clear;32-90F |  |  | 23-0009146 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1813639 | 0 | EPSS Ckt | N | 2023 | B C
63287 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2023-01-08 | 113 | 20230109 | 910 | 1931673 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 3018 | 2769564 | 38.7716 | -120.8148 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1799425 | 0 | EPSS Ckt | N | 2023 | C GRD
63293 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 2023-01-08 | 120 | 20230108 | 656 | 1931698 | 336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 29 | 9744 | 38.6728 | -120.6678 | Yes | Clear;32-90F |  |  | 23-0009838 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1799688 | 0 | EPSS Ckt | N | 2023
63306 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OTHER | WIRE DOWN 1 LD SIDE CGC2240008240567 | 2023-01-08 | 146 | 20230109 | 1400 | 1931839 | 2174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 23201 | 38.7722 | -120.5955 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010254 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | Yes | 1800103 | 0 | EPSS Ckt | N | 2023
63314 | SIERRA | NEVADA | SHADY GLEN 1102 | 152431102 | FUSE | 6575 | 2023-01-08 | 536 | 20230109 | 1520 | 1932265 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 26609 | 39.1392 | -120.9663 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010099 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1799946 | 0 | EPSS Ckt | N | 2023
63352 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 2023-01-09 | 404 | 20230109 | 950 | 1937165 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 27334 | 38.686 | -120.6419 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0010932 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800772 | 0 | EPSS Ckt | N | 2023
63357 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-01-09 | 734 | 20230109 | 1338 | 1936530 | 364 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 5096 | 38.7941 | -120.8199 | Yes | Clear;32-90F |  |  | 23-0011241 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801030 | 0 | EPSS Ckt | N | 2023
63358 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 2023-01-09 | 741 | 20230109 | 1214 | 1936555 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1365 | 38.8986 | -120.8986 | Yes | Clear;32-90F |  |  | 23-0011087 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1800902 | 0 | EPSS Ckt | N | 2023
63359 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 2023-01-09 | 742 | 20230109 | 1006 | 1936562 | 144 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 25200 | 38.9133 | -120.9318 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0010859 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1800708 | 0 | EPSS Ckt | N | 2023 | B & C
63365 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 2023-01-09 | 841 | 20230109 | 1331 | 1937041 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 22330 | 38.7941 | -120.7143 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011232 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801023 | 0 | EPSS Ckt | N | 2023
63380 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20521 | 2023-01-09 | 1725 | 20230109 | 1926 | 1939050 | 121 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 726 | 38.6497 | -120.676 | Yes | Clear;32-90F |  |  | 23-0011570 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801333 | 0 | EPSS Ckt | N | 2023
63413 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18939 | 2023-01-10 | 420 | 20230111 | 1443 | 1945545 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10315 | 38.6302 | -120.8255 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011869 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802277 | 0 | EPSS Ckt | N | 2023
63414 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2023-01-10 | 420 | 20230111 | 1816 | 1942018 | 2202 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 2679319 | 38.7716 | -120.8148 | Yes | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011874 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1801641 | 0 | EPSS Ckt | N | 2023 | ABC
63415 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-01-10 | 420 | 20230110 | 1242 | 1944063 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 7028 | 38.7941 | -120.8199 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0012093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1801866 | 0 | EPSS Ckt | N | 2023
63416 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 24189 | 2023-01-10 | 420 | 20230111 | 1512 | 1944897 | 2092 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18828 | 38.8025 | -120.7947 | Yes | Strong Winds-Heavy Rain; | Pole-Wood | Broken | 23-0012326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802073 | 0 | EPSS Ckt | N | 2023
63445 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12623 | 2023-01-10 | 430 | 20230110 | 920 | 1942141 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 6090 | 38.7856 | -120.6992 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0012095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801869 | 0 | EPSS Ckt | N | 2023
63449 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 21415 | 2023-01-10 | 434 | 20230110 | 1125 | 1942201 | 411 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 19 | 7809 | 38.7136 | -120.632 | Yes | Clear;32-90 F |  |  | 23-0012271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1802029 | 0 | EPSS Ckt | N | 2023
63451 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 30145 | 2023-01-10 | 438 | 20230111 | 1004 | 1942356 | 1766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 15894 | 39.1623 | -120.8618 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0013502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803003 | 0 | EPSS Ckt | N | 2023
63452 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-01-10 | 440 | 20230110 | 1438 | 1942331 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 1874 | 359957 | 39.0997 | -121.05 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 23-0011891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1801659 | 0 | EPSS Ckt | N | 2023 | SGF
63464 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18873 | 2023-01-10 | 959 | 20230110 | 1020 | 1944458 | 21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 357 | 38.8161 | -120.9016 | Yes | Clear;32-90 F |  |  | 23-0012189 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1801952 | 0 | EPSS Ckt | N | 2023
63469 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 1055 | 2023-01-10 | 1111 | 20230111 | 1458 | 1945160 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 61679 | 38.652 | -120.6282 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012687 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1802328 | 0 | EPSS Ckt | N | 2023
63496 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | SWITCH | 740738 | 2023-01-11 | 1244 | 20230111 | 1300 | 1947985 | 16 | Distribution Circuit | Company Initiated | Return Circuit Normal | 214 | 3424 | 38.7139 | -120.6222 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0008986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1803095 | 0 | EPSS Ckt | N | 2023
63507 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8003 | 2023-01-12 | 738 | 20230113 | 1251 | 1949457 | 1753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3506 | 39.4456 | -120.8237 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0015110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804183 | 0 | EPSS Ckt | N | 2023
63508 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 2023-01-12 | 1133 | 20230112 | 1458 | 1949971 | 205 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 205 | 39.322 | -120.8533 | No | Clear;32-90F |  |  | 23-0014631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1803810 | 0 | EPSS Ckt | N | 2023
63526 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-01-14 | 717 | 20230114 | 931 | 1952977 | 134 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1876 | 38.7941 | -120.8199 | Yes | Clear;32-90F |  |  | 23-0015997 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804816 | 0 | EPSS Ckt | N | 2023
63541 | SIERRA | PLACER | DRUM 1101 | 152321101 | RECLOSER | 1101/2 | 2023-01-14 | 1059 | 20230115 | 1725 | 1954075 | 1483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 196080 | 39.2562 | -120.7669 | Yes | Rain; | Insulator | Broken | 23-0016116 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804908 | 0 | EPSS Ckt | N | 2023 | A+C
63543 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 2023-01-14 | 1127 | 20230114 | 1240 | 1954141 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 73 | 39.322 | -120.8533 | Yes | Rain; |  |  | 23-0016195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1804968 | 0 | EPSS Ckt | N | 2023
63551 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 2023-01-14 | 1428 | 20230114 | 1517 | 1954304 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 1078 | 38.7956 | -120.8033 | Yes | Rain;32-90 F | Conductor- Overhead | Normal | 23-0016284 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805040 | 0 | EPSS Ckt | N | 2023
63566 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223320540745 | 2023-01-14 | 1922 | 20230115 | 1353 | 1955111 | 1111 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 3333 | 38.7782 | -120.8354 | Yes | Snow;32-90 F | Transformer | Failed/Faulted | 23-0016631 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805370 | 0 | EPSS Ckt | N | 2023
63573 | SIERRA | NEVADA | BRUNSWICK 1102 | 152481102 | FUSE | 3891 | 2023-01-15 | 1051 | 20230115 | 1216 | 1955820 | 85 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 2635 | 39.2197 | -120.9493 | No | Snow; |  |  | 23-0016665 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805400 | 0 | EPSS Ckt | N | 2023
63575 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 9015 | 2023-01-15 | 1218 | 20230115 | 1649 | 1955907 | 271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 271 | 39.322 | -120.8533 | No | Snow; | Conductor- Overhead | Broken | 23-0016712 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805429 | 0 | EPSS Ckt | N | 2023
63578 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 2023-01-15 | 1259 | 20230118 | 1701 | 1955966 | 1567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1000 | 319094 | 39.4655 | -120.8444 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0016684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805412 | 0 | EPSS Ckt | N | 2023 | SGF
63578 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 2023-01-15 | 1259 | 20230118 | 1701 | 1955966 | 1567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1000 | 319094 | 39.4655 | -120.8444 | No | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0016684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805412 | 0 | EPSS Ckt | N | 2023 | SGF
63581 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 2023-01-16 | 515 | 20230117 | 2121 | 1957999 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 1659 | 3526892 | 38.7934 | -120.6201 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017173 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805860 | 0 | EPSS Ckt | N | 2023 | A B C PH TIME OC
63594 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 2023-01-16 | 1057 | 20230116 | 2114 | 1957727 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 11723 | 38.7136 | -120.632 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0017271 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1805948 | 0 | EPSS Ckt | N | 2023
63598 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 2023-01-16 | 1211 | 20230116 | 1403 | 1957998 | 112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 896 | 38.9409 | -120.7298 | Yes | Clear;32-90F |  |  | 23-0017247 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1805921 | 0 | EPSS Ckt | N | 2023
63600 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-01-16 | 1218 | 20230117 | 1348 | 1958034 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 451944 | 38.7391 | -120.6681 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017179 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | Yes | No | 1805866 | 0 | EPSS Ckt | N | 2023 | SGF
63603 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 2023-01-16 | 1317 | 20230117 | 1112 | 1958141 | 1315 | Distribution Circuit | Environmental/External | Ice or snow | 59 | 77585 | 38.6204 | -120.6018 | Yes | Clear;32-90 F | Insulator | Broken | 23-0017358 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1806028 | 0 | EPSS Ckt | N | 2023
63607 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223495039480 | 2023-01-17 | 718 | 20230117 | 1002 | 1959130 | 164 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 164 | 38.7433 | -120.7749 | No | Clear;32-90 F | Transformer (OH) |  | 23-0017557 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1806175 | 0 | EPSS Ckt | N | 2023
63644 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 2 SPANS SS OF CGC 223425541680 | 2023-01-19 | 2250 | 20230120 | 1403 | 1962868 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2006 | 38.8055 | -120.7997 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0019190 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1806962 | 0 | EPSS Ckt | N | 2023
63656 | SIERRA | NEVADA | COLUMBIA HILL 1101 | 152471101 | RECLOSER | 583518 | 2023-01-21 | 1651 | 20230121 | 1657 | 1964239 | 6 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 37 | 222 | 39.3256 | -121.1123 | No | Clear;32-90F |  |  | 23-0019767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807230 | 0 | EPSS Ckt | N | 2023 | A+C
63664 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 2023-01-22 | 1517 | 20230122 | 1747 | 1964895 | 150 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3900 | 38.7681 | -120.951 | No | Clear;32-90F |  |  | 23-0019929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807363 | 0 | EPSS Ckt | N | 2023
63666 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 2023-01-22 | 2346 | 20230123 | 1412 | 1965281 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19052 | 38.7956 | -120.8033 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0020003 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1807434 | 0 | EPSS Ckt | N | 2023
63667 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 24189 | 2023-01-23 | 132 | 20230123 | 435 | 1965280 | 183 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 1647 | 38.8025 | -120.7947 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0020004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1807435 | 0 | EPSS Ckt | N | 2023
63683 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223666041091 | 2023-01-24 | 1725 | 20230125 | 1720 | 1967344 | 1435 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 2870 | 38.7874 | -120.7154 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0020985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1807964 | 0 | EPSS Ckt | N | 2023
63690 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-01-26 | 127 | 20230126 | 1635 | 1968437 | 864 | Distribution Circuit | Environmental/External | Ice or snow | 202 | 137094 | 39.2562 | -120.7669 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0021521 | OH | Sus | 31635651 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | Yes | No | 1808259 | 0 | EPSS Ckt | N | 2023 | AB
63711 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223282049250 | 2023-01-31 | 300 | 20230131 | 1045 | 1972342 | 465 | Transformer only | Vegetation | Tree - fell into line | 2 | 930 | 39.0129 | -120.8449 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0023230 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | Yes | No | 1809300 | 0 | EPSS Ckt | N | 2023
63714 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 2023-01-31 | 1414 | 20230201 | 227 | 1973026 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 19933 | 38.7911 | -120.7022 | No | Clear;32-90 F | Secondary | Broken | 23-0023633 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1809523 | 0 | EPSS Ckt | N | 2023
63727 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 57465 | 2023-02-05 | 330 | 20230205 | 1149 | 1977145 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10978 | 39.3625 | -120.7904 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0025335 | OH | Sus | 35424879 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1810640 | 0 | EPSS Ckt | N | 2023
63730 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223630741581 | 2023-02-05 | 1530 | 20230205 | 1552 | 1977471 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 38.8011 | -120.7272 | No | Clear;32-90 F | Fuse | Broken | 23-0025424 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1810713 | 0 | EPSS Ckt | N | 2023
63740 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223026042370 | 2023-02-06 | 1639 | 20230206 | 1938 | 1978565 | 179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 179 | 38.8253 | -120.9389 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0025950 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1811052 | 0 | EPSS Ckt | N | 2023
63760 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222593061072 | 2023-02-13 | 1508 | 20230213 | 1638 | 1983863 | 90 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 180 | 39.3409 | -121.0845 | No | Clear;32-90F |  |  | 23-0028307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1812875 | 0 | EPSS Ckt | N | 2023
63765 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12627 | 2023-02-15 | 1135 | 20230216 | 52 | 1986098 | 797 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2391 | 38.7925 | -120.7023 | No | Clear;32-90 F | Insulator | Broken | 23-0029437 | OH | Sus | 31636888 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1813574 | 0 | EPSS Ckt | N | 2023
63766 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223913038203 | 2023-02-15 | 1401 | 20230215 | 1854 | 1986259 | 293 | Transformer only | Company Initiated | Construction Activity/equip- company | 1 | 293 | 38.7066 | -120.6293 | No | Clear;32-90 F | Transformer | Malfunctioning | 23-0023443 | OH | Sus | 31611150 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1813546 | 0 | EPSS Ckt | N | 2023
63770 | SIERRA | NEVADA | PIKE CITY 1101 | 152201101 | FUSE | 6765 | 2023-02-16 | 902 | 20230216 | 1258 | 1986745 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2832 | 39.4912 | -121.0862 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0029640 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1813736 | 0 | EPSS Ckt | N | 2023
63775 | SIERRA | PLACER | FORESTHILL 1102 | 152181102 | FUSE | 6047 | 2023-02-17 | 1457 | 20230217 | 1646 | 1987827 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 872 | 38.9807 | -120.9404 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0030276 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1814043 | 0 | EPSS Ckt | N | 2023
63789 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 875388 | 2023-02-21 | 1425 | 20230222 | 1155 | 1991609 | 1290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 206 | 17286 | 39.2827 | -120.9454 | Yes | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0031217 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1814899 | 0 | EPSS Ckt | N | 2023 | A B INST TIME
63797 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 2023-02-21 | 1516 | 20230221 | 1700 | 1992281 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 2704 | 38.7681 | -120.951 | Yes | Clear;32-90 F |  |  | 23-0031601 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815222 | 0 | EPSS Ckt | N | 2023
63804 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 2023-02-21 | 1748 | 20230222 | 843 | 1994222 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 23270 | 38.7681 | -120.951 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0031765 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1815365 | 0 | EPSS Ckt | N | 2023
63806 | SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | TRANSFORMER | 223519239461 | 2023-02-21 | 1824 | 20230221 | 2021 | 1992480 | 117 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 351 | 38.7431 | -120.7676 | Yes | Clear;32-90 F |  |  | 23-0031801 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1815400 | 0 | EPSS Ckt | N | 2023
63809 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-02-22 | 602 | 20230222 | 1656 | 1996406 | 654 | Distribution Circuit | 3rd Party | Vehicle | 936 | 237600 | 38.7391 | -120.6681 | No | Clear;Below 32 F | Pole-Wood | Broken | 23-0032048 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1815649 | 0 | EPSS Ckt | N | 2023 | N/A
63825 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 7597 | 2023-02-24 | 854 | 20230224 | 1124 | 2004401 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 3150 | 39.0663 | -120.9467 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0033995 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1816967 | 0 | EPSS Ckt | N | 2023
63830 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 35323 | 2023-02-24 | 1054 | 20230224 | 1717 | 2004949 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | 39.096 | -121.0531 | Yes | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0034037 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1816998 | 0 | EPSS Ckt | N | 2023
63833 | SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 33947 | 2023-02-24 | 1115 | 20230225 | 1125 | 2005209 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1450 | 39.0329 | -120.951 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0035073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817936 | 0 | EPSS Ckt | N | 2023
63838 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18745 | 2023-02-24 | 1311 | 20230225 | 1018 | 2005669 | 1267 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3801 | 38.6551 | -120.7047 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Normal | 23-0034420 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1817274 | 0 | EPSS Ckt | N | 2023
63843 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 69880 | 2023-02-24 | 1406 | 20230224 | 1517 | 2005768 | 71 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 1207 | 39.0808 | -120.9419 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034287 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1817175 | 0 | EPSS Ckt | N | 2023 | NONE
63847 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 2023-02-24 | 1534 | 20230224 | 2105 | 2006036 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4634 | 38.8109 | -120.8052 | Yes | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0034492 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817341 | 0 | EPSS Ckt | N | 2023
63849 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 2023-02-24 | 1707 | 20230225 | 1049 | 2006350 | 1062 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 8496 | 38.9409 | -120.7298 | Yes | Clear;32-90F |  |  | 23-0035136 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817999 | 0 | EPSS Ckt | N | 2023
63851 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223016555572 | 2023-02-24 | 1747 | 20230225 | 1234 | 2006489 | 1126 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 6412 | 39.1879 | -120.9366 | Yes | Overcast-Snow;32-90 F |  |  | 23-0034529 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1817379 | 0 | EPSS Ckt | N | 2023
63854 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 2023-02-24 | 1926 | 20230225 | 1121 | 2006841 | 955 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 955 | 38.6344 | -120.6373 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1817510 | 0 | EPSS Ckt | N | 2023
63869 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3631 | 2023-02-26 | 1916 | 20230308 | 1459 | 2025973 | 14143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 183859 | 39.2143 | -120.959 | Yes | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041381 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822708 | 0 | EPSS Ckt | N | 2023
63870 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3633 | 2023-02-26 | 1916 | 20230309 | 1044 | 2025974 | 15328 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 275904 | 39.211 | -120.9576 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041382 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822709 | 0 | EPSS Ckt | N | 2023
63871 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7469 | 2023-02-26 | 1916 | 20230310 | 2103 | 2025978 | 17387 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 799802 | 39.2081 | -120.9493 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041383 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822710 | 0 | EPSS Ckt | N | 2023
63876 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | JUMPER | OJ'S 1 SPAN SS OF 30629 | 2023-02-26 | 2123 | 20230310 | 1300 | 2024966 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16777 | 39.4717 | -121.0849 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822435 | 0 | EPSS Ckt | N | 2023
63877 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | JUMPER | OJ'S @ HARD TAP SS OF CGC 222577565960 | 2023-02-26 | 2123 | 20230310 | 1300 | 2024969 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 100662 | 39.474 | -121.0853 | Yes | Overcast-Snow;32-90 F | Conductor- Overhead | Normal | 23-0040877 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1822436 | 0 | EPSS Ckt | N | 2023
63903 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31407 | 2023-02-26 | 2228 | 20230311 | 1219 | 2030894 | 18111 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 181110 | 39.2779 | -120.9453 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043032 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1823705 | 0 | EPSS Ckt | N | 2023
63918 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 2023-02-27 | 1031 | 20230227 | 1210 | 2011804 | 99 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 2377 | 39.2095 | -120.827 | Yes | Clear;32-90F |  |  | 23-0036342 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819017 | 1 | EPSS Ckt | N | 2023
63919 | SIERRA | PLACER | BONNIE NOOK 1101 | 152301101 | FUSE | 6375 | 2023-02-27 | 1032 | 20230228 | 1238 | 2011781 | 1566 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 120 | 186419 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0036275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1818972 | 0 | EPSS Ckt | N | 2023
63920 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 80083 | 2023-02-27 | 1039 | 20230302 | 1256 | 2011826 | 4457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 22285 | 39.2151 | -120.8091 | Yes | Clear;32-90F | Lightning Arrestor | Broken | 23-0038799 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820864 | 0 | EPSS Ckt | N | 2023
63925 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6901 | 2023-02-27 | 1047 | 20230307 | 1921 | 2022908 | 12034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 180510 | 38.94 | -120.7288 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821827 | 0 | EPSS Ckt | N | 2023
63926 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 2023-02-27 | 1047 | 20230308 | 1959 | 2022910 | 13512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 108096 | 38.9409 | -120.7298 | Yes | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0040084 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821828 | 0 | EPSS Ckt | N | 2023
63967 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | SWITCH | 1975 | 2023-02-27 | 1303 | 20230310 | 1956 | 2025931 | 16253 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 796397 | 39.2099 | -120.9358 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041355 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822685 | 0 | EPSS Ckt | N | 2023
63975 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 2023-02-27 | 1310 | 20230307 | 1755 | 2025759 | 11805 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 318735 | 39.1757 | -120.9295 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041280 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822651 | 0 | EPSS Ckt | N | 2023
63990 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8789 | 2023-02-27 | 1340 | 20230307 | 1511 | 2025070 | 11611 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 325108 | 39.1878 | -120.9258 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822457 | 0 | EPSS Ckt | N | 2023
63990 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 8789 | 2023-02-27 | 1340 | 20230307 | 1511 | 2025070 | 11611 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 325108 | 39.1878 | -120.9258 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040905 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1822457 | 0 | EPSS Ckt | N | 2023
64007 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 2023-02-27 | 1350 | 20230307 | 1513 | 2018311 | 11603 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 475723 | 39.0098 | -120.8455 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038181 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820413 | 0 | EPSS Ckt | N | 2023
64016 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33299 | 2023-02-27 | 1354 | 20230310 | 1520 | 2024779 | 15926 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 382224 | 39.1705 | -120.9927 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822395 | 0 | EPSS Ckt | N | 2023
64016 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 33299 | 2023-02-27 | 1354 | 20230310 | 1520 | 2024779 | 15926 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 382224 | 39.1705 | -120.9927 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040789 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822395 | 0 | EPSS Ckt | N | 2023
64017 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12623 | 2023-02-27 | 1356 | 20230228 | 1249 | 2014316 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28833 | 38.7856 | -120.6992 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819607 | 0 | EPSS Ckt | N | 2023
64018 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9353 | 2023-02-27 | 1402 | 20230306 | 1155 | 2012780 | 9953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 43087 | 38.9015 | -120.9035 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0039979 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1821735 | 1 | EPSS Ckt | N | 2023
64019 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 2023-02-27 | 1411 | 20230227 | 1711 | 2012638 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3420 | 38.7136 | -120.632 | Yes |  | Conductor- Overhead | Normal | 23-0036684 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819246 | 0 | EPSS Ckt | N | 2023
64028 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 63545 | 2023-02-27 | 1442 | 20230309 | 1806 | 2020109 | 14604 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29208 | 39.3638 | -120.795 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0038889 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820919 | 0 | EPSS Ckt | N | 2023
64029 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8051 | 2023-02-27 | 1442 | 20230310 | 1707 | 2020113 | 15985 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 63940 | 39.3575 | -120.8018 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0038891 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820920 | 0 | EPSS Ckt | N | 2023
64030 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | TRANSFORMER | 223405061940 | 2023-02-27 | 1442 | 20230313 | 636 | 2020176 | 19674 | Transformer only | Environmental/External | Ice or snow | 1 | 19674 | 39.3609 | -120.7964 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0038957 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820964 | 0 | EPSS Ckt | N | 2023
64035 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22029 | 2023-02-27 | 1508 | 20230227 | 1825 | 2012789 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1576 | 38.7993 | -120.7168 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0036705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819265 | 0 | EPSS Ckt | N | 2023
64039 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 2023-02-27 | 1515 | 20230228 | 1643 | 2012826 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 21392 | 38.8109 | -120.8052 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036736 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819296 | 0 | EPSS Ckt | N | 2023
64079 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ'S 1 SPAN E/OF CGC 223242854376 | 2023-02-27 | 1617 | 20230307 | 1538 | 2025020 | 11481 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 23490 | 39.1542 | -120.8567 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0040894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1822450 | 0 | EPSS Ckt | N | 2023
64091 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 2023-02-27 | 1653 | 20230303 | 2151 | 2021563 | 6058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 121160 | 38.8528 | -120.789 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1821349 | 0 | EPSS Ckt | N | 2023
64092 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5591 | 2023-02-27 | 1653 | 20230308 | 1654 | 2021569 | 12961 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 240117 | 38.8608 | -120.7883 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039551 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821351 | 0 | EPSS Ckt | N | 2023
64093 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 1 S/O 5591 | 2023-02-27 | 1653 | 20230308 | 1555 | 2021957 | 12902 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 289113 | 38.8605 | -120.7884 | Yes | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1821490 | 0 | EPSS Ckt | N | 2023
64098 | SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | TRANSFORMER | 223524938552 | 2023-02-27 | 1713 | 20230228 | 1730 | 2013224 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1995 | 38.7184 | -120.7647 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0036933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819477 | 0 | EPSS Ckt | N | 2023
64108 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 2023-02-27 | 1844 | 20230301 | 1858 | 2013567 | 2894 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 69491 | 39.2095 | -120.827 | Yes | Clear;32-90 F | Lightning Arrestor | Broken | 23-0038443 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820637 | 1 | EPSS Ckt | N | 2023
64110 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6365 | 2023-02-27 | 1845 | 20230306 | 1719 | 2024702 | 9994 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 239856 | 39.1734 | -120.8591 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1822371 | 0 | EPSS Ckt | N | 2023
64116 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223837533500 | 2023-02-27 | 2005 | 20230228 | 1504 | 2013753 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1139 | 38.5782 | -120.6586 | Yes | Clear;Below 32 F | Transformer (OH) | Broken- wire on ground | 23-0037156 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1819633 | 0 | EPSS Ckt | N | 2023
64133 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 2023-02-28 | 738 | 20230228 | 1250 | 2014990 | 312 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 62 | 19429 | 38.7959 | -120.7508 | Yes | Clear;32-90 F |  |  | 23-0037301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819728 | 1 | EPSS Ckt | N | 2023
64134 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-02-28 | 745 | 20230310 | 1704 | 2014302 | 14959 | Distribution Circuit | Environmental/External | Ice or snow | 157 | 1306904 | 39.4655 | -120.8443 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken | 23-0037093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819603 | 0 | EPSS Ckt | N | 2023 | A & C
64134 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-02-28 | 745 | 20230310 | 1704 | 2014302 | 14959 | Distribution Circuit | Environmental/External | Ice or snow | 157 | 1306904 | 39.4655 | -120.8443 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken | 23-0037093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819603 | 0 | EPSS Ckt | N | 2023 | A & C
64139 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 2023-02-28 | 931 | 20230228 | 951 | 2014662 | 20 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 178 | 3560 | 38.7138 | -120.6231 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037180 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819653 | 0 | EPSS Ckt | N | 2023
64142 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1471 | 2023-02-28 | 940 | 20230228 | 1208 | 2014700 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 4588 | 38.7418 | -120.6624 | Yes | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0037340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819753 | 0 | EPSS Ckt | N | 2023
64150 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5925 | 2023-02-28 | 955 | 20230302 | 1830 | 2020209 | 3395 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 16975 | 39.0331 | -120.797 | Yes | Clear;32-90 F |  |  | 23-0038954 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820961 | 0 | EPSS Ckt | N | 2023
64167 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6023 | 2023-02-28 | 1151 | 20230305 | 1508 | 2021854 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 59176 | 38.9929 | -120.9242 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039701 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821455 | 0 | EPSS Ckt | N | 2023
64172 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 30261 | 2023-02-28 | 1158 | 20230305 | 1725 | 2021857 | 7527 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 338715 | 38.986 | -120.9067 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039702 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1821456 | 0 | EPSS Ckt | N | 2023
64175 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 9957 | 2023-02-28 | 1208 | 20230228 | 1504 | 2015213 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 12320 | 38.5762 | -120.6628 | Yes | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken | 23-0037337 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1819750 | 0 | EPSS Ckt | N | 2023
64176 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8225 | 2023-02-28 | 1216 | 20230310 | 1128 | 2024634 | 14352 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 489872 | 39.4541 | -121.0327 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1822354 | 0 | EPSS Ckt | N | 2023
64177 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 2023-02-28 | 1216 | 20230309 | 1723 | 2024635 | 13267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 132670 | 39.4564 | -121.0375 | Yes | Overcast-Fog-Snow;32-90 F | Cutout- fuse holder | Broken | 23-0040694 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822355 | 0 | EPSS Ckt | N | 2023
64179 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21407 | 2023-02-28 | 1217 | 20230306 | 1510 | 2015386 | 8813 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 105756 | 38.7116 | -120.6263 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken | 23-0037574 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819918 | 0 | EPSS Ckt | N | 2023
64181 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | FUSE | 32449 | 2023-02-28 | 1218 | 20230310 | 1906 | 2020076 | 14808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 592320 | 39.5403 | -120.8846 | Yes | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Deteriorated | 23-0038872 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820907 | 0 | EPSS Ckt | N | 2023
64182 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | OCB | 1101/2 | 2023-02-28 | 1220 | 20230309 | 1645 | 2017699 | 13225 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 2769836 | 39.4382 | -120.9964 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820265 | 0 | EPSS Ckt | N | 2023 | NA
64183 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 920859 | 2023-02-28 | 1223 | 20230307 | 1352 | 2018231 | 10169 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 40676 | 39.3663 | -121.0374 | Yes | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0038415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820614 | 0 | EPSS Ckt | N | 2023
64186 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 2023-02-28 | 1245 | 20230306 | 1550 | 2015672 | 8825 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 347669 | 38.7941 | -120.7143 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037417 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1819822 | 0 | EPSS Ckt | N | 2023
64188 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12629 | 2023-02-28 | 1303 | 20230305 | 1630 | 2015651 | 7407 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 185175 | 38.7928 | -120.7012 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037590 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819928 | 0 | EPSS Ckt | N | 2023
64189 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 2023-02-28 | 1303 | 20230306 | 1609 | 2015734 | 8826 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 322336 | 39.3823 | -121.0478 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038299 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820501 | 0 | EPSS Ckt | N | 2023
64190 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12627 | 2023-02-28 | 1304 | 20230305 | 1616 | 2015654 | 7392 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22176 | 38.7925 | -120.7023 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0037580 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1819922 | 0 | EPSS Ckt | N | 2023
64193 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 2023-02-28 | 1315 | 20230228 | 1557 | 2015675 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 62 | 10088 | 38.7959 | -120.7508 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037547 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1819900 | 1 | EPSS Ckt | N | 2023
64195 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33319 | 2023-02-28 | 1323 | 20230306 | 1602 | 2018413 | 8799 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 70392 | 39.1339 | -120.9411 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038237 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | No | 1820462 | 0 | EPSS Ckt | N | 2023
64200 | SIERRA | PLACER | HIGGINS-1110 | 152691110 | JUMPER | WIRE DOWN 1 SPAN E/OF 33943 | 2023-02-28 | 1349 | 20230228 | 1631 | 2015773 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 14940 | 39.0222 | -120.9558 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037450 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | Yes | Yes | 1819837 | 0 | EPSS Ckt | N | 2023
64203 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223935937618 | 2023-02-28 | 1357 | 20230228 | 1458 | 2015820 | 61 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 183 | 38.6919 | -120.6219 | Yes | Clear;32-90 F |  |  | 23-0037462 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1819845 | 0 | EPSS Ckt | N | 2023
64205 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223327956367 | 2023-02-28 | 1425 | 20230305 | 1637 | 2015866 | 7332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 14664 | 39.2085 | -120.8267 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0038920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820937 | 0 | EPSS Ckt | N | 2023
64216 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 2023-02-28 | 1620 | 20230305 | 1854 | 2016167 | 7354 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 85019 | 39.2024 | -120.8369 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037612 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | Yes | 1819949 | 1 | EPSS Ckt | N | 2023
64218 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-02-28 | 1641 | 20230304 | 902 | 2016226 | 5301 | Distribution Circuit | Vegetation | Tree - fell into line | 2121 | 904643 | 39.0997 | -121.05 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037611 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1819947 | 0 | EPSS Ckt | N | 2023 | A B
64226 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | RECLOSER | 69880 | 2023-02-28 | 1707 | 20230304 | 1025 | 2016335 | 5358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 91086 | 39.0808 | -120.9419 | Yes | Clear;32-90 F |  |  | 23-0039934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1821693 | 0 | EPSS Ckt | N | 2023 | AB
64227 | SIERRA | PLACER | HIGGINS-1110 | 152691110 | FUSE | 8707 | 2023-02-28 | 1710 | 20230302 | 1218 | 2016317 | 2588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 82816 | 39.0409 | -120.94 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0038767 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820846 | 0 | EPSS Ckt | N | 2023
64236 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 11933 | 2023-02-28 | 1743 | 20230304 | 1625 | 2016362 | 5682 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 270238 | 38.6952 | -120.6095 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820172 | 0 | EPSS Ckt | N | 2023
64236 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 11933 | 2023-02-28 | 1743 | 20230304 | 1625 | 2016362 | 5682 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 270238 | 38.6952 | -120.6095 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820172 | 0 | EPSS Ckt | N | 2023
64240 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223332556465 | 2023-02-28 | 1826 | 20230302 | 1702 | 2016307 | 2796 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2796 | 39.2102 | -120.825 | Yes | Clear;32-90 F | Fuse | Failed/Faulted | 23-0038983 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1820984 | 0 | EPSS Ckt | N | 2023
64242 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 2023-02-28 | 1851 | 20230305 | 1435 | 2016799 | 6944 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 302432 | 39.2024 | -120.8369 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Three Phase Fault | 0 | No | No | No | 1820328 | 0 | EPSS Ckt | N | 2023
64245 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6375 | 2023-02-28 | 1926 | 20230302 | 1110 | 2016768 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 171056 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Bent or Twisted | 23-0038049 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1820322 | 0 | EPSS Ckt | N | 2023
64249 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20619 | 2023-02-28 | 1949 | 20230304 | 1952 | 2019689 | 5763 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 103734 | 38.7219 | -120.6608 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820807 | 0 | EPSS Ckt | N | 2023
64251 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223924238369 | 2023-02-28 | 1949 | 20230307 | 1439 | 2024851 | 9770 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 9770 | 38.7112 | -120.6259 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer | Broken | 23-0040825 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1822414 | 0 | EPSS Ckt | N | 2023
64252 | SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1433 | 2023-02-28 | 1952 | 20230302 | 1115 | 2019259 | 2363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 11815 | 38.7502 | -120.7568 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0038536 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820719 | 0 | EPSS Ckt | N | 2023
64256 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18579 | 2023-02-28 | 1952 | 20230303 | 1247 | 2018887 | 3895 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27265 | 38.7393 | -120.6685 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820588 | 0 | EPSS Ckt | N | 2023
64259 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 2023-02-28 | 1953 | 20230304 | 1838 | 2017050 | 5685 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 773748 | 38.7138 | -120.6231 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1820089 | 0 | EPSS Ckt | N | 2023
64267 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 2023-02-28 | 1955 | 20230305 | 1649 | 2019571 | 7014 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 453930 | 38.7911 | -120.7022 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038653 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820779 | 0 | EPSS Ckt | N | 2023
64269 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 2023-02-28 | 1955 | 20230304 | 1838 | 2018204 | 5683 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 107977 | 38.7136 | -120.632 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038121 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820374 | 0 | EPSS Ckt | N | 2023
64271 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ LINE & BUCK S/S CGC 223834436887 | 2023-02-28 | 2000 | 20230301 | 2045 | 2018905 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1485 | 38.6712 | -120.6568 | Yes | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Open Circuit | 0 | No | Yes | No | 1820595 | 0 | EPSS Ckt | N | 2023
64272 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 10497 | 2023-02-28 | 2014 | 20230303 | 1035 | 2018675 | 3741 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 44919 | 38.7319 | -120.6758 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820524 | 0 | EPSS Ckt | N | 2023
64274 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18917 | 2023-02-28 | 2056 | 20230304 | 1952 | 2022187 | 5696 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 28480 | 38.7225 | -120.6428 | Yes | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken | 23-0039897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1821658 | 0 | EPSS Ckt | N | 2023
64277 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 2023-02-28 | 2103 | 20230302 | 1805 | 2017080 | 2702 | Distribution Circuit | Environmental/External | Ice or snow | 1895 | 3682342 | 38.7393 | -120.6773 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820160 | 0 | EPSS Ckt | N | 2023 | NONE
64278 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22073 | 2023-02-28 | 2103 | 20230303 | 942 | 2018867 | 3639 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 90975 | 38.7381 | -120.6736 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038389 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820579 | 0 | EPSS Ckt | N | 2023
64279 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22075 | 2023-02-28 | 2103 | 20230303 | 911 | 2018869 | 3608 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 54120 | 38.7384 | -120.673 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820581 | 0 | EPSS Ckt | N | 2023
64280 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 18577 | 2023-02-28 | 2103 | 20230303 | 1001 | 2018974 | 3658 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 91450 | 38.74 | -120.6708 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820618 | 0 | EPSS Ckt | N | 2023
64284 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 2023-02-28 | 2103 | 20230301 | 2045 | s1820438 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 21330 | 38.6765 | -120.6617 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037791 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820438 | 0 | EPSS Ckt | N | 2023
64286 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 2023-02-28 | 2103 | 20230304 | 1017 | 2017070 | 5114 | Distribution Circuit | Vegetation | Tree - fell into line | 2723 | 6847351 | 38.7934 | -120.62 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken | 23-0036774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1820125 | 0 | EPSS Ckt | N | 2023 | NA
64287 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 2023-02-28 | 2103 | 20230302 | 1645 | 2017072 | 2622 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1638 | 4281199 | 38.7934 | -120.6201 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037803 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820131 | 0 | EPSS Ckt | N | 2023 | NA
64288 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | JUMPER | OJS @ CGC 224006940584 | 2023-02-28 | 2103 | 20230303 | 1035 | 2020147 | 3692 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 33228 | 38.7722 | -120.5954 | Yes | Clear;32-90 F | Insulator | Broken | 23-0038918 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1820933 | 0 | EPSS Ckt | N | 2023
64289 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 4595 | 2023-02-28 | 2108 | 20230305 | 1605 | 2020302 | 6897 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 255189 | 38.6981 | -120.6039 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820994 | 0 | EPSS Ckt | N | 2023
64289 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 4595 | 2023-02-28 | 2108 | 20230305 | 1605 | 2020302 | 6897 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 255189 | 38.6981 | -120.6039 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038994 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820994 | 0 | EPSS Ckt | N | 2023
64291 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1471 | 2023-02-28 | 2110 | 20230304 | 1518 | 2018807 | 5408 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 167648 | 38.7418 | -120.6624 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1820559 | 0 | EPSS Ckt | N | 2023
64297 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 2023-02-28 | 2154 | 20230303 | 1303 | 2017101 | 3789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22734 | 39.3753 | -121.0378 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0039548 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1821348 | 0 | EPSS Ckt | N | 2023
64299 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 44383 | 2023-02-28 | 2208 | 20230303 | 937 | 2017141 | 3569 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3569 | 38.899 | -120.9148 | Yes | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037843 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1820173 | 0 | EPSS Ckt | N | 2023
64308 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 3773 | 2023-03-01 | 1026 | 20230306 | 1800 | 2018606 | 7654 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 15308 | 38.8839 | -120.83 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0038308 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | No | No | 1820508 | 0 | EPSS Ckt | N | 2023
64319 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 2023-03-01 | 2001 | 20230302 | 1133 | 2019153 | 932 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 22379 | 39.2095 | -120.827 | No | Clear;32-90F |  |  | 23-0038757 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820839 | 1 | EPSS Ckt | N | 2023
64320 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 1521 | 2023-03-01 | 2016 | 20230303 | 1510 | 2019174 | 2574 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 105534 | 38.741 | -120.6619 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038489 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1820674 | 0 | EPSS Ckt | N | 2023
64323 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223807439397 | 2023-03-01 | 2110 | 20230303 | 1041 | 2019217 | 2251 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 11255 | 38.7406 | -120.6661 | No | Clear;32-90 F |  |  | 23-0039391 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821253 | 0 | EPSS Ckt | N | 2023
64325 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30813 | 2023-03-01 | 2142 | 20230303 | 1313 | 2019244 | 2371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 21339 | 38.8876 | -120.8304 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038965 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820968 | 0 | EPSS Ckt | N | 2023
64326 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 2023-03-01 | 2151 | 20230304 | 1057 | 2019252 | 3666 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 40326 | 38.8791 | -120.8335 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039016 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821011 | 0 | EPSS Ckt | N | 2023
64329 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223793639402 | 2023-03-02 | 740 | 20230303 | 1106 | 2019410 | 1646 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 6584 | 38.7407 | -120.6714 | No | Clear;32-90F |  |  | 23-0039407 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821264 | 0 | EPSS Ckt | N | 2023
64330 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 2023-03-02 | 823 | 20230302 | 1603 | 2019450 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9200 | 38.7853 | -120.6077 | No | Clear;32-90F | Conductor- Overhead | On Ground | 23-0038879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | Yes | No | 1820910 | 0 | EPSS Ckt | N | 2023
64333 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 99087 | 2023-03-02 | 944 | 20230302 | 1653 | 2019661 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 429 | 39.1914 | -120.8315 | No | Clear;32-90F | Lightning Arrestor | Broken | 23-0038688 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1820802 | 0 | EPSS Ckt | N | 2023
64337 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 2023-03-02 | 1207 | 20230303 | 1657 | 2019784 | 1730 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 102070 | 38.6204 | -120.6018 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039012 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1821008 | 0 | EPSS Ckt | N | 2023
64343 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5681 | 2023-03-02 | 1400 | 20230305 | 1200 | 2021085 | 4200 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8400 | 39.0095 | -120.8449 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0040332 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822062 | 0 | EPSS Ckt | N | 2023
64344 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 31185 | 2023-03-02 | 1415 | 20230302 | 1932 | 2019987 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 951 | 39.1897 | -120.85 | No | Clear;32-90 F | Lightning Arrestor | Broken | 23-0039073 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821062 | 0 | EPSS Ckt | N | 2023
64351 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222735562820 | 2023-03-02 | 1744 | 20230307 | 1119 | 2020343 | 6815 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 6815 | 39.3879 | -121.0329 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0039446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821294 | 0 | EPSS Ckt | N | 2023
64356 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 2563 | 2023-03-03 | 623 | 20230304 | 1519 | 2020768 | 1976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 123047 | 38.7959 | -120.7508 | No | Overcast;32-90 F | Insulator | Burned/flashed | 23-0039823 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821590 | 1 | EPSS Ckt | N | 2023
64357 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-03-03 | 717 | 20230303 | 1340 | 2021298 | 383 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1040 | 393168 | 38.7391 | -120.6681 | No | Overcast;32-90 F |  |  | 23-0037831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821317 | 0 | EPSS Ckt | N | 2023 | SGF
64359 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 2023-03-03 | 1015 | 20230303 | 1050 | 2021571 | 35 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 210 | 39.3753 | -121.0378 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0039554 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1821353 | 0 | EPSS Ckt | N | 2023
64360 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 37335 | 2023-03-03 | 1037 | 20230303 | 1202 | 2020891 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 595 | 39.1743 | -120.8299 | No | Clear;32-90F | Conductor- Overhead | Together | 23-0039278 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821200 | 0 | EPSS Ckt | N | 2023
64371 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 30813 | 2023-03-03 | 1413 | 20230303 | 1431 | 2021476 | 18 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 162 | 38.8876 | -120.8304 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0041195 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1822626 | 0 | EPSS Ckt | N | 2023
64375 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | WIRE DOWN | 2023-03-03 | 1855 | 20230305 | 1505 | 2021827 | 2650 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2650 | 39.1368 | -120.9214 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039960 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1821715 | 0 | EPSS Ckt | N | 2023
64376 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | SWITCH | 12639 | 2023-03-03 | 1920 | 20230304 | 1924 | 2021837 | 1444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 187720 | 38.7892 | -120.7073 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0039692 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1821447 | 0 | EPSS Ckt | N | 2023
64378 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223952037797 | 2023-03-03 | 1950 | 20230304 | 911 | 2021873 | 801 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 801 | 38.6957 | -120.6163 | No | Clear;32-90F | Fuse | Normal | 23-0039901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821659 | 0 | EPSS Ckt | N | 2023
64382 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | TRANSFORMER | 223168547708 | 2023-03-04 | 648 | 20230305 | 1918 | 2022087 | 2190 | Transformer only | Vegetation | Tree - fell into line | 2 | 4380 | 38.9716 | -120.8862 | No | Clear;32-90 F | Transformer | Broken | 23-0039885 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1821648 | 0 | EPSS Ckt | N | 2023
64388 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222685062240 | 2023-03-04 | 1133 | 20230304 | 1148 | 2021744 | 15 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 45 | 39.3724 | -121.0507 | No | Clear;32-90 F |  |  | 23-0039951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1821706 | 0 | EPSS Ckt | N | 2023
64398 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223876138504 | 2023-03-04 | 2111 | 20230305 | 1029 | 2022957 | 798 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1596 | 38.7165 | -120.6428 | No |  | Transformer | Broken- wire on ground | 23-0040293 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822032 | 0 | EPSS Ckt | N | 2023
64404 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 22029 | 2023-03-05 | 1052 | 20230305 | 1100 | 2023626 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 64 | 38.7993 | -120.7168 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0040307 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1822044 | 0 | EPSS Ckt | N | 2023
64412 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3841 | 2023-03-05 | 1822 | 20230306 | 802 | 2024035 | 820 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 68060 | 39.1277 | -120.9168 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0040523 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822258 | 0 | EPSS Ckt | N | 2023
64420 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 100000040277 | 2023-03-06 | 917 | 20230306 | 1044 | 2024225 | 87 | Transformer only | Vegetation | Tree - fell into line | 1 | 87 | 38.7143 | -120.6164 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0040619 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1822323 | 0 | EPSS Ckt | N | 2023
64426 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | WIRE DOWN | 2023-03-06 | 1646 | 20230308 | 1658 | 2024978 | 2892 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2892 | 39.3812 | -121.0594 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041148 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Open Circuit | 0 | No | Yes | No | 1822614 | 0 | EPSS Ckt | N | 2023
64427 | SIERRA | NEVADA | BRUNSWICK-1104 | 152481104 | FUSE | 3133 | 2023-03-06 | 1702 | 20230307 | 1624 | 2024988 | 1402 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4206 | 39.2896 | -121.0462 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041228 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1822638 | 0 | EPSS Ckt | N | 2023
64436 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4817 | 2023-03-07 | 2033 | 20230311 | 1812 | 2026356 | 5619 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 258474 | 39.2099 | -120.9363 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1823059 | 0 | EPSS Ckt | N | 2023
64441 | SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 2023-03-08 | 721 | 20230311 | 920 | 2026284 | 4439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 35504 | 39.4382 | -120.9965 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041494 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | Yes | No | 1822812 | 0 | EPSS Ckt | N | 2023 | NONE
64442 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 2023-03-08 | 859 | 20230310 | 1605 | 2026386 | 3306 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 42978 | 39.2097 | -120.9435 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041833 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1822975 | 0 | EPSS Ckt | N | 2023
64456 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 2023-03-09 | 1259 | 20230312 | 1515 | 2028295 | 4456 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 120312 | 39.1757 | -120.9295 | Yes | Overcast;32-90 F |  |  | 23-0043746 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824263 | 0 | EPSS Ckt | N | 2023
64459 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 2023-03-09 | 1637 | 20230309 | 1829 | 2028124 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 19936 | 38.7138 | -120.6231 | Yes | Partly Cloudy-Fog-Rain;32-90 F | Insulator | Broken | 23-0042242 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1823190 | 0 | EPSS Ckt | N | 2023
64473 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 2023-03-10 | 238 | 20230310 | 406 | 2029954 | 88 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2495 | 219560 | 38.7393 | -120.6773 | No | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0042700 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1823513 | 0 | EPSS Ckt | N | 2023 | ABC TIME
64478 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-03-10 | 348 | 20230310 | 1140 | 2030026 | 472 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 6608 | 38.7941 | -120.8199 | No | Clear;32-90F |  |  | 23-0043026 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823700 | 0 | EPSS Ckt | N | 2023
64495 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2023-03-10 | 1758 | 20230310 | 2025 | 2031508 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2058 | 38.7941 | -120.8199 | No | Overcast;32-90 F |  |  | 23-0043253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1823840 | 0 | EPSS Ckt | N | 2023
64499 | SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 2023-03-10 | 2338 | 20230312 | 1551 | 2031764 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 293315 | 39.3638 | -120.7923 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037093 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1823988 | 0 | Non-EPSS | N | 2023 | SGF
64513 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6369 | 2023-03-11 | 1818 | 20230312 | 1048 | 2032813 | 990 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2970 | 39.2167 | -120.8238 | No | Clear;32-90F | Crossarm- Steel | Broken | 23-0043550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824089 | 0 | EPSS Ckt | N | 2023
64514 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30263 | 2023-03-11 | 1918 | 20230312 | 1546 | 2032850 | 1228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 41752 | 39.2154 | -120.9321 | No | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 23-0043604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824144 | 0 | EPSS Ckt | N | 2023
64517 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 2023-03-12 | 718 | 20230312 | 904 | 2033078 | 106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 132 | 13992 | 38.8063 | -120.925 | No | Clear;32-90F |  |  | 23-0043657 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1824192 | 0 | EPSS Ckt | N | 2023
64523 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30251 | 2023-03-12 | 1543 | 20230312 | 1850 | 2033426 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2618 | 39.1686 | -120.9373 | No | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0043768 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1824282 | 0 | EPSS Ckt | N | 2023
64534 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223449243043 | 2023-03-13 | 1011 | 20230313 | 1123 | 2034272 | 72 | Transformer only | Environmental/External | Lightning | 1 | 72 | 38.8417 | -120.7897 | No | Clear;32-90F | Fuse | Failed/Faulted | 23-0044100 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1824519 | 0 | EPSS Ckt | N | 2023
64557 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21295 | 2023-03-14 | 1145 | 20230314 | 2013 | 2038083 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | 38.6429 | -120.6988 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044936 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1825026 | 0 | EPSS Ckt | N | 2023
64563 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 2023-03-14 | 1216 | 20230315 | 1907 | 2038331 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9255 | 38.5951 | -120.8115 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825482 | 0 | EPSS Ckt | N | 2023
64567 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9353 | 2023-03-14 | 1247 | 20230315 | 1241 | 2039356 | 1434 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18642 | 38.9015 | -120.9035 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0045357 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | No | No | 1825346 | 0 | EPSS Ckt | N | 2023
64574 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 2023-03-14 | 1405 | 20230316 | 1141 | 2041765 | 2736 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 10096 | 39.3823 | -121.0478 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045433 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825410 | 0 | EPSS Ckt | N | 2023
64576 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3911 | 2023-03-14 | 1419 | 20230315 | 1801 | 2042006 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8310 | 39.3625 | -121.1125 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045630 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825574 | 0 | EPSS Ckt | N | 2023
64589 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18873 | 2023-03-14 | 1623 | 20230315 | 1755 | 2043253 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 32172 | 38.8161 | -120.9016 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825652 | 0 | EPSS Ckt | N | 2023
64593 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 2023-03-14 | 1714 | 20230315 | 1811 | 2043753 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 348214 | 39.3676 | -121.0458 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1825604 | 0 | EPSS Ckt | N | 2023 | A+B+C
64596 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-03-14 | 1808 | 20230315 | 1453 | 2043997 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 1041 | 92145 | 38.8154 | -120.8221 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045724 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1825661 | 0 | EPSS Ckt | N | 2023 | A+C
64597 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 32831 | 2023-03-14 | 1826 | 20230315 | 943 | 2044237 | 917 | Distribution Circuit | Company Initiated | Improper Construction | 3 | 2751 | 39.3861 | -121.0336 | Yes | Clear-Strong Winds;32-90 F | Lightning Arrestor | Burned/flashed | 23-0045907 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1825832 | 0 | EPSS Ckt | N | 2023
64607 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222735562820 | 2023-03-15 | 1425 | 20230315 | 1452 | 2046246 | 27 | Transformer only | Vegetation | Tree - fell into line | 1 | 27 | 39.3879 | -121.0329 | No | Clear;32-90 F | Lightning Arrestor | Burned/flashed | 23-0046363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1826173 | 0 | EPSS Ckt | N | 2023
64626 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223979237978 | 2023-03-18 | 1435 | 20230318 | 1643 | 2051296 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 256 | 38.701 | -120.6069 | No | Clear;32-90 F |  |  | 23-0048345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1827549 | 0 | EPSS Ckt | N | 2023
64626 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223979237978 | 2023-03-18 | 1435 | 20230318 | 1643 | 2051296 | 128 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 256 | 38.701 | -120.6069 | No | Clear;32-90 F |  |  | 23-0048345 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1827549 | 0 | EPSS Ckt | N | 2023
64659 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8107 | 2023-03-22 | 1836 | 20230323 | 1411 | 2063576 | 1175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 112800 | 39.3524 | -121.0655 | No | Partly Cloudy-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0050993 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1829380 | 0 | EPSS Ckt | N | 2023
64677 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223374556595 | 2023-03-27 | 1056 | 20230327 | 1841 | 2068594 | 465 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 930 | 39.2146 | -120.8102 | No | Clear;Below 32 F | Transformer (OH) | Normal | 23-0053050 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1830847 | 0 | EPSS Ckt | N | 2023
64681 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6379 | 2023-03-27 | 1532 | 20230327 | 1722 | 2069013 | 110 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1430 | 39.2052 | -120.8318 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0053069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1830857 | 0 | EPSS Ckt | N | 2023
64694 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-03-28 | 908 | 20230329 | 1117 | 2069856 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 2003 | 412640 | 39.0997 | -121.05 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0053335 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831048 | 0 | EPSS Ckt | N | 2023 | A GRD
64696 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 2023-03-28 | 912 | 20230328 | 1319 | 2069869 | 247 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 10127 | 39.0098 | -120.8455 | No | Clear-Strong Winds;32-90 F |  |  | 23-0053593 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831202 | 0 | EPSS Ckt | N | 2023
64702 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6365 | 2023-03-28 | 924 | 20230328 | 1454 | 2069915 | 330 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 24 | 7920 | 39.1734 | -120.8591 | No | Partly Cloudy-Strong Winds;32-90 F |  |  | 23-0053716 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831274 | 0 | EPSS Ckt | N | 2023
64755 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 2023-03-28 | 1625 | 20230329 | 1207 | 2071052 | 1182 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 102834 | 39.3404 | -121.1319 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053790 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831304 | 0 | EPSS Ckt | N | 2023 | ABC
64762 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13789 | 2023-03-28 | 1705 | 20230329 | 1258 | 2071201 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 53685 | 38.5961 | -120.8061 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831364 | 0 | EPSS Ckt | N | 2023
64768 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | OCB | 1101/2 | 2023-03-28 | 1804 | 20230329 | 1620 | 2071371 | 1336 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 412 | 494692 | 39.4382 | -120.9964 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0053866 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831357 | 0 | EPSS Ckt | N | 2023 | INSTA OC
64769 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8107 | 2023-03-28 | 1806 | 20230329 | 1922 | 2071342 | 1516 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 145536 | 39.3524 | -121.0655 | No | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken | 23-0054212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831566 | 0 | EPSS Ckt | N | 2023
64770 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 2023-03-28 | 1807 | 20230329 | 1949 | 2071351 | 1542 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 63222 | 39.3451 | -121.0765 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0054344 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831623 | 0 | EPSS Ckt | N | 2023
64777 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2023-03-28 | 1859 | 20230329 | 1641 | 2071657 | 1302 | Distribution Circuit | 3rd Party | Vehicle | 613 | 182496 | 38.9 | -120.9074 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053888 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831371 | 0 | EPSS Ckt | N | 2023 | A B C
64782 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 9257 | 2023-03-28 | 1917 | 20230329 | 1900 | 2072467 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 65458 | 39.2008 | -120.932 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054628 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831729 | 0 | EPSS Ckt | N | 2023
64783 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 7469 | 2023-03-28 | 1922 | 20230329 | 1111 | 2071915 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 73073 | 39.2081 | -120.9493 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831600 | 0 | EPSS Ckt | N | 2023
64794 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 2023-03-28 | 2036 | 20230329 | 1434 | 2072042 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14014 | 39.2097 | -120.9435 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Normal | 23-0054517 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831680 | 0 | EPSS Ckt | N | 2023
64804 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-03-29 | 255 | 20230331 | 1006 | 2072241 | 3311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 130262 | 39.4655 | -120.8443 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0053985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831463 | 0 | EPSS Ckt | N | 2023 | SGF
64804 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-03-29 | 255 | 20230331 | 1006 | 2072241 | 3311 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 130262 | 39.4655 | -120.8443 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0053985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1831463 | 0 | EPSS Ckt | N | 2023 | SGF
64805 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8003 | 2023-03-29 | 255 | 20230331 | 1514 | 2074367 | 3619 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7238 | 39.4456 | -120.8237 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0054974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Three Phase Fault | 0 | No | Yes | No | 1831954 | 0 | EPSS Ckt | N | 2023
64813 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224010739430 | 2023-03-29 | 949 | 20230329 | 1119 | 2072684 | 90 | Transformer only | Environmental/External | Ice or snow | 2 | 180 | 38.7397 | -120.5957 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0054272 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831589 | 0 | EPSS Ckt | N | 2023
64814 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | RECLOSER | 875388 | 2023-03-29 | 1009 | 20230330 | 1304 | 2072720 | 1402 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 107768 | 39.2827 | -120.9454 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0054194 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1831558 | 0 | EPSS Ckt | N | 2023 | A & B
64817 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3991 | 2023-03-29 | 1050 | 20230329 | 1217 | 2072772 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 522 | 39.3935 | -121.1101 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0054227 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1831575 | 0 | EPSS Ckt | N | 2023
64818 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223991040742 | 2023-03-29 | 1056 | 20230329 | 1109 | 2072808 | 13 | Transformer only | Environmental/External | Ice or snow | 2 | 26 | 38.7754 | -120.5988 | No | Overcast;32-90 F | Fuse | Failed/Faulted | 23-0054248 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831583 | 0 | EPSS Ckt | N | 2023
64820 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 3891 | 2023-03-29 | 1158 | 20230329 | 1638 | 2073015 | 280 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 31 | 8680 | 39.2197 | -120.9493 | No | Overcast-Drizzle;32-90 F |  |  | 23-0054583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1831701 | 0 | EPSS Ckt | N | 2023
64822 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 2023-03-29 | 1221 | 20230329 | 1827 | 2073036 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5322 | 39.2095 | -120.827 | No | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Failed/Faulted | 23-0054502 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831676 | 1 | EPSS Ckt | N | 2023
64823 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6373 | 2023-03-29 | 1408 | 20230329 | 1629 | 2073224 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 3856 | 39.1972 | -120.833 | No | Overcast-Fog-Snow;Below 32 F | Lightning Arrestor | Burned/flashed | 23-0054507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831677 | 1 | EPSS Ckt | N | 2023
64827 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 2023-03-29 | 2001 | 20230330 | 1146 | 2073697 | 945 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 59 | 55755 | 39.2173 | -120.8092 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0054704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1831794 | 0 | EPSS Ckt | N | 2023
64845 | SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 2023-03-31 | 1320 | 20230331 | 1329 | 2075510 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1278 | 39.3638 | -120.7923 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0053985 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1832233 | 0 | Non-EPSS | N | 2023 | NONE
64850 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222495060485 | 2023-04-01 | 1523 | 20230401 | 2045 | 2076821 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 644 | 39.3246 | -121.1201 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0055886 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1832481 | 0 | EPSS Ckt | N | 2023
64890 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222987556615 | 2023-04-08 | 1919 | 20230408 | 2045 | 2083413 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 39.2165 | -120.9469 | No | Clear;32-90 F |  |  | 23-0058814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | None | 0 | No | No | No | 1834266 | 0 | EPSS Ckt | N | 2023
64897 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21411 | 2023-04-10 | 1116 | 20230410 | 2215 | 2084431 | 659 | Distribution Circuit | 3rd Party | Vehicle | 17 | 11203 | 38.7165 | -120.623 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0059137 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1834578 | 0 | EPSS Ckt | N | 2023
64902 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ'S 1/S/OF CGC#222980856721 | 2023-04-10 | 2222 | 20230411 | 31 | 2084931 | 129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 4119 | 39.2194 | -120.9489 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0059325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1834653 | 0 | EPSS Ckt | N | 2023
64928 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 3841 | 2023-04-16 | 2146 | 20230416 | 2237 | 2089838 | 51 | Distribution Circuit | 3rd Party | Vehicle | 83 | 4233 | 39.1277 | -120.9168 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0061503 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836193 | 0 | EPSS Ckt | N | 2023
64931 | SIERRA | PLACER | HALSEY-1102 | 152241102 | JUMPER | OJ'S 1 POLE N/OF CGC 222871748284 | 2023-04-17 | 1019 | 20230417 | 1331 | 2090292 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 768 | 38.9881 | -120.9907 | No | Overcast;32-90 F | Pole-Wood | Broken | 23-0061604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1836386 | 0 | EPSS Ckt | N | 2023
64945 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4499 | 2023-04-19 | 1148 | 20230419 | 1346 | 2092531 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1534 | 39.2097 | -120.9435 | No | Overcast;32-90 F | Conductor- Overhead | Deteriorated | 23-0062452 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1837034 | 0 | EPSS Ckt | N | 2023
64973 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9279 | 2023-04-25 | 1405 | 20230425 | 1457 | 2096810 | 52 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 1092 | 38.9451 | -120.9136 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0064583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1838463 | 0 | EPSS Ckt | N | 2023
64977 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223267942569 | 2023-04-26 | 1811 | 20230426 | 2112 | 2097824 | 181 | Transformer only | Vegetation | Tree - fell into line | 2 | 362 | 38.83 | -120.8538 | No | Clear;32-90 F | Transformer | Broken | 23-0065215 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | No | No | 1838815 | 0 | EPSS Ckt | N | 2023
64980 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | JUMPER | OJS 2 SPANS S/OF CGC 222943351499 | 2023-04-27 | 1207 | 20230427 | 1304 | 2098401 | 57 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 57 | 39.0749 | -120.9632 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0065477 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839026 | 0 | EPSS Ckt | N | 2023
64986 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 2023-04-28 | 1323 | 20230428 | 1440 | 2099306 | 77 | Distribution Circuit | Vegetation | Tree - grew into line | 11 | 847 | 38.8791 | -120.8335 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0066103 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1839347 | 0 | EPSS Ckt | N | 2023
65002 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | 1 SPAN SS OF CGC 223968335265 | 2023-05-01 | 1144 | 20230501 | 1610 | 2101574 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 266 | 38.6275 | -120.6115 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066662 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1839901 | 0 | EPSS Ckt | N | 2023
65013 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-05-02 | 1518 | 20230502 | 1531 | 2103037 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 2596 | 39.2562 | -120.7669 | No | Overcast-Fog;32-90 F |  |  | 23-0067309 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1840251 | 0 | EPSS Ckt | N | 2023 | ABOVE MTT
65022 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-05-03 | 1417 | 20230503 | 1430 | 2103933 | 13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 202 | 2606 | 39.2562 | -120.7669 | No | Overcast-Fog;Below 32 F |  |  | 23-0067756 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1840552 | 0 | EPSS Ckt | N | 2023 | SGF
65028 | SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 2023-05-04 | 1832 | 20230505 | 242 | 2104938 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 12740 | 39.4382 | -120.9965 | No | Overcast;32-90 F | Insulator | Broken | 23-0068463 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1840932 | 0 | EPSS Ckt | N | 2023 | NONE
65058 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 2023-05-08 | 1559 | 20230509 | 1401 | 2107994 | 1322 | Distribution Circuit | 3rd Party | Vehicle | 59 | 75086 | 39.2173 | -120.8092 | No | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 23-0069705 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | Yes | No | 1841780 | 0 | EPSS Ckt | N | 2023
65071 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 30447 | 2023-05-11 | 400 | 20230511 | 1200 | 2109881 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 960 | 39.2144 | -120.9575 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0070715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1842413 | 0 | EPSS Ckt | N | 2023
65076 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222639561110 | 2023-05-11 | 1751 | 20230512 | 241 | 2110621 | 530 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1590 | 39.3404 | -121.0672 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071141 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1842673 | 0 | EPSS Ckt | N | 2023
65093 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | FUSE | 4177 | 2023-05-15 | 2110 | 20230516 | 23 | 2113584 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2509 | 39.2159 | -120.9505 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072096 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843421 | 0 | EPSS Ckt | N | 2023
65097 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 2 N/OF OF CGC 222966656766 | 2023-05-16 | 1455 | 20230516 | 1852 | 2114289 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 474 | 39.2214 | -120.9545 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072396 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843660 | 0 | EPSS Ckt | N | 2023
65100 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223667241479 | 2023-05-17 | 946 | 20230517 | 1159 | 2114920 | 133 | Transformer only | Vegetation | Tree - fell into line | 1 | 133 | 38.7983 | -120.7156 | No | Clear;32-90 F | Fuse | Burned Open | 23-0072697 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1843955 | 0 | EPSS Ckt | N | 2023
65102 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 1 N/OF CGC 222982556776 | 2023-05-17 | 1330 | 20230517 | 1459 | 2114965 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 890 | 39.2214 | -120.9486 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0072663 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1843938 | 0 | EPSS Ckt | N | 2023
65109 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 836878 | 2023-05-18 | 959 | 20230518 | 1958 | 2115958 | 599 | Distribution Circuit | Company Initiated | Coordination failure | 4863 | 2388135 | 38.7371 | -120.6759 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0073057 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1844174 | 0 | EPSS Ckt | Y | 2023 | DCD SGF
65128 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | TRANSFORMER | 222995553395 | 2023-05-20 | 1132 | 20230520 | 1223 | 2117607 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 153 | 39.128 | -120.9454 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0073831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1844681 | 0 | EPSS Ckt | N | 2023
65143 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223876138504 | 2023-05-22 | 2118 | 20230523 | 304 | 2119110 | 346 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 692 | 38.7165 | -120.6428 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0074426 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1845148 | 0 | EPSS Ckt | N | 2023
65161 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 41535 | 2023-05-27 | 757 | 20230527 | 845 | 2122568 | 48 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 144 | 39.0864 | -120.9667 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0076279 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1846295 | 0 | EPSS Ckt | N | 2023
65182 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 2023-06-05 | 1542 | 20230606 | 121 | 2129440 | 579 | Distribution Circuit | Environmental/External | Lightning | 20 | 6667 | 38.8528 | -120.789 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0079124 | OH | Sus | 35454305 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1848132 | 0 | EPSS Ckt | N | 2023
65187 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-06-05 | 2110 | 20230605 | 2120 | 2130031 | 10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 284 | 2835 | 39.2562 | -120.7669 | No | Partly Cloudy;32-90 F |  |  | 23-0079133 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848143 | 0 | EPSS Ckt | N | 2023 | SGF
65192 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-06-06 | 1708 | 20230606 | 1801 | 2131159 | 53 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 15047 | 39.2562 | -120.7669 | No | Overcast-Rain;32-90 F |  |  | 23-0079542 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848462 | 0 | EPSS Ckt | N | 2023 | SGF
65199 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-06-08 | 704 | 20230608 | 817 | 2132334 | 73 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 284 | 20717 | 39.2562 | -120.7669 | No | Partly Cloudy;32-90 F |  |  | 23-0080149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1848894 | 0 | EPSS Ckt | N | 2023 | SGF
65207 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 2023-06-10 | 1636 | 20230611 | 59 | 2134377 | 503 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 10060 | 38.7853 | -120.6077 | No | Partly Cloudy-Lightning;32-90 F |  |  | 23-0081234 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849679 | 0 | EPSS Ckt | N | 2023
65209 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223976240822 | 2023-06-10 | 1653 | 20230611 | 1126 | 2134389 | 1113 | Transformer only | Environmental/External | Lightning | 1 | 1113 | 38.7783 | -120.6058 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081239 | OH | Sus | 35457023 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849684 | 0 | EPSS Ckt | N | 2023
65210 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223970541066 | 2023-06-11 | 124 | 20230611 | 1603 | 2134516 | 879 | Transformer only | Environmental/External | Lightning | 1 | 879 | 38.7859 | -120.6077 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0081235 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1849680 | 0 | EPSS Ckt | N | 2023
65213 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223938040859 | 2023-06-11 | 843 | 20230611 | 1715 | 2134719 | 512 | Transformer only | Environmental/External | Lightning | 1 | 512 | 38.7801 | -120.6193 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0081320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849738 | 0 | EPSS Ckt | N | 2023
65214 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223961541100 | 2023-06-11 | 911 | 20230611 | 1216 | 2134567 | 185 | Transformer only | Environmental/External | Lightning | 1 | 185 | 38.7867 | -120.6118 | No | Partly Cloudy;32-90 F | Transformer | Malfunctioning | 23-0081258 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1849702 | 0 | EPSS Ckt | N | 2023
65225 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6045 | 2023-06-13 | 1710 | 20230614 | 1301 | 2136336 | 1191 | Distribution Circuit | Equipment Failure/Involved | Underground | 16 | 19056 | 38.9775 | -120.8892 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0082116 | UG | Sus | 45846456 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1850425 | 0 | EPSS Ckt | N | 2023
65231 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6373 | 2023-06-14 | 1309 | 20230614 | 1529 | 2136984 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 5740 | 39.1972 | -120.833 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0082339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1850628 | 0 | EPSS Ckt | N | 2023
65237 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-06-15 | 1454 | 20230615 | 1648 | 2137825 | 114 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 936 | 106704 | 38.7391 | -120.6681 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1850880 | 0 | EPSS Ckt | Y | 2023 | BC
65244 | SIERRA | NEVADA | HIGGINS-1110 | 152691110 | SWITCH | 6305 | 2023-06-16 | 907 | 20230616 | 1125 | 2138377 | 138 | Distribution Circuit | Company Initiated | Return Circuit Normal | 19 | 2618 | 39.0899 | -120.98 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0082914 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | None | 0 | No | No | No | 1851089 | 0 | EPSS Ckt | N | 2023
65248 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | SWITCH | 645945 | 2023-06-16 | 1355 | 20230616 | 1601 | 2138666 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 4788 | 38.609 | -120.8441 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0083178 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851168 | 0 | EPSS Ckt | N | 2023
65250 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 2023-06-16 | 1714 | 20230617 | 633 | 2139150 | 799 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 2397 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0083326 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851249 | 0 | EPSS Ckt | N | 2023
65256 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 2023-06-17 | 640 | 20230617 | 752 | 2139154 | 72 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 216 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0083327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1851250 | 0 | EPSS Ckt | N | 2023
65257 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223850138915 | 2023-06-17 | 814 | 20230617 | 940 | 2139184 | 86 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 258 | 38.7285 | -120.6517 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0083351 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1851300 | 0 | EPSS Ckt | N | 2023
65273 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-06-20 | 1400 | 20230620 | 1411 | 2141494 | 11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 934 | 10274 | 38.7391 | -120.6681 | No | Clear;32-90 F | Woodpin | Normal | 23-0083938 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851931 | 0 | EPSS Ckt | N | 2023 | N/A
65274 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 2023-06-20 | 2044 | 20230621 | 1517 | 2141776 | 1113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 42420 | 39.4642 | -120.8458 | No | Clear;32-90 F | Insulator | Broken | 23-0084019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1851973 | 0 | EPSS Ckt | N | 2023
65280 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223022845646 | 2023-06-21 | 853 | 20230621 | 1407 | 2142063 | 314 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 628 | 38.9148 | -120.9391 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0084347 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852205 | 0 | EPSS Ckt | N | 2023
65281 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | TRANSFORMER | 223068548540 | 2023-06-21 | 858 | 20230621 | 1010 | 2142090 | 72 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 72 | 38.9943 | -120.922 | No | Clear;32-90 F |  |  | 23-0084191 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1852122 | 0 | EPSS Ckt | N | 2023
65282 | SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 2023-06-21 | 1537 | 20230621 | 1547 | 2142584 | 10 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1420 | 39.3638 | -120.7923 | No | Clear;32-90 F | Insulator | Normal | 23-0084019 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1852222 | 0 | Non-EPSS | N | 2023 | NONE
65291 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 55686 | 2023-06-23 | 1105 | 20230623 | 1604 | 2144125 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 164 | 49036 | 39.4652 | -120.8449 | No | Clear;32-90 F |  |  | 23-0085064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852717 | 0 | EPSS Ckt | Y | 2023 | B & C
65291 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 55686 | 2023-06-23 | 1105 | 20230623 | 1604 | 2144125 | 299 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 164 | 49036 | 39.4652 | -120.8449 | No | Clear;32-90 F |  |  | 23-0085064 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852717 | 0 | EPSS Ckt | Y | 2023 | B & C
65292 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | FUSE | 8021 | 2023-06-23 | 1755 | 20230624 | 1310 | 2144359 | 1155 | Distribution Circuit | Animal | Bird found | 9 | 10395 | 39.463 | -120.8507 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0085250 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1852776 | 0 | EPSS Ckt | N | 2023
65296 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223204943047 | 2023-06-26 | 1114 | 20230626 | 1136 | 2145975 | 22 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 22 | 38.8431 | -120.8753 | No | Clear;32-90 F | Secondary | Deteriorated | 23-0085595 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1853196 | 0 | EPSS Ckt | N | 2023
65305 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-06-27 | 1959 | 20230627 | 2017 | 2147317 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 165 | 2970 | 39.4655 | -120.8443 | No | Clear;32-90 F |  |  | 23-0040752 | OH | Sus | 31605566 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853552 | 0 | EPSS Ckt | N | 2023 | SGF
65305 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2023-06-27 | 1959 | 20230627 | 2017 | 2147317 | 18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 165 | 2970 | 39.4655 | -120.8443 | No | Clear;32-90 F |  |  | 23-0040752 | OH | Sus | 31605566 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1853552 | 0 | EPSS Ckt | N | 2023 | SGF
65322 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ 2 SPANS SS OF CGC 222971053592 | 2023-06-30 | 1958 | 20230630 | 2318 | 2150308 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 18600 | 39.1332 | -120.9533 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0087749 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1854447 | 0 | EPSS Ckt | N | 2023
65330 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21133 | 2023-07-02 | 917 | 20230702 | 1446 | 2151959 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 987 | 38.6426 | -120.6995 | No | Clear;32-90 F | Other | Malfunctioning | 23-0088148 | OH | Sus | 45867513 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1854777 | 0 | EPSS Ckt | N | 2023
65345 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 56865 | 2023-07-05 | 1102 | 20230705 | 1255 | 2154617 | 113 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 4633 | 39.1923 | -120.832 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0088943 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1855321 | 0 | EPSS Ckt | N | 2023
65346 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5591 | 2023-07-05 | 1200 | 20230705 | 1505 | 2154650 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 3700 | 38.8608 | -120.7883 | No | Clear;32-90 F |  |  | 23-0089028 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855335 | 0 | EPSS Ckt | N | 2023
65359 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 2023-07-08 | 827 | 20230708 | 949 | 2156969 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 1640 | 38.7853 | -120.6077 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0090069 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1855829 | 0 | EPSS Ckt | N | 2023
65361 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 935730 | 2023-07-08 | 1205 | 20230708 | 1643 | 2157148 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 24186 | 39.4387 | -120.9996 | No | Clear;32-90 F |  |  | 23-0090108 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1855861 | 0 | EPSS Ckt | Y | 2023 | A & C
65385 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6161 | 2023-07-12 | 921 | 20230712 | 1452 | 2160606 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8937 | 39.0231 | -120.9583 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0091188 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1856789 | 0 | EPSS Ckt | N | 2023
65386 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-07-12 | 930 | 20230712 | 1426 | 2160628 | 296 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 840 | 121286 | 38.643 | -120.6953 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091202 | OH | Sus | 31655232 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856805 | 0 | EPSS Ckt | Y | 2023 | A/B
65386 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-07-12 | 930 | 20230712 | 1426 | 2160628 | 296 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 840 | 121286 | 38.643 | -120.6953 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0091202 | OH | Sus | 31655232 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1856805 | 0 | EPSS Ckt | Y | 2023 | A/B
65392 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223837633802 | 2023-07-12 | 1936 | 20230713 | 340 | 2161187 | 484 | Transformer only | 3rd Party | Vehicle | 1 | 484 | 38.5868 | -120.658 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0091548 | OH | Sus | 31655156 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1856941 | 0 | EPSS Ckt | N | 2023
65408 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-07-15 | 1956 | 20230716 | 1152 | 2163818 | 956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1042 | 703940 | 38.8154 | -120.8221 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092713 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857733 | 0 | EPSS Ckt | Y | 2023 | C AND GRD
65413 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | TRANSFORMER | 223292034834 | 2023-07-16 | 902 | 20230716 | 1007 | 2164085 | 65 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 130 | 38.6177 | -120.8488 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0092792 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1857824 | 0 | EPSS Ckt | N | 2023
65420 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-07-17 | 555 | 20230717 | 1026 | 2165017 | 271 | Distribution Circuit | Animal | Bird found | 1042 | 245014 | 38.8154 | -120.8221 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0092981 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1857995 | 0 | EPSS Ckt | Y | 2023 | A C
65421 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 2023-07-17 | 815 | 20230717 | 2334 | 2165237 | 919 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 919 | 38.6344 | -120.6373 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0093061 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858106 | 0 | EPSS Ckt | N | 2023
65425 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | FB 2 POLES SS OF CGC 222641060670 | 2023-07-17 | 1457 | 20230717 | 1553 | 2165722 | 56 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 112 | 39.3312 | -121.0667 | No | Clear;Above 90 | Crossarm- Wood | Broken | 23-0093281 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858220 | 0 | EPSS Ckt | N | 2023
65429 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223887035590 | 2023-07-18 | 804 | 20230718 | 1433 | 2166263 | 389 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 389 | 38.6352 | -120.6401 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0093698 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858512 | 0 | EPSS Ckt | N | 2023
65434 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223823239455 | 2023-07-19 | 101 | 20230719 | 245 | 2167362 | 104 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 312 | 38.7423 | -120.6605 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0093988 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858626 | 0 | EPSS Ckt | N | 2023
65438 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-07-19 | 1020 | 20230719 | 1121 | 2167792 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 827 | 48084 | 38.643 | -120.6953 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0094149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858823 | 0 | EPSS Ckt | Y | 2023 | C GRD
65438 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-07-19 | 1020 | 20230719 | 1121 | 2167792 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 827 | 48084 | 38.643 | -120.6953 | No | Clear;32-90 F | Conductor- Overhead | Together | 23-0094149 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1858823 | 0 | EPSS Ckt | Y | 2023 | C GRD
65439 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8417 | 2023-07-19 | 1538 | 20230719 | 2156 | 2168345 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 13230 | 39.4605 | -121.0327 | No | Clear;Above 90 | Conductor- Overhead | Deteriorated | 23-0094334 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858903 | 0 | EPSS Ckt | N | 2023
65440 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 2023-07-19 | 1627 | 20230719 | 1716 | 2168326 | 49 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 8575 | 38.9133 | -120.9318 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0094353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858908 | 0 | EPSS Ckt | N | 2023 | NONE
65442 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S 1 SPAN S/S OF CGC 223552240344 | 2023-07-19 | 2045 | 20230720 | 27 | 2168484 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 222 | 38.7674 | -120.7558 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0094399 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1858928 | 0 | EPSS Ckt | N | 2023
65452 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-07-21 | 905 | 20230722 | 46 | 2169718 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 51191 | 39.2562 | -120.7669 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0095098 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1859374 | 0 | EPSS Ckt | Y | 2023 | A & B
65455 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 497205 | 2023-07-21 | 1447 | 20230721 | 2108 | 2170075 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 19431 | 39.4657 | -120.8447 | No | Clear;Above 90 | Insulator | Broken | 23-0095353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859463 | 0 | EPSS Ckt | N | 2023
65455 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 497205 | 2023-07-21 | 1447 | 20230721 | 2108 | 2170075 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 19431 | 39.4657 | -120.8447 | No | Clear;Above 90 | Insulator | Broken | 23-0095353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1859463 | 0 | EPSS Ckt | N | 2023
65481 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 2023-07-24 | 1214 | 20230724 | 1721 | 2172571 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3377 | 39.4564 | -121.0375 | No | Clear;32-90 F | Insulator | Broken | 23-0095986 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860061 | 0 | EPSS Ckt | N | 2023
65482 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-07-25 | 109 | 20230725 | 300 | 2172977 | 111 | Distribution Circuit | Animal | Squirrel | 1872 | 207792 | 39.0997 | -121.05 | No | Clear;32-90 F | Regulator | Normal | 23-0096270 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1860172 | 0 | EPSS Ckt | Y | 2023 | B & C
65491 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 4513 | 2023-07-26 | 908 | 20230726 | 1229 | 2174224 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 11055 | 39.2037 | -120.8377 | No | Clear;32-90 F | Secondary | Broken | 23-0096934 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1860628 | 0 | EPSS Ckt | N | 2023
65500 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223777537275 | 2023-07-27 | 1511 | 20230727 | 1838 | 2175589 | 207 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 207 | 38.6825 | -120.6776 | No | Clear;32-90 F |  |  | 23-0097811 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861049 | 0 | EPSS Ckt | N | 2023
65501 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-07-27 | 1648 | 20230728 | 254 | 2175677 | 606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1872 | 222205 | 39.0997 | -121.05 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0097764 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1861033 | 0 | EPSS Ckt | Y | 2023 | C
65507 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 2023-07-28 | 1038 | 20230728 | 1511 | 2176297 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 12058 | 39.4642 | -120.8458 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0097949 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861279 | 0 | EPSS Ckt | N | 2023
65508 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 863 | 2023-07-28 | 1122 | 20230728 | 1246 | 2176317 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1010 | 84840 | 39.4673 | -120.8462 | No | Clear;32-90 F | Insulator | Broken | 23-0097928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861286 | 0 | EPSS Ckt | N | 2023
65508 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | SWITCH | 863 | 2023-07-28 | 1122 | 20230728 | 1246 | 2176317 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1010 | 84840 | 39.4673 | -120.8462 | No | Clear;32-90 F | Insulator | Broken | 23-0097928 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1861286 | 0 | EPSS Ckt | N | 2023
65549 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 2023-08-04 | 1736 | 20230805 | 322 | 2182697 | 586 | Distribution Circuit | 3rd Party | Vehicle | 41 | 15122 | 39.3451 | -121.0765 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0100800 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | Yes | No | 1863179 | 0 | EPSS Ckt | N | 2023
65565 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2023-08-08 | 1229 | 20230808 | 1550 | 2185794 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 18090 | 38.9 | -120.9074 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0101531 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1864050 | 0 | EPSS Ckt | Y | 2023 | NA
65566 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-08-08 | 1630 | 20230808 | 1818 | 2185995 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 1872 | 202176 | 39.0997 | -121.05 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0101901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1864092 | 0 | EPSS Ckt | Y | 2023 | B
65595 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30929 | 2023-08-15 | 1332 | 20230815 | 1449 | 2191765 | 77 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 77 | 38.896 | -120.9189 | No | Clear;Above 90 |  |  | 23-0104669 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865947 | 0 | EPSS Ckt | N | 2023
65596 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-08-15 | 1537 | 20230815 | 1731 | 2191893 | 114 | Distribution Circuit | Vegetation | Tree - fell into line | 937 | 106818 | 38.7391 | -120.6681 | No | Clear;Above 90 | Conductor- Overhead | Normal | 23-0104720 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865963 | 0 | EPSS Ckt | Y | 2023 | B-C
65598 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-15 | 1747 | 20230815 | 2128 | 2192065 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 863 | 168205 | 38.643 | -120.6953 | No | Clear;Above 90 |  |  | 23-0104786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865987 | 0 | EPSS Ckt | Y | 2023 | B & C
65598 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-15 | 1747 | 20230815 | 2128 | 2192065 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 863 | 168205 | 38.643 | -120.6953 | No | Clear;Above 90 |  |  | 23-0104786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1865987 | 0 | EPSS Ckt | Y | 2023 | B & C
65599 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | SWITCH | 836878 | 2023-08-16 | 936 | 20230816 | 1128 | 2192681 | 112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4951 | 273331 | 38.7371 | -120.6759 | No | Clear;32-90 F | Metering Equipment | Malfunctioning | 23-0104980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1866203 | 0 | EPSS Ckt | Y | 2023
65601 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223164739955 | 2023-08-16 | 1241 | 20230816 | 1828 | 2192869 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 694 | 38.7588 | -120.8911 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0105159 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1866289 | 0 | EPSS Ckt | N | 2023
65630 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 2023-08-19 | 2110 | 20230820 | 1324 | 2196476 | 974 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4870 | 38.8277 | -120.9417 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0106527 | OH | Sus | 31664104 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | Yes | No | 1867197 | 0 | EPSS Ckt | N | 2023
65651 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-21 | 1518 | 20230821 | 1537 | 2198402 | 19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 863 | 16258 | 38.643 | -120.6953 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0107184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867713 | 0 | EPSS Ckt | Y | 2023 | A GRD
65651 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-21 | 1518 | 20230821 | 1537 | 2198402 | 19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 863 | 16258 | 38.643 | -120.6953 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0107184 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867713 | 0 | EPSS Ckt | Y | 2023 | A GRD
65653 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-08-21 | 1546 | 20230822 | 920 | 2198448 | 1054 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 202 | 170632 | 39.2562 | -120.7669 | No | Partly Cloudy-Rain-Lightning;32-90 F |  |  | 23-0107212 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867731 | 0 | EPSS Ckt | Y | 2023 | C GRD
65659 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223882338785 | 2023-08-21 | 1751 | 20230821 | 2127 | 2198617 | 216 | Transformer only | Environmental/External | Lightning | 2 | 432 | 38.724 | -120.6405 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1867774 | 0 | EPSS Ckt | N | 2023
65666 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 2023-08-23 | 1829 | 20230823 | 1838 | 2200596 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3676 | 33084 | 38.9144 | -121.0197 | No | Clear;32-90 F | Other | Broken | 23-0108297 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1868407 | 0 | EPSS Ckt | Y | 2023 | N/A
65684 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-08-27 | 1115 | 20230827 | 1344 | 2203318 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 48044 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 23-0109509 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1869329 | 0 | EPSS Ckt | Y | 2023 | B & C
65686 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-28 | 306 | 20230828 | 945 | 2203570 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 863 | 219450 | 38.643 | -120.6953 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869382 | 0 | EPSS Ckt | Y | 2023 | A+GRD
65686 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2023-08-28 | 306 | 20230828 | 945 | 2203570 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 863 | 219450 | 38.643 | -120.6953 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109591 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1869382 | 0 | EPSS Ckt | Y | 2023 | A+GRD
65716 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-09-02 | 1629 | 20230902 | 2347 | 2208817 | 438 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 936 | 136254 | 38.7391 | -120.6681 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112157 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1870971 | 0 | EPSS Ckt | Y | 2023 | AB
65718 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-09-03 | 504 | 20230903 | 625 | 2208980 | 81 | Distribution Circuit | Animal | Squirrel | 1873 | 151713 | 39.0997 | -121.05 | No | Overcast-Fog-Drizzle;32-90 F | Regulator | Normal | 23-0112203 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871014 | 0 | EPSS Ckt | Y | 2023 | BC
65723 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2023-09-04 | 1444 | 20230904 | 1643 | 2209468 | 119 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 936 | 111384 | 38.7391 | -120.6681 | No | Clear;32-90 F |  |  | 23-0112354 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1871133 | 0 | EPSS Ckt | Y | 2023 | BC
65755 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2023-09-12 | 741 | 20230912 | 1122 | 2216202 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3029 | 457097 | 38.7716 | -120.8148 | No | Clear;32-90 F |  |  | 23-0115321 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1873158 | 0 | EPSS Ckt | Y | 2023 | BC
65764 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | JUMPER | OJ 8 POLES N/OF CGC 223279856195 | 2023-09-13 | 1736 | 20230913 | 1924 | 2218208 | 108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 216 | 39.2059 | -120.8405 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0116288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1873780 | 0 | EPSS Ckt | N | 2023
65786 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | SWITCH | 10181 | 2023-09-18 | 2110 | 20230919 | 146 | 2222024 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 30912 | 38.8054 | -120.8181 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0117955 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1874979 | 0 | EPSS Ckt | N | 2023
65793 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223552240344 | 2023-09-19 | 1730 | 20230920 | 243 | 2222746 | 553 | Transformer only | Vegetation | Tree - fell into line | 1 | 553 | 38.7679 | -120.7549 | No | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0118480 | OH | Sus | 35490040 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | Yes | No | 1875321 | 0 | EPSS Ckt | N | 2023
65797 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2023-09-20 | 845 | 20230920 | 912 | 2223093 | 27 | Distribution Circuit | Company Initiated | Personnel- company | 570 | 15390 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0118616 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1875459 | 0 | EPSS Ckt | N | 2023 | NONE
65820 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | SWITCH | 6163 | 2023-09-25 | 1156 | 20230925 | 1313 | 2226601 | 77 | Distribution Circuit | Equipment Failure/Involved | Overhead | 201 | 15477 | 39.03 | -120.9656 | No | Clear;32-90 F | Other | Broken | 23-0120418 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876603 | 0 | EPSS Ckt | N | 2023
65822 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 2023-09-25 | 1628 | 20230925 | 1848 | 2226882 | 140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 18620 | 38.8063 | -120.925 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0120583 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1876670 | 0 | EPSS Ckt | N | 2023
65838 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30923 | 2023-09-27 | 1240 | 20230927 | 1410 | 2228615 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 450 | 38.8989 | -120.9485 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0121525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1877327 | 0 | EPSS Ckt | N | 2023
65852 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-09-29 | 1904 | 20230930 | 833 | 2230699 | 809 | Distribution Circuit | Company Initiated | Personnel- company | 203 | 164227 | 39.2562 | -120.7669 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0122758 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1877990 | 0 | EPSS Ckt | Y | 2023 | SGF
65857 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | T930513 | 2023-09-30 | 2138 | 20231001 | 1212 | 2231962 | 874 | Distribution Circuit | Equipment Failure/Involved | Underground | 1 | 874 | 39.1628 | -121.0017 | No | Partly Cloudy;32-90 F | Transformer (UG) | Failed/Faulted | 23-0123057 | UG | Sus | 45995740 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1878286 | 0 | EPSS Ckt | N | 2023
65860 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2023-10-01 | 1901 | 20231001 | 2005 | 2232280 | 64 | Distribution Circuit | Equipment Failure/Involved | Substation | 203 | 12992 | 39.2562 | -120.7669 | No | Overcast;32-90 F | Relay | Malfunctioning | 23-0123139 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1878373 | 0 | EPSS Ckt | Y | 2023 | SGF
65864 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S @ HARD TAP SS CGC 223112541295 | 2023-10-02 | 1448 | 20231003 | 147 | 2233273 | 659 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 3 | 1977 | 38.7959 | -120.9086 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0123550 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1878678 | 0 | EPSS Ckt | N | 2023
65874 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2023-10-04 | 1114 | 20231004 | 1323 | 2234568 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 11610 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0124213 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1879303 | 0 | EPSS Ckt | Y | 2023 | NA
65877 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 583518 | 2023-10-05 | 1033 | 20231005 | 1930 | 2235608 | 537 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 37 | 7584 | 39.3256 | -121.1123 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0124903 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | Yes | No | 1879651 | 0 | EPSS Ckt | Y | 2023 | A C
65880 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2023-10-05 | 1657 | 20231005 | 1902 | 2235960 | 125 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1873 | 79094 | 39.0997 | -121.05 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0125082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1879710 | 0 | EPSS Ckt | Y | 2023 | A & B
65894 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJS 2 SS OF CGC#223802036905 | 2023-10-09 | 831 | 20231009 | 1350 | 2238650 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1595 | 38.6728 | -120.6689 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0125947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1880464 | 0 | EPSS Ckt | N | 2023
65897 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | BURNED OJ HS OF FUCO 30815 | 2023-10-09 | 1339 | 20231009 | 2002 | 2239112 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1532 | 38.8868 | -120.8302 | No | Clear;32-90 F | Jumper | Burned Open | 23-0126225 | OH | Sus | 46004145 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1880686 | 0 | EPSS Ckt | N | 2023
65915 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222566060970 | 2023-10-14 | 1906 | 20231014 | 2018 | 2243537 | 72 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 216 | 39.338 | -121.0938 | No | Clear;32-90 F |  |  | 23-0128361 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1882212 | 0 | EPSS Ckt | N | 2023
65927 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 38097 | 2023-10-17 | 2308 | 20231018 | 226 | 2245753 | 198 | Distribution Circuit | Equipment Failure/Involved | Underground | 2 | 396 | 39.1837 | -120.9215 | No | Partly Cloudy;32-90 F | Transformer (UG) | Leaking | 23-0129378 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1882954 | 0 | EPSS Ckt | N | 2023
65929 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S 1 N/OF CGC 223546040325 | 2023-10-18 | 900 | 20231018 | 1220 | 2245961 | 200 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 4 | 800 | 38.7674 | -120.7571 | No | Clear;32-90 F | Pole-Wood | Normal | 23-0129488 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1883067 | 0 | EPSS Ckt | N | 2023
65930 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-10-19 | 805 | 20231019 | 1006 | 2246676 | 121 | Distribution Circuit | Animal | Bird found | 1042 | 84678 | 38.8154 | -120.8221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0130000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1883302 | 0 | EPSS Ckt | Y | 2023 | B C
65947 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 2023-10-23 | 2046 | 20231023 | 2230 | 2250224 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 520 | 38.5951 | -120.8115 | No | Clear;32-90 F |  |  | 23-0131602 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1884411 | 0 | EPSS Ckt | N | 2023
65955 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | FUSE | 30249 | 2023-10-25 | 1421 | 20231025 | 1849 | 2251735 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 7155 | 39.1757 | -120.9295 | No | Partly Cloudy-Drizzle;32-90 F |  |  | 23-0132553 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885023 | 0 | EPSS Ckt | N | 2023
65962 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH | 58420 | 2023-10-27 | 1002 | 20231027 | 1418 | 2253245 | 256 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 716 | 168456 | 38.8988 | -120.9106 | No | Clear;32-90 F |  |  | 23-0133185 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1885613 | 0 | EPSS Ckt | N | 2023
65965 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJ 1 SPAN SS OF CGC 223816439624 | 2023-10-28 | 756 | 20231028 | 1145 | 2253981 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | 38.7464 | -120.6635 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0133481 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1885762 | 0 | EPSS Ckt | N | 2023
65979 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222691561680 | 2023-10-30 | 1049 | 20231030 | 1209 | 2255365 | 80 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 160 | 39.3566 | -121.0481 | No | Clear;32-90 F |  |  | 23-0133980 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | None | 0 | No | No | No | 1886250 | 0 | EPSS Ckt | N | 2023
65993 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | SWITCH | 1818 | 2023-11-02 | 1038 | 20231102 | 1421 | 2258333 | 223 | Distribution Circuit | Equipment Failure/Involved | Underground | 80 | 5718 | 38.9853 | -120.8976 | No | Clear;32-90 F | Elbow | Failed/Faulted | 23-0134969 | UG | Sus | 46045468 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1887222 | 0 | EPSS Ckt | N | 2023
66015 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 9722 | 2023-11-06 | 1 | 20231106 | 1114 | 2260832 | 582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3557 | 669009 | 38.6412 | -120.6587 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0136081 | OH | Sus | 31675406 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1887962 | 0 | EPSS Ckt | Y | 2023 | SGF+DCD
66029 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2023-11-08 | 1714 | 20231108 | 2148 | 2264541 | 274 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 215913 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 23-0137255 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1889002 | 0 | EPSS Ckt | Y | 2023 | B-C
66052 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRIP-SAVER | 8233 | 2023-11-13 | 1509 | 20231113 | 1643 | 2268044 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 4538 | 39.3422 | -121.0615 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0138549 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Multi-Fault | 0 | No | No | No | 1890219 | 0 | EPSS Ckt | N | 2023 | AB
66055 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2023-11-13 | 2138 | 20231114 | 2 | 2268499 | 144 | Distribution Circuit | Animal | Bird found | 582 | 53057 | 38.9 | -120.9074 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0138623 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1890275 | 0 | EPSS Ckt | Y | 2023 | AB
66064 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2023-11-16 | 640 | 20231116 | 708 | 2270593 | 28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3053 | 76526 | 38.7716 | -120.8148 | No | Partly Cloudy-Fog-Drizzle;32-90 F |  |  | 23-0139750 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Three Phase Fault | 0 | No | No | No | 1890976 | 0 | EPSS Ckt | Y | 2023 | INST - A - B - C
66068 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6377 | 2023-11-16 | 1154 | 20231116 | 1221 | 2270837 | 27 | Distribution Circuit | Company Initiated | Other Circuits | 114 | 3078 | 39.2023 | -120.8368 | No | Overcast-Drizzle;32-90 F | Other | Normal | 23-0139933 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891060 | 0 | EPSS Ckt | N | 2023
66069 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 4437 | 2023-11-16 | 1154 | 20231116 | 1303 | 2270894 | 69 | Distribution Circuit | Company Initiated | Other Circuits | 1 | 69 | 39.2062 | -120.8381 | No | Partly Cloudy-Drizzle;32-90 F | Other | Normal | 23-0139974 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891077 | 0 | EPSS Ckt | N | 2023
66070 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 9593 | 2023-11-16 | 1330 | 20231116 | 1339 | 2270922 | 9 | Distribution Circuit | Company Initiated | Other Circuits | 59 | 531 | 39.2173 | -120.8092 | No | Partly Cloudy;32-90 F | Other | Normal | 23-0140018 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1891088 | 0 | EPSS Ckt | N | 2023
66076 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 2023-11-18 | 723 | 20231118 | 835 | 2272069 | 72 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 360 | 38.8986 | -120.8986 | No | Overcast-Fog-Rain;32-90 F |  |  | 23-0140797 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891513 | 0 | EPSS Ckt | N | 2023
66077 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223009955266 | 2023-11-18 | 1035 | 20231118 | 1456 | 2272418 | 261 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 522 | 39.1796 | -120.941 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0140861 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1891564 | 0 | EPSS Ckt | N | 2023
66119 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222596561680 | 2023-12-03 | 1017 | 20231203 | 1706 | 2282713 | 409 | Transformer only | Animal | Squirrel | 1 | 409 | 39.3572 | -121.0828 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0145027 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1894677 | 0 | EPSS Ckt | N | 2023
66129 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222987556615 | 2023-12-05 | 2129 | 20231206 | 312 | 2284722 | 343 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 343 | 39.2165 | -120.9469 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0145727 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1895432 | 0 | EPSS Ckt | N | 2023
66130 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ SS CGC 223241054370 | 2023-12-06 | 922 | 20231206 | 1106 | 2284964 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 416 | 39.1591 | -120.8602 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Bent or Twisted | 23-0145804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1895536 | 0 | EPSS Ckt | N | 2023
66166 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 889 | 2023-12-15 | 734 | 20231215 | 742 | 2292277 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 1136 | 39.3653 | -120.7935 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897999 | 0 | EPSS Ckt | N | 2023
66168 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | 811 | 2023-12-15 | 856 | 20231215 | 1446 | 2292355 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4900 | 39.4642 | -120.8458 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147519 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1898061 | 0 | EPSS Ckt | N | 2023
66169 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | FUSE | 31407 | 2023-12-15 | 904 | 20231215 | 1257 | 2292232 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2330 | 39.2779 | -120.9453 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0147525 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1897973 | 0 | EPSS Ckt | N | 2023
66206 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 18875 | 2023-12-25 | 1409 | 20231225 | 1525 | 2299494 | 76 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 86 | 6536 | 38.8221 | -120.8809 | No | Clear;32-90 F |  |  | 23-0148834 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1899905 | 0 | EPSS Ckt | N | 2023
66221 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223726036195 | 2024-01-02 | 53 | 20240102 | 403 | 2304450 | 190 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 190 | 38.6527 | -120.6969 | No | Clear;32-90 F | Connector or Splice (OH) | Burned Open | 24-0005849 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1900948 | 0 | EPSS Ckt | N | 2024
66223 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222685062240 | 2024-01-02 | 1213 | 20240103 | 331 | 2304857 | 918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2754 | 39.3724 | -121.0507 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0006118 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901091 | 0 | EPSS Ckt | N | 2024
66229 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 9593 | 2024-01-03 | 1004 | 20240103 | 1432 | s1901362 | 268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 12983 | 39.2173 | -120.8092 | No | Clear;32-90 F | Lightning Arrestor | Broken | 24-0006364 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1901362 | 0 | EPSS Ckt | N | 2024
66243 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223405056270 | 2024-01-08 | 1705 | 20240108 | 1718 | 2310133 | 13 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 35 | 39.2054 | -120.7994 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 24-0008110 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1902421 | 0 | EPSS Ckt | N | 2024
66248 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 2024-01-10 | 1851 | 20240110 | 2157 | 2312216 | 186 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 25854 | 38.895 | -120.9113 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0009295 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903069 | 0 | EPSS Ckt | N | 2024 | B C
66250 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2024-01-10 | 1956 | 20240110 | 2141 | 2312330 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1470 | 38.7941 | -120.8199 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0009339 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Line | 0 | No | No | No | 1903103 | 0 | EPSS Ckt | N | 2024
66275 | SIERRA | NEVADA | ALLEGHANY SUB | 15210 | OCB | 52G | 2024-01-16 | 1700 | 20240116 | 1709 | 2316854 | 9 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 1278 | 39.3638 | -120.7923 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Normal | 23-0128857 | OH | Sus | 31624660 | NORTH VALLEY AND SIERRA | JAN | None | 0 | No | No | No | 1904367 | 0 | Non-EPSS | N | 2024 | NA
66298 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223036355670 | 2024-01-22 | 1359 | 20240122 | 1454 | 2321517 | 55 | Transformer only | 3rd Party | Vehicle | 1 | 55 | 39.1904 | -120.9291 | No | Overcast-Fog;32-90 F | Fuse | Burned Open | 24-0013533 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1905616 | 0 | EPSS Ckt | N | 2024
66306 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222708761275 | 2024-01-24 | 1603 | 20240124 | 1700 | 2323367 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 114 | 39.3453 | -121.0428 | No | Overcast-Fog-Drizzle;32-90 F | Fuse | Broken | 24-0014678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Line to Ground | 0 | No | No | No | 1906114 | 0 | EPSS Ckt | N | 2024
66326 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5925 | 2024-01-30 | 1536 | 20240130 | 1652 | 2328452 | 76 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 456 | 39.0331 | -120.797 | No | Partly Cloudy;32-90 F | Insulator | Broken | 24-0016829 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JAN | Force Out | 0 | No | No | No | 1907570 | 0 | EPSS Ckt | N | 2024
66356 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223266742573 | 2024-02-02 | 609 | 20240202 | 1013 | 2332127 | 244 | Transformer only | Vegetation | Tree - fell into line | 1 | 244 | 38.8302 | -120.8543 | No | Overcast-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0018543 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1908590 | 0 | EPSS Ckt | N | 2024
66383 | SIERRA | NEVADA | HIGGINS-1110 | 152691110 | FUSE | 7709 | 2024-02-04 | 1447 | 20240206 | 1833 | 2365310 | 3106 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 71 | 220526 | 39.0742 | -121.007 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F |  |  | 24-0023639 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913043 | 0 | EPSS Ckt | N | 2024
66394 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 6303 | 2024-02-04 | 1500 | 20240204 | 1630 | 2342523 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 83 | 7470 | 39.0896 | -120.9657 | Yes | Overcast;32-90 F |  |  | 24-0020356 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910184 | 0 | EPSS Ckt | N | 2024
66445 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1374 | 2024-02-04 | 1557 | 20240209 | 1409 | 2345212 | 7092 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 3178058 | 39.0987 | -121.0518 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020370 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Multi-Fault | 0 | No | Yes | No | 1910198 | 0 | EPSS Ckt | N | 2024 | A B C TIME OC
66458 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 2024-02-04 | 1619 | 20240208 | 1612 | 2346047 | 5753 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 46024 | 38.9807 | -120.9404 | Yes | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022275 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1911928 | 0 | EPSS Ckt | N | 2024
66460 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 6053 | 2024-02-04 | 1624 | 20240206 | 1151 | 2346301 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 117820 | 38.84 | -120.8753 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910524 | 0 | EPSS Ckt | N | 2024
66486 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | JUMPER | OJ 3 SS OF CGC 222998054815 | 2024-02-04 | 1652 | 20240209 | 1228 | 2364739 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6936 | 39.1682 | -120.9427 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023493 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | Yes | No | 1912921 | 0 | EPSS Ckt | N | 2024
66512 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 33241 | 2024-02-04 | 1733 | 20240206 | 1823 | 2354271 | 2930 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 26370 | 39.1274 | -120.9453 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0021033 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1910856 | 0 | EPSS Ckt | N | 2024
66513 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | OJ AT CGC 222980153417 | 2024-02-04 | 1733 | 20240208 | 1548 | 2365514 | 5655 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 50895 | 39.1287 | -120.9504 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0023708 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1913100 | 0 | EPSS Ckt | N | 2024
66530 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 2024-02-04 | 1837 | 20240205 | 1332 | 2351159 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 30282 | 39.0098 | -120.8455 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Burned/flashed | 24-0021929 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1911661 | 1 | EPSS Ckt | N | 2024
66533 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 2024-02-04 | 1853 | 20240209 | 846 | 2351552 | 6593 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1165 | 3206443 | 39.3313 | -121.1015 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1910623 | 0 | EPSS Ckt | N | 2024 | B-C INST OC
66541 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 979598 | 2024-02-04 | 1911 | 20240205 | 1631 | 2352144 | 1280 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 225280 | 38.9133 | -120.9318 | Yes | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0020897 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1910717 | 0 | EPSS Ckt | N | 2024 | A LOCKOUT
66542 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2024-02-04 | 1915 | 20240205 | 2121 | 2357805 | 1566 | Distribution Circuit | Vegetation | Tree - fell into line | 998 | 1098510 | 38.8154 | -120.8221 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1911394 | 0 | EPSS Ckt | N | 2024 | C GRD
66557 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 38371 | 2024-02-04 | 1934 | 20240208 | 1146 | 2352829 | 5292 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 127008 | 39.4746 | -121.033 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Together | 24-0023303 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1912789 | 0 | EPSS Ckt | N | 2024
66598 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222991058975 | 2024-02-05 | 714 | 20240206 | 1705 | 2357396 | 2031 | Transformer only | Vegetation | Tree - fell into line | 4 | 8124 | 39.2815 | -120.9447 | No | Overcast-Fog;32-90 F | Service conductor | Broken- wire on ground | 24-0023652 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1913061 | 0 | EPSS Ckt | N | 2024
66614 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31013 | 2024-02-05 | 1633 | 20240208 | 1236 | 2361034 | 4083 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4083 | 38.911 | -120.9312 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022395 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | Yes | No | 1912048 | 0 | EPSS Ckt | N | 2024
66622 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2024-02-05 | 1821 | 20240206 | 1140 | 2361657 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1726 | 148248 | 38.643 | -120.6953 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912220 | 0 | EPSS Ckt | N | 2024 | A GRD
66622 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 2024-02-05 | 1821 | 20240206 | 1140 | 2361657 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1726 | 148248 | 38.643 | -120.6953 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022592 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | Yes | No | 1912220 | 0 | EPSS Ckt | N | 2024 | A GRD
66650 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 8229 | 2024-02-06 | 2033 | 20240208 | 1908 | 2365575 | 2795 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16770 | 39.3753 | -121.0378 | No | Clear;32-90 F | Insulator | Broken | 24-0023876 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1913247 | 0 | EPSS Ckt | N | 2024
66682 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 2024-02-10 | 911 | 20240210 | 1208 | 2372543 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 1416 | 38.9807 | -120.9404 | No | Clear;32-90 F |  |  | 24-0027375 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1915841 | 0 | EPSS Ckt | N | 2024
66686 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 2024-02-11 | 1605 | 20240211 | 1728 | 2373406 | 83 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 14774 | 38.7138 | -120.6231 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0027643 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1916063 | 0 | EPSS Ckt | N | 2024
66690 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 41345 | 2024-02-13 | 1513 | 20240214 | 1114 | 2375478 | 1201 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1201 | 39.0118 | -120.8419 | No | Clear;32-90 F | Transformer (UG) | Normal | 24-0028604 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1916639 | 0 | EPSS Ckt | N | 2024
66692 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER | 222560861010 | 2024-02-13 | 2307 | 20240214 | 449 | 2375726 | 342 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 342 | 39.339 | -121.0954 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0028636 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1916667 | 0 | EPSS Ckt | N | 2024
66703 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 6043 | 2024-02-16 | 834 | 20240216 | 1537 | 2378058 | 423 | Distribution Circuit | Company Initiated | Personnel- company | 77 | 32487 | 38.9764 | -120.8906 | No | Partly Cloudy;32-90 F |  |  | 24-0004995 | OH | Sus | 35496650 | NORTH VALLEY AND SIERRA | FEB | None | 0 | No | No | No | 1917329 | 0 | EPSS Ckt | N | 2024
66728 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | TRANSFORMER | 223074646760 | 2024-02-19 | 853 | 20240219 | 1256 | 2380542 | 243 | Transformer only | Environmental/External | Lightning | 1 | 243 | 38.9455 | -120.9205 | No | Partly Cloudy-Fog-Drizzle;32-90 F | Transformer | Failed/Faulted | 24-0030761 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1917972 | 0 | EPSS Ckt | N | 2024
66734 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223198042725 | 2024-02-19 | 1309 | 20240219 | 1812 | 2381346 | 303 | Transformer only | Environmental/External | Lightning | 2 | 606 | 38.8345 | -120.8793 | No | Overcast-Strong Winds;32-90 F | Transformer (OH) | Failed/Faulted | 24-0030925 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918088 | 0 | EPSS Ckt | N | 2024
66738 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 222999453483 | 2024-02-19 | 1638 | 20240220 | 1119 | 2381887 | 1121 | Transformer only | Environmental/External | Lightning | 1 | 1121 | 39.13 | -120.9435 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0031055 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918172 | 0 | EPSS Ckt | N | 2024
66748 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 10735 | 2024-02-20 | 1748 | 20240220 | 2000 | 2383321 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 5412 | 38.7023 | -120.7619 | No | Overcast-Fog-Lightning;32-90 F |  |  | 24-0031675 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Line | 0 | No | No | No | 1918510 | 0 | EPSS Ckt | N | 2024
66751 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223527537865 | 2024-02-20 | 2032 | 20240221 | 1204 | 2383409 | 932 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1864 | 38.6998 | -120.7649 | No | Rain-Overcast-Fog;32-90 F | Transformer | Failed/Faulted | 24-0031690 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Line to Ground | 0 | No | No | No | 1918519 | 0 | EPSS Ckt | N | 2024
66760 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 2024-02-22 | 1129 | 20240222 | 1626 | 2385238 | 297 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1167 | 8748 | 39.3313 | -121.1015 | No | Clear;32-90 F | Insulator | Failed/Faulted | 24-0032569 | OH | Sus | 31684854 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1919154 | 0 | EPSS Ckt | N | 2024 | NONE
66772 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | JUMPER | S SPANS N/E OF CGC 223241054370 | 2024-02-26 | 915 | 20240226 | 1152 | 2387820 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 628 | 39.1596 | -120.8586 | No | Overcast-Fog;32-90 F | Pole-Wood | Deteriorated | 24-0033737 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | FEB | Force Out | 0 | No | No | No | 1920029 | 0 | EPSS Ckt | N | 2024
66804 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1491 | 2024-03-01 | 1723 | 20240301 | 1906 | 2392590 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1442 | 38.7941 | -120.8199 | Yes | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0036415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921461 | 0 | EPSS Ckt | N | 2024
66814 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2024-03-01 | 1906 | 20240304 | 1738 | 2392923 | 4232 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 317040 | 39.2562 | -120.7669 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036410 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1921454 | 0 | EPSS Ckt | N | 2024 | B+C+GRD
66820 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1249 | 2024-03-01 | 2001 | 20240302 | 1115 | 2393315 | 914 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 31076 | 38.8114 | -120.8047 | Yes | Snow;Below 32 F | Conductor- Overhead | Together | 24-0036785 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1921808 | 0 | EPSS Ckt | N | 2024
66826 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 6973 | 2024-03-01 | 2124 | 20240302 | 1616 | 2393632 | 1132 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 35420 | 39.3385 | -121.0579 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036558 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921599 | 0 | EPSS Ckt | N | 2024
66834 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | RECLOSER | 86696 | 2024-03-01 | 2149 | 20240302 | 1309 | 2393692 | 920 | Distribution Circuit | Vegetation | Tree - fell into line | 770 | 700907 | 39.1827 | -120.8571 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036608 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | Yes | No | 1921649 | 0 | EPSS Ckt | N | 2024 | B OC
66835 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 6375 | 2024-03-01 | 2149 | 20240303 | 1601 | 2394698 | 2532 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 218340 | 39.2011 | -120.836 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken | 24-0036831 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | None | 0 | No | No | No | 1921841 | 0 | EPSS Ckt | N | 2024
66836 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 57223 | 2024-03-01 | 2149 | 20240303 | 1230 | 2394950 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9284 | 39.2092 | -120.8186 | Yes | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036924 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1921903 | 0 | EPSS Ckt | N | 2024
66883 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 32361 | 2024-03-03 | 1934 | 20240304 | 1205 | 2396384 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10901 | 38.8791 | -120.8335 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0037325 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1922231 | 0 | EPSS Ckt | N | 2024
66884 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5811 | 2024-03-03 | 1937 | 20240303 | 2201 | 2396334 | 144 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 15 | 2206 | 38.8819 | -120.8303 | No | Overcast-Fog-Drizzle;32-90 F |  |  | 24-0037324 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1922230 | 1 | EPSS Ckt | N | 2024
66889 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 30145 | 2024-03-04 | 1337 | 20240304 | 1642 | 2396882 | 185 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 1665 | 39.1623 | -120.8618 | No | Partly Cloudy;32-90 F |  |  | 24-0037734 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1922354 | 0 | EPSS Ckt | N | 2024
66908 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2024-03-07 | 1234 | 20240307 | 1316 | 2399405 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 6502 | 39.4655 | -120.8443 | No | Clear;32-90 F | Insulator | Broken | 24-0039082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923280 | 0 | EPSS Ckt | N | 2024 | NONE
66908 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 2024-03-07 | 1234 | 20240307 | 1316 | 2399405 | 42 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 6502 | 39.4655 | -120.8443 | No | Clear;32-90 F | Insulator | Broken | 24-0039082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1923280 | 0 | EPSS Ckt | N | 2024 | NONE
66936 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2024-03-14 | 810 | 20240314 | 1433 | 2404312 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 3052 | 386692 | 38.7716 | -120.8148 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0041878 | OH | Sus | 46211570 | NORTH VALLEY AND SIERRA | MAR | Multi-Fault | 0 | No | Yes | No | 1924901 | 0 | EPSS Ckt | N | 2024 | A B C GRD & TIME OC
66938 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 2024-03-14 | 953 | 20240314 | 1123 | 2404629 | 90 | Distribution Circuit | Vegetation | Tree - branch fell on line | 262 | 23580 | 39.3676 | -121.0458 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0041976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925033 | 0 | EPSS Ckt | N | 2024 | A-B TIME OC
66949 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 37335 | 2024-03-15 | 857 | 20240315 | 1655 | 2405967 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3824 | 39.1743 | -120.8299 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0042762 | OH | Sus | 31686654 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | Yes | No | 1925550 | 0 | EPSS Ckt | N | 2024
66954 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | TRANSFORMER | 223943037719 | 2024-03-15 | 1401 | 20240316 | 1759 | 2406640 | 1678 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 2920 | 38.6947 | -120.6196 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043061 | OH | Sus | 35537933 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1925699 | 0 | EPSS Ckt | N | 2024
66955 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20521 | 2024-03-15 | 1425 | 20240315 | 1806 | 2406690 | 221 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 1326 | 38.6497 | -120.676 | No | Clear;32-90 F |  |  | 24-0043004 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925648 | 0 | EPSS Ckt | N | 2024
66958 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | FUSE | 31173 | 2024-03-16 | 1535 | 20240316 | 2315 | 2407362 | 460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4025 | 39.1905 | -120.809 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0043164 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925827 | 0 | EPSS Ckt | N | 2024
66963 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 30719 | 2024-03-17 | 1113 | 20240317 | 1258 | 2407724 | 105 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 2310 | 39.3701 | -121.1017 | No | Clear;32-90 F |  |  | 24-0043253 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1925939 | 0 | EPSS Ckt | N | 2024
66972 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 31133 | 2024-03-18 | 2047 | 20240318 | 2310 | 2408854 | 143 | Distribution Circuit | Animal | Bird found | 2 | 286 | 38.8304 | -120.8781 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043838 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1926417 | 0 | EPSS Ckt | N | 2024
66985 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | SWITCH | 645945 | 2024-03-22 | 1026 | 20240322 | 1149 | 2411877 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 3154 | 38.609 | -120.8441 | No | Partly Cloudy;32-90 F | Connector or Splice (OH) | Deteriorated | 24-0045449 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1927472 | 0 | EPSS Ckt | N | 2024
66994 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12641 | 2024-03-22 | 2126 | 20240323 | 46 | 2412427 | 200 | Distribution Circuit | Environmental/External | Lightning | 78 | 15600 | 38.7941 | -120.7143 | No | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0045882 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1927618 | 0 | EPSS Ckt | N | 2024
66996 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 20793 | 2024-03-22 | 2208 | 20240323 | 905 | 2412449 | 657 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 10512 | 38.6546 | -120.644 | No | Overcast-Fog-Rain-Lightning;32-90 F | Fuse | Failed/Faulted | 24-0045947 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Line | 0 | No | No | No | 1927698 | 0 | EPSS Ckt | N | 2024
67011 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223077855897 | 2024-03-26 | 1003 | 20240326 | 1518 | 2415515 | 315 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 315 | 39.1965 | -120.9148 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0046930 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Line to Ground | 0 | No | No | No | 1928494 | 0 | EPSS Ckt | N | 2024
67014 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S @ FLYING BELLS 1/N/OF 21065 | 2024-03-26 | 1325 | 20240326 | 1509 | 2415725 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 227 | 10674 | 38.7713 | -120.7704 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Deteriorated | 24-0046901 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1928519 | 0 | EPSS Ckt | N | 2024
67040 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S 3 SPANS SS OF 223138542610 | 2024-03-29 | 1033 | 20240329 | 1138 | 2417996 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 65 | 38.8324 | -120.8959 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0048320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929381 | 0 | EPSS Ckt | N | 2024
67040 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | OJ'S 3 SPANS SS OF 223138542610 | 2024-03-29 | 1033 | 20240329 | 1138 | 2417996 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 65 | 38.8324 | -120.8959 | No | Overcast;32-90 F | Conductor- Overhead | Broken | 24-0048320 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAR | Force Out | 0 | No | No | No | 1929381 | 0 | EPSS Ckt | N | 2024
67049 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12567 | 2024-04-01 | 1313 | 20240401 | 1450 | 2420286 | 97 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 97 | 38.6403 | -120.6541 | No | Clear;32-90 F |  |  | 24-0049304 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1930007 | 0 | EPSS Ckt | N | 2024
67058 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223019755236 | 2024-04-03 | 835 | 20240403 | 957 | 2421581 | 82 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 82 | 39.1783 | -120.9356 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0050059 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1930495 | 0 | EPSS Ckt | N | 2024
67076 | SIERRA | EL DORADO | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20255 | 2024-04-06 | 1738 | 20240406 | 2003 | 2425418 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 33350 | 38.6208 | -120.8489 | No | Overcast;32-90 F |  |  | 24-0051824 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1931568 | 0 | EPSS Ckt | N | 2024
67122 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 2024-04-19 | 2002 | 20240419 | 2146 | 2435274 | 104 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 5928 | 38.9142 | -120.9386 | No | Clear;32-90 F |  |  | 24-0057082 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Line | 0 | No | No | No | 1935084 | 0 | EPSS Ckt | N | 2024
67128 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | OTHER | HOT WIRE DOWN 16882 YOU BET RD | 2024-04-21 | 1206 | 20240421 | 1609 | 2435860 | 243 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 172 | 13380 | 39.1905 | -120.9368 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0057314 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Line to Ground | 0 | No | Yes | Yes | 1935322 | 0 | EPSS Ckt | N | 2024
67137 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | JUMPER | OJ 1 E/OF MTR# 1005205910 | 2024-04-23 | 1032 | 20240423 | 1355 | 2437284 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 406 | 38.7324 | -120.6613 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0057900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1935766 | 0 | EPSS Ckt | N | 2024
67140 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2024-04-24 | 1847 | 20240425 | 132 | 2438417 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 938 | 23775 | 38.7391 | -120.6681 | No | Overcast;32-90 F | Crossarm- Wood | Broken | 24-0058687 | OH | Sus | 31692140 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1936196 | 0 | EPSS Ckt | N | 2024 | N/A
67141 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 2024-04-24 | 2301 | 20240425 | 220 | 2438551 | 181 | Distribution Circuit | Animal | Other | 3692 | 165097 | 38.9144 | -121.0197 | No | Partly Cloudy;32-90 F | Recloser | Normal | 24-0058715 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Multi-Fault | 0 | No | No | No | 1936223 | 0 | EPSS Ckt | N | 2024 | A-C- GRD
67156 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 18793 | 2024-04-30 | 1031 | 20240430 | 1317 | s1937745 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1660 | 38.6472 | -120.6835 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0060511 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | APR | Force Out | 0 | No | No | No | 1937745 | 0 | EPSS Ckt | N | 2024
67163 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223802636713 | 2024-05-01 | 2200 | 20240502 | 324 | 2443823 | 324 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1296 | 38.6703 | -120.6692 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0061119 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1938137 | 0 | EPSS Ckt | N | 2024
67168 | SIERRA | NEVADA | ALLEGHANY SUB | 15210 | OCB | 52G | 2024-05-02 | 1700 | 20240502 | 1706 | 2444508 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 142 | 852 | 39.3638 | -120.7923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0010940 | OH | Sus | 31624660 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1938421 | 0 | Non-EPSS | N | 2024 | NONE
67210 | SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1435 | 2024-05-09 | 1145 | 20240509 | 1357 | 2449844 | 132 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2640 | 38.7507 | -120.7582 | No | Clear;32-90 F |  |  | 24-0064285 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1940429 | 0 | EPSS Ckt | N | 2024
67216 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 3451 | 2024-05-10 | 1729 | 20240510 | 2000 | 2451130 | 151 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 1057 | 39.211 | -120.8206 | No | Clear;32-90 F |  |  | 24-0064879 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1940786 | 1 | EPSS Ckt | N | 2024
67233 | SIERRA | PLACER | WEIMAR-1101 | 152491101 | FUSE | 30485 | 2024-05-13 | 839 | 20240513 | 1008 | 2452427 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 2403 | 39.0391 | -120.9399 | No | Clear;32-90 F |  |  | 24-0065350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1941261 | 0 | EPSS Ckt | N | 2024
67235 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER | OJ AT CGC 223082045872 | 2024-05-13 | 1434 | 20240513 | 1611 | 2452714 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 776 | 38.9225 | -120.9175 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0065415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1941313 | 0 | EPSS Ckt | N | 2024
67246 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31025 | 2024-05-16 | 1229 | 20240516 | 1356 | 2460684 | 87 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 870 | 38.9005 | -120.9155 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0066837 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942088 | 0 | EPSS Ckt | N | 2024
67259 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 1249 | 2024-05-19 | 1040 | 20240519 | 1513 | 2462553 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 5026 | 38.8114 | -120.8047 | No | Clear;32-90 F |  |  | 24-0067629 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Line | 0 | No | No | No | 1942664 | 0 | EPSS Ckt | N | 2024
67264 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223033956461 | 2024-05-20 | 1238 | 20240520 | 1319 | 2463317 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 39.2101 | -120.9291 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0067920 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1942925 | 0 | EPSS Ckt | N | 2024
67277 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | 223313055681 | 2024-05-22 | 923 | 20240522 | 1307 | 2464976 | 224 | Transformer only | Unknown Cause | Patrol - found nothing | 5 | 1120 | 39.1896 | -120.8316 | No | Clear;32-90 F |  |  | 24-0061791 | OH | Sus | 35468820 | NORTH VALLEY AND SIERRA | MAY | None | 0 | No | No | No | 1943460 | 0 | EPSS Ckt | N | 2024
67292 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 2024-05-24 | 1325 | 20240524 | 2115 | 2466695 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 17570 | 39.0896 | -120.9657 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0069863 | OH | Sus | 31695146 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | Yes | No | 1944092 | 0 | EPSS Ckt | N | 2024
67307 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223031055584 | 2024-05-29 | 1518 | 20240529 | 1636 | 2470077 | 78 | Transformer only | Animal | Bird found | 1 | 78 | 39.188 | -120.9315 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0071095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945003 | 0 | EPSS Ckt | N | 2024
67307 | SIERRA | NEVADA | BRUNSWICK-1106 | 152481106 | TRANSFORMER | 223031055584 | 2024-05-29 | 1518 | 20240529 | 1636 | 2470077 | 78 | Transformer only | Animal | Bird found | 1 | 78 | 39.188 | -120.9315 | No | Clear;32-90 F | Fuse | Failed/Faulted | 24-0071095 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945003 | 0 | EPSS Ckt | N | 2024
67310 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223268165885 | 2024-05-30 | 1034 | 20240530 | 1140 | 2470812 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 330 | 39.47 | -120.8434 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945297 | 0 | EPSS Ckt | N | 2024
67310 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223268165885 | 2024-05-30 | 1034 | 20240530 | 1140 | 2470812 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 330 | 39.47 | -120.8434 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071446 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Line to Ground | 0 | No | No | No | 1945297 | 0 | EPSS Ckt | N | 2024
67312 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223267065870 | 2024-05-30 | 1140 | 20240530 | 1805 | 2470914 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1540 | 39.4696 | -120.8435 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1945281 | 0 | EPSS Ckt | N | 2024
67312 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | TRANSFORMER | 223267065870 | 2024-05-30 | 1140 | 20240530 | 1805 | 2470914 | 385 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 1540 | 39.4696 | -120.8435 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071412 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Force Out | 0 | No | No | No | 1945281 | 0 | EPSS Ckt | N | 2024
67314 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 2024-05-31 | 1306 | 20240531 | 1419 | 2471863 | 73 | Distribution Circuit | Animal | Bird found | 3692 | 269516 | 38.9144 | -121.0197 | No | Clear;32-90 F | Recloser | Normal | 24-0071940 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | MAY | Multi-Fault | 0 | No | No | No | 1945600 | 0 | EPSS Ckt | Y | 2024 | A-C- GRD
67349 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | FUSE | 30337 | 2024-06-07 | 400 | 20240607 | 638 | 2478833 | 158 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 948 | 39.095 | -121.054 | No | Clear;32-90 F |  |  | 24-0074498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1947406 | 0 | EPSS Ckt | N | 2024
67351 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2024-06-07 | 1056 | 20240607 | 1524 | 2479186 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 244727 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0074644 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1947538 | 0 | EPSS Ckt | Y | 2024 | B GRD
67361 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 2024-06-09 | 2245 | 20240610 | 327 | 2480703 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1410 | 39.3404 | -121.1319 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0075175 | OH | Sus | 31696721 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1947919 | 0 | EPSS Ckt | N | 2024 | N/A
67379 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 2024-06-13 | 2251 | 20240614 | 253 | 2485059 | 242 | Distribution Circuit | 3rd Party | Vehicle | 3941 | 698622 | 38.7934 | -120.62 | No | Clear;32-90 F | Anchor or Guy | Broken | 24-0076946 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1949193 | 0 | EPSS Ckt | Y | 2024 | AC- INST OC- SET A RLY
67381 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | OJ'S @ LINE AND BUCK OFF HARD TAP | 2024-06-14 | 1222 | 20240614 | 1330 | 2485529 | 68 | Distribution Circuit | 3rd Party | Vehicle | 3 | 204 | 38.6969 | -120.7617 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0077135 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | Yes | No | 1949394 | 0 | EPSS Ckt | N | 2024
67387 | SIERRA | PLACER | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 2024-06-16 | 743 | 20240616 | 1237 | 2486890 | 294 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 60010 | 39.2562 | -120.7669 | No | Clear;Above 90 |  |  | 24-0077457 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Multi-Fault | 0 | No | No | No | 1949617 | 0 | EPSS Ckt | Y | 2024 | A-B GRD
67397 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 2024-06-18 | 1214 | 20240618 | 1332 | 2489318 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 624 | 38.9807 | -120.9404 | No | Clear;32-90 F | Insulator | Broken | 24-0078152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950241 | 0 | EPSS Ckt | N | 2024
67400 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 2024-06-18 | 2043 | 20240619 | 1442 | 2489642 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 938 | 883411 | 38.7391 | -120.6681 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0078318 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | Yes | No | 1950306 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
67404 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | JUMPER | OJ'S SS OF CGC 223311555726 | 2024-06-19 | 956 | 20240619 | 1248 | 2489897 | 172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 172 | 39.1906 | -120.8315 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0078415 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950417 | 0 | EPSS Ckt | N | 2024
67405 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ'S 4 SPANS SS OF CGC 222445360625 | 2024-06-19 | 1004 | 20240619 | 1112 | 2489970 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 68 | 39.3259 | -121.1386 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0078429 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Force Out | 0 | No | No | No | 1950435 | 0 | EPSS Ckt | N | 2024
67422 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | TRANSFORMER | 223166441174 | 2024-06-22 | 1207 | 20240622 | 1420 | 2492436 | 133 | Transformer only | 3rd Party | Vehicle | 1 | 133 | 38.7918 | -120.89 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0079419 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1951064 | 0 | EPSS Ckt | N | 2024
67447 | SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | OCB | 1103/2 | 2024-06-27 | 23 | 20240627 | 734 | 2497263 | 431 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1301 | 313393 | 38.7393 | -120.6773 | No | Clear;32-90 F |  |  | 24-0081117 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1952327 | 0 | EPSS Ckt | Y | 2024 | A- GRD PH INST OC
67450 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223788235985 | 2024-06-27 | 1309 | 20240627 | 2108 | 2497765 | 479 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 479 | 38.6474 | -120.6748 | No | Clear;32-90 F | Bushing | Burned/flashed | 24-0081445 | OH | Sus | 46269506 | NORTH VALLEY AND SIERRA | JUN | Line to Ground | 0 | No | No | No | 1952534 | 0 | EPSS Ckt | N | 2024
67452 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2024-06-27 | 1648 | 20240627 | 1952 | 2497906 | 171 | Distribution Circuit | Vegetation | Tree - fell into line | 1042 | 91986 | 38.8154 | -120.8221 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0081498 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUN | Line to Line | 0 | No | No | No | 1952549 | 0 | EPSS Ckt | Y | 2024 | A-B
67488 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 2024-07-03 | 1850 | 20240704 | 159 | 2504266 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 233 | 42653 | 38.8435 | -120.8737 | No | Clear-Heat Wave;Above 90 | Transformer (OH) | Broken | 24-0083798 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1953994 | 0 | EPSS Ckt | Y | 2024 | C- GRD
67598 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 8971 | 2024-07-17 | 2051 | 20240717 | 2202 | 2519914 | 71 | Distribution Circuit | Animal | Bird found | 54 | 3834 | 38.6756 | -120.6646 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0089104 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1957578 | 0 | EPSS Ckt | N | 2024
67615 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 11321 | 2024-07-20 | 949 | 20240720 | 1446 | 2521685 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3267 | 38.7054 | -120.7628 | No | Clear;32-90 F | Conductor- Overhead | Bent or Twisted | 24-0090033 | OH | Sus | 46282483 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958121 | 0 | EPSS Ckt | N | 2024
67618 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2024-07-20 | 1828 | 20240720 | 2019 | 2522038 | 111 | Distribution Circuit | Animal | Bird found | 1878 | 131108 | 39.0997 | -121.05 | No | Clear;Above 90 | Insulator | Normal | 24-0090080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958157 | 0 | EPSS Ckt | Y | 2024 | A C INSTA OC
67621 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2024-07-21 | 613 | 20240721 | 1321 | 2522266 | 428 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1042 | 445976 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0090132 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Line | 0 | No | No | No | 1958207 | 0 | EPSS Ckt | Y | 2024 | B C
67649 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | TRANSFORMER | T244 | 2024-07-24 | 936 | 20240724 | 1230 | 2525493 | 174 | Transformer only | Company Initiated | Personnel- company | 2 | 348 | 39.1873 | -120.8335 | No | Heat Wave-Clear;Above 90 | Transformer | Malfunctioning | 24-0091425 | UG | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Line to Ground | 0 | No | No | No | 1959149 | 0 | EPSS Ckt | N | 2024
67652 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S @ MTR# 1010656108 | 2024-07-24 | 944 | 20240724 | 1306 | 2525412 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 606 | 38.8471 | -120.7877 | No | Clear-Heat Wave;32-90 F | Pole-Wood | Broken | 24-0091350 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959080 | 0 | EPSS Ckt | N | 2024
67654 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | SWITCH | 8843 | 2024-07-24 | 1242 | 20240724 | 1411 | 2525761 | 89 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 9078 | 39.2028 | -120.7963 | No | Clear-Heat Wave;Above 90 | Connector or Splice (OH) | Broken | 24-0091482 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | Force Out | 0 | No | No | No | 1959167 | 0 | EPSS Ckt | N | 2024
67666 | SIERRA | NEVADA | BRUNSWICK-1105 | 152481105 | SWITCH | 2751 | 2024-07-25 | 2014 | 20240725 | 2237 | 2527014 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 9724 | 39.2809 | -120.9453 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0091900 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | JUL | None | 0 | No | No | No | 1959571 | 0 | EPSS Ckt | N | 2024
67709 | SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 2024-08-05 | 922 | 20240805 | 1024 | 2534801 | 62 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 1612 | 39.4382 | -120.9965 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0095747 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962047 | 0 | EPSS Ckt | Y | 2024 | NA
67715 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 2024-08-06 | 957 | 20240806 | 1311 | 2535736 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1076 | 208744 | 39.4655 | -120.8444 | No | Clear;32-90 F |  |  | 24-0096267 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962365 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
67715 | SIERRA | NEVADA | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 2024-08-06 | 957 | 20240806 | 1311 | 2535736 | 194 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1076 | 208744 | 39.4655 | -120.8444 | No | Clear;32-90 F |  |  | 24-0096267 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1962365 | 0 | EPSS Ckt | Y | 2024 | SGF-DCD
67723 | SIERRA | PLACER | SHADY GLEN-1101 | 152431101 | SWITCH | 6305 | 2024-08-07 | 1725 | 20240807 | 2018 | 2537026 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3633 | 39.0899 | -120.98 | No | Clear;Above 90 | Crossarm- Wood | Broken | 24-0096951 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1962787 | 0 | EPSS Ckt | N | 2024
67743 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 2024-08-10 | 2025 | 20240810 | 2212 | 2539607 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 9309 | 39.3405 | -121.1318 | No | Clear;32-90 F |  |  | 24-0098034 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Multi-Fault | 0 | No | No | No | 1963493 | 0 | EPSS Ckt | Y | 2024 | A-C- INST OC
67757 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 406999 | 2024-08-14 | 1751 | 20240814 | 1841 | 2542366 | 50 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 3835 | 39.0016 | -120.9074 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 24-0099500 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | None | 0 | No | No | No | 1964445 | 1 | EPSS Ckt | Y | 2024
67784 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S @ CGC 223819738702 | 2024-08-19 | 1356 | 20240819 | 1551 | 2545743 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 115 | 38.7222 | -120.662 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0100733 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1965353 | 0 | EPSS Ckt | N | 2024
67785 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 223020556505 | 2024-08-19 | 1646 | 20240819 | 1935 | 2545774 | 169 | Transformer only | Company Initiated | Personnel- company | 1 | 169 | 39.213 | -120.9345 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100804 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1965378 | 0 | EPSS Ckt | N | 2024
67807 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 2024-08-24 | 910 | 20240824 | 1255 | 2550026 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 16277 | 38.895 | -120.9113 | No | Overcast;32-90 F | Lightning Arrestor | Burned/flashed | 24-0102731 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Ground | 0 | No | No | No | 1966685 | 0 | EPSS Ckt | Y | 2024 | A GRD
67826 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 2024-08-28 | 1605 | 20240829 | 200 | 2554154 | 595 | Distribution Circuit | 3rd Party | Vehicle | 4977 | 535179 | 38.7394 | -120.6774 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0104336 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Line to Line | 0 | No | No | No | 1967926 | 0 | EPSS Ckt | Y | 2024 | PH INST OC
67834 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | TRANSFORMER | 223830036785 | 2024-08-30 | 1004 | 20240830 | 1045 | 2555835 | 41 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 158 | 38.6686 | -120.6603 | No | Clear;32-90 F | Insulator | Broken | 24-0105211 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | AUG | Force Out | 0 | No | No | No | 1968492 | 0 | EPSS Ckt | N | 2024
67847 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 674140 | 2024-09-03 | 1015 | 20240903 | 1152 | 2558199 | 97 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1261 | 38.9015 | -120.9036 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0105941 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1969058 | 0 | EPSS Ckt | N | 2024 | N/A
67853 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 35424 | 2024-09-03 | 2002 | 20240904 | 1409 | 2558757 | 1087 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 39550 | 39.3432 | -121.1213 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0106423 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1969178 | 0 | EPSS Ckt | Y | 2024 | A C
67869 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 810550 | 2024-09-05 | 1245 | 20240905 | 1259 | 2560323 | 14 | Distribution Circuit | Company Initiated | Personnel- company | 23 | 322 | 38.6733 | -120.6967 | No | Clear;Above 90 | Conductor- Overhead | Normal | 24-0107340 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | No | No | 1969764 | 0 | EPSS Ckt | Y | 2024 | A & B
67877 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 2024-09-06 | 1537 | 20240906 | 1915 | 2561438 | 218 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2500 | 212476 | 38.7393 | -120.6773 | No | Clear;Above 90 |  |  | 24-0108083 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1970130 | 0 | EPSS Ckt | Y | 2024 | a
67878 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223793639402 | 2024-09-06 | 2235 | 20240906 | 2244 | 2561614 | 9 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 36 | 38.7407 | -120.6714 | No | Clear;32-90 F |  |  | 24-0108152 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1970172 | 0 | EPSS Ckt | N | 2024
67883 | SIERRA | NEVADA | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 2024-09-07 | 1843 | 20240908 | 1753 | 2562184 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 36140 | 39.4382 | -120.9965 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0108301 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Line | 0 | No | Yes | No | 1970314 | 0 | EPSS Ckt | Y | 2024 | B-C INST OC
67931 | SIERRA | PLACER | SHADY GLEN-1102 | 152431102 | TRANSFORMER | 223243455393 | 2024-09-18 | 925 | 20240918 | 1057 | 2571488 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 828 | 39.1824 | -120.8568 | No | Overcast;32-90 F | Insulator | Broken | 24-0112353 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1973213 | 0 | EPSS Ckt | N | 2024
67940 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | JUMPER | 449475 | 2024-09-19 | 916 | 20240919 | 1612 | 2572558 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7473 | 38.696 | -120.6069 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0113065 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | Yes | Yes | 1973559 | 0 | EPSS Ckt | N | 2024
67940 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | JUMPER | 449475 | 2024-09-19 | 916 | 20240919 | 1612 | 2572558 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7473 | 38.696 | -120.6069 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0113065 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Open Circuit | 0 | No | Yes | Yes | 1973559 | 0 | EPSS Ckt | N | 2024
67950 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | TRANSFORMER | 222961856817 | 2024-09-21 | 1950 | 20240921 | 2116 | 2574257 | 86 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 86 | 39.2221 | -120.9557 | No | Clear;32-90 F |  |  | 24-0114080 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | None | 0 | No | No | No | 1974142 | 0 | EPSS Ckt | N | 2024
67961 | SIERRA | NEVADA | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 2024-09-24 | 1653 | 20240924 | 1822 | 2576720 | 89 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1878 | 111966 | 39.0997 | -121.05 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0115114 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Line to Ground | 0 | No | No | No | 1974974 | 0 | EPSS Ckt | Y | 2024 | B PHASE
67969 | SIERRA | EL DORADO | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 21797 | 2024-09-25 | 1706 | 20240925 | 1916 | 2577721 | 130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 390 | 38.7935 | -120.912 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0115678 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | SEP | Force Out | 0 | No | No | No | 1975351 | 0 | EPSS Ckt | N | 2024
67991 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | TRANSFORMER | 223869539293 | 2024-10-01 | 1233 | 20241001 | 1330 | 2582382 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 38.7355 | -120.6447 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 24-0117847 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1976966 | 0 | EPSS Ckt | N | 2024
68011 | SIERRA | EL DORADO | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 2024-10-05 | 2348 | 20241006 | 409 | 2587089 | 261 | Distribution Circuit | Animal | Squirrel | 3938 | 884504 | 38.7934 | -120.62 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0119894 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1978131 | 0 | EPSS Ckt | Y | 2024 | C+GRD
68050 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | RECLOSER | COLUMBIA HILL TEMP GEN | 2024-10-15 | 1517 | 20241015 | 1616 | 2595489 | 59 | Distribution Circuit | Company Initiated | Personnel- company | 978 | 57702 | 39.333 | -121.0999 | No | Clear;32-90 F | Switch (OH) | Normal | 24-0100880 | OH | Sus | 35555475 | NORTH VALLEY AND SIERRA | OCT | Multi-Fault | 0 | No | No | No | 1980807 | 0 | EPSS Ckt | N | 2024 | A B C
68060 | SIERRA | NEVADA | ALLEGHANY-1102 | 152101102 | SWITCH | WC 1101/2 | 2024-10-17 | 1541 | 20241018 | 1013 | 2597505 | 1112 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 103177 | 39.364 | -120.7923 | Yes | Partly Cloudy;32-90 F |  |  | 24-0124725 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981428 | 0 | EPSS Ckt | N | 2024
68062 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | FUSE | 11313 | 2024-10-17 | 1756 | 20241017 | 1932 | 2597638 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1536 | 38.7837 | -120.8169 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0124786 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981510 | 0 | EPSS Ckt | N | 2024
68064 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 2024-10-17 | 2201 | 20241018 | 810 | 2598019 | 609 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1043 | 150420 | 38.8435 | -120.8737 | Yes | Clear;32-90 F |  |  | 24-0124814 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981578 | 0 | EPSS Ckt | Y | 2024 | A & C
68074 | SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 2024-10-18 | 1933 | 20241018 | 1956 | 2598979 | 23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 165 | 3687 | 39.3638 | -120.7923 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0094752 | OH | Sus | 31649085 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981853 | 0 | Non-EPSS | N | 2024 | N/A
68075 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 2024-10-18 | 1945 | 20241018 | 2235 | 2598984 | 170 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1043 | 83466 | 38.8154 | -120.8221 | No | Clear;32-90 F |  |  | 24-0125274 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1981857 | 0 | EPSS Ckt | Y | 2024 | B & C
68076 | SIERRA | NEVADA | PIKE CITY SUB | 15220 | RECLOSER | PIKE CITY GENERATOR | 2024-10-18 | 2009 | 20241018 | 2026 | 2599004 | 17 | Distribution Circuit | Company Initiated | Return Circuit Normal | 438 | 7446 | 39.438 | -120.996 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0100603 | OH | Sus | 35559799 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1981866 | 0 | Non-EPSS | N | 2024 | NONE
68078 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 2024-10-19 | 707 | 20241019 | 923 | 2599109 | 136 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 680 | 38.8986 | -120.8986 | No | Clear;32-90 F |  |  | 24-0125327 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1981952 | 0 | EPSS Ckt | N | 2024
68093 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | JUMPER | OJ TWD CGC 223955535637 | 2024-10-24 | 1656 | 20241024 | 2235 | 2603270 | 339 | Distribution Circuit | Vegetation | Other ground vegetation | 1 | 339 | 38.6369 | -120.6146 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0127604 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1983350 | 0 | EPSS Ckt | N | 2024
68096 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | OTHER | WIRE DOWN | 2024-10-26 | 232 | 20241026 | 1142 | s1983656 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8038 | 38.7896 | -120.7353 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0128108 | OH | Sus | 46344796 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | Yes | Yes | 1983656 | 0 | EPSS Ckt | N | 2024
68101 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | RECLOSER | 935730 | 2024-10-26 | 1216 | 20241026 | 1423 | 2604886 | 127 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 87 | 11049 | 39.4387 | -120.9996 | No | Clear;32-90 F |  |  | 24-0128182 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Ground | 0 | No | No | No | 1983785 | 0 | EPSS Ckt | Y | 2024 | A
68112 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 2024-10-28 | 712 | 20241028 | 840 | 2605672 | 88 | Distribution Circuit | Animal | Bird found | 582 | 32176 | 38.9 | -120.9074 | No | Fog;32-90 F | Conductor- Overhead | Normal | 24-0128371 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1983985 | 0 | EPSS Ckt | Y | 2024 | b+c
68118 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2024-10-29 | 724 | 20241029 | 1017 | 2606823 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3061 | 160043 | 38.7716 | -120.8148 | No | Clear;32-90 F |  |  | 24-0128839 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Line to Line | 0 | No | No | No | 1984311 | 0 | EPSS Ckt | Y | 2024 | B-C INST OC
68129 | SIERRA | EL DORADO | APPLE HILL-1104 | 153661104 | FUSE | 12625 | 2024-10-29 | 2145 | 20241030 | 119 | 2607823 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 32528 | 38.7911 | -120.7022 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0129289 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | OCT | Force Out | 0 | No | No | No | 1984633 | 0 | EPSS Ckt | N | 2024
68153 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 2024-11-02 | 646 | 20241102 | 1013 | 2611292 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3691 | 247443 | 38.9144 | -121.0197 | No | Overcast-Fog;32-90 F |  |  | 24-0130842 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1985710 | 0 | EPSS Ckt | Y | 2024 | B GRD
68157 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 6765 | 2024-11-02 | 1552 | 20241102 | 1714 | 2611815 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 984 | 39.4912 | -121.0862 | No | Partly Cloudy;32-90 F |  |  | 24-0131021 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1985896 | 0 | EPSS Ckt | N | 2024
68174 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | RECLOSER | 654798 | 2024-11-05 | 2220 | 20241106 | 619 | 2615034 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1044 | 122076 | 38.8435 | -120.8737 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132298 | OH | Sus | 31716514 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1986822 | 0 | EPSS Ckt | Y | 2024 | A/C
68175 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | RECLOSER | 11132 | 2024-11-06 | 16 | 20241106 | 1242 | 2615249 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 2827 | 556689 | 38.7716 | -120.8148 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0132316 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1986879 | 0 | EPSS Ckt | Y | 2024 | LINE TO GRD
68183 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJS LINE & BUCK @ CGC 222649061475 | 2024-11-06 | 1818 | 20241106 | 2221 | 2617229 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 39.3509 | -121.064 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0132887 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1987326 | 0 | EPSS Ckt | N | 2024
68190 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | RECLOSER | 836878 | 2024-11-08 | 640 | 20241108 | 1608 | 2618410 | 568 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4908 | 1446145 | 38.7371 | -120.6759 | No | Clear;32-90 F |  |  | 24-0133388 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1987678 | 0 | EPSS Ckt | Y | 2024 | DCD
68217 | SIERRA | NEVADA | PIKE CITY-1101 | 152201101 | FUSE | 38371 | 2024-11-12 | 2325 | 20241113 | 258 | 2623476 | 213 | Distribution Circuit | Company Initiated | Other Circuits | 24 | 5112 | 39.4746 | -121.033 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0134875 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Force Out | 0 | No | No | No | 1989133 | 0 | EPSS Ckt | N | 2024
68233 | SIERRA | NEVADA | BRUNSWICK-1102 | 152481102 | JUMPER | OJ 2 SP S/SIDE OF CGC# 223014056380 | 2024-11-18 | 815 | 20241118 | 1200 | 2628214 | 225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 676 | 24772 | 39.2103 | -120.939 | No | Clear;32-90 F | Jumper | Burned Open | 24-0136512 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Open Circuit | 0 | No | No | No | 1990642 | 1 | EPSS Ckt | N | 2024
68243 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | 3 SPANS N/O TX CGC 223441037065 | 2024-11-20 | 830 | 20241120 | 1009 | 2630327 | 99 | Distribution Circuit | Environmental/External | Flood/Erosion | 4 | 396 | 38.679 | -120.7946 | No | Overcast;32-90 F | Other | Broken | 24-0137535 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1991260 | 0 | EPSS Ckt | N | 2024
68251 | SIERRA | PLACER | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 2024-11-20 | 1105 | 20241120 | 1454 | 2630713 | 229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 9160 | 39.0098 | -120.8455 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 24-0137759 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991434 | 0 | EPSS Ckt | N | 2024
68259 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5811 | 2024-11-20 | 1432 | 20241120 | 1920 | 2631373 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 16416 | 38.8819 | -120.8303 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0137966 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1991553 | 0 | EPSS Ckt | N | 2024
68268 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 2024-11-21 | 737 | 20241121 | 908 | 2632337 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 455 | 38.8986 | -120.8986 | No | Overcast-Rain;32-90 F |  |  | 24-0138263 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1991756 | 0 | EPSS Ckt | N | 2024
68277 | SIERRA | EL DORADO | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER | 223522638310 | 2024-11-22 | 1730 | 20241122 | 2054 | 2635151 | 204 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 204 | 38.7127 | -120.7665 | No | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 24-0139291 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1992302 | 0 | EPSS Ckt | N | 2024
68279 | SIERRA | NEVADA | COLUMBIA HILL-1101 | 152471101 | FUSE | 3911 | 2024-11-22 | 1808 | 20241123 | 1313 | 2635438 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5725 | 39.3625 | -121.1126 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0139288 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | Yes | No | 1992298 | 0 | EPSS Ckt | N | 2024
68287 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 11425 | 2024-11-22 | 2146 | 20241123 | 113 | 2635582 | 207 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 10 | 2070 | 38.6859 | -120.6469 | No | Overcast-Drizzle-Strong Winds;32-90 F |  |  | 24-0139365 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Line | 0 | No | No | No | 1992371 | 0 | EPSS Ckt | N | 2024
68297 | SIERRA | PLACER | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 2024-11-23 | 906 | 20241123 | 1028 | 2635948 | 82 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 1640 | 38.8528 | -120.789 | No | Overcast-Fog-Rain;32-90 F |  |  | 24-0139453 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | NOV | Line to Ground | 0 | No | No | No | 1992463 | 0 | EPSS Ckt | N | 2024
68326 | SIERRA | EL DORADO | APPLE HILL-1103 | 153661103 | FUSE | 1435 | 2024-12-05 | 1355 | 20241205 | 1550 | 2645177 | 115 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 20 | 2300 | 38.7507 | -120.7582 | No | Clear;32-90 F |  |  | 24-0143046 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1994867 | 0 | EPSS Ckt | N | 2024
68329 | SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | SWITCH | 610307 | 2024-12-05 | 1630 | 20241205 | 1804 | 2645331 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 7896 | 39.2992 | -121.0399 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994884 | 0 | EPSS Ckt | N | 2024
68329 | SIERRA | NEVADA | BRUNSWICK-1103 | 152481103 | SWITCH | 610307 | 2024-12-05 | 1630 | 20241205 | 1804 | 2645331 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 7896 | 39.2992 | -121.0399 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0143097 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1994884 | 0 | EPSS Ckt | N | 2024
68342 | SIERRA | NEVADA | WASHINGTON CITY SUB | 15804 | OCB | 52G | 2024-12-11 | 1739 | 20241211 | 1808 | 2650166 | 29 | Distribution Circuit | Company Initiated | Return Circuit Normal | 156 | 4524 | 39.3638 | -120.7923 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0131574 | OH | Sus | 35578012 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1996625 | 0 | Non-EPSS | N | 2024 | NONE
68346 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 2019 | 2024-12-12 | 621 | 20241212 | 1012 | 2650440 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 5313 | 38.5874 | -120.6609 | No | Overcast-Heavy Rain;32-90 F | Insulator | Broken | 24-0144555 | OH | Sus | 46415887 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1996705 | 0 | EPSS Ckt | N | 2024
68355 | SIERRA | PLACER | BONNIE NOOK-1101 | 152301101 | FUSE | 6389 | 2024-12-13 | 1104 | 20241213 | 1114 | 2651826 | 10 | Distribution Circuit | Company Initiated | Improper Construction | 6 | 60 | 39.1984 | -120.8338 | No | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Normal | 24-0138212 | OH | Sus | 35367335 | NORTH VALLEY AND SIERRA | DEC | Force Out | 0 | No | No | No | 1997146 | 0 | EPSS Ckt | N | 2024
68379 | SIERRA | EL DORADO | APPLE HILL-2102 | 153662102 | FUSE | 12121 | 2024-12-14 | 729 | 20241214 | 918 | 2654387 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 1308 | 38.6376 | -120.6493 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145363 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1997680 | 0 | EPSS Ckt | N | 2024
68399 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223394241627 | 2024-12-14 | 857 | 20241215 | 1700 | 2656223 | 1923 | Transformer only | Vegetation | Tree - fell into line | 1 | 1923 | 38.8034 | -120.8064 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146000 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998341 | 0 | EPSS Ckt | N | 2024
68400 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223407041627 | 2024-12-14 | 857 | 20241214 | 1830 | 2658314 | 573 | Transformer only | Vegetation | Tree - fell into line | 1 | 573 | 38.8034 | -120.8056 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Fuse | Normal | 24-0146005 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998344 | 0 | EPSS Ckt | N | 2024
68436 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 2024-12-14 | 1215 | 20241214 | 1759 | 2658779 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1720 | 38.8986 | -120.8986 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145774 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998106 | 0 | EPSS Ckt | N | 2024
68438 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 2024-12-14 | 1218 | 20241215 | 1132 | 2658814 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 79458 | 38.9142 | -120.9386 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145979 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | Yes | No | 1998318 | 0 | EPSS Ckt | N | 2024
68443 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 914599 | 2024-12-14 | 1352 | 20241215 | 1426 | 2659574 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8844 | 39.0084 | -120.8974 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145976 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | Yes | No | 1998314 | 0 | EPSS Ckt | N | 2024
68444 | SIERRA | EL DORADO | EL DORADO PH-2102 | 152762102 | TRANSFORMER | 224004240528 | 2024-12-14 | 1545 | 20241215 | 936 | 2660013 | 1071 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 2142 | 38.7708 | -120.5964 | Yes | Overcast-Fog-Rain;32-90 F | Fuse | Normal | 24-0146209 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998558 | 0 | EPSS Ckt | N | 2024
68445 | SIERRA | PLACER | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 2024-12-14 | 1558 | 20241214 | 2031 | 2660010 | 273 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 2184 | 38.9807 | -120.9404 | Yes | Partly Cloudy-Fog;32-90 F |  |  | 24-0146071 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 1998413 | 0 | EPSS Ckt | N | 2024
68455 | SIERRA | PLACER | BONNIE NOOK-1102 | 152301102 | FUSE | 6377 | 2024-12-16 | 811 | 20241216 | 857 | 2662440 | 46 | Distribution Circuit | Company Initiated | Improper Construction | 89 | 4111 | 39.2023 | -120.8368 | No | Overcast-Fog-Rain;32-90 F | Fuse | Normal | 24-0146507 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1998881 | 1 | EPSS Ckt | N | 2024
68466 | SIERRA | EL DORADO | PLACERVILLE-2106 | 153082106 | TRANSFORMER | 223303841219 | 2024-12-17 | 1027 | 20241217 | 1233 | 2664094 | 126 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 126 | 38.7914 | -120.842 | No | Clear;32-90 F | Service conductor | Broken | 24-0146795 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Ground | 0 | No | No | No | 1999287 | 0 | EPSS Ckt | N | 2024
68482 | SIERRA | EL DORADO | PLACERVILLE-1112 | 153081112 | RECLOSER | 74084 | 2024-12-26 | 735 | 20241226 | 907 | 2669880 | 92 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 15548 | 38.7191 | -120.7692 | No | Overcast-Drizzle;32-90 F |  |  | 24-0147781 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2000841 | 0 | EPSS Ckt | N | 2024 | A-C
68503 | SIERRA | PLACER | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 2024-12-31 | 840 | 20241231 | 1133 | 2673024 | 173 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 9861 | 38.9142 | -120.9386 | No | Clear;32-90 F |  |  | 24-0148296 | OH | Sus | 0 | NORTH VALLEY AND SIERRA | DEC | Line to Line | 0 | No | No | No | 2001588 | 0 | EPSS Ckt | N | 2024
69222 | SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | FUSE | 735 | 2023-02-25 | 1759 | 20230301 | 1545 | 2009078 | 5626 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 56260 | 38.8027 | -122.8323 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035423 | OH | Sus | 0 | NORTH COAST | FEB | Three Phase Fault | 0 | No | Yes | No | 1818269 | 0 | EPSS Ckt | N | 2023
69259 | SONOMA | SANTA ROSA | CLOVERDALE-1102 | 42821102 | TRANSFORMER | T34579 | 2023-03-02 | 1119 | 20230303 | 1045 | 2019707 | 1406 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2812 | 38.8834 | -122.9938 | No | Clear;32-90 F |  |  | 23-0038803 | OH | Sus | 0 | NORTH COAST | MAR | Line to Ground | 0 | No | No | No | 1820867 | 0 | EPSS Ckt | N | 2023
69940 | SONOMA | SANTA ROSA | GEYSERVILLE-1102 | 42891102 | TRANSFORMER | 217632241396 | 2023-08-31 | 854 | 20230831 | 1242 | 2206801 | 228 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 228 | 38.8003 | -122.8321 | No | Partly Cloudy;32-90 F | Transformer | Failed/Faulted | 23-0111169 | OH | Sus | 0 | NORTH COAST | AUG | Line to Ground | 0 | No | No | No | 1870498 | 0 | EPSS Ckt | N | 2023
72548 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 91241 | 2023-01-04 | 53 | 20230104 | 1209 | 1912612 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 676 | 38.2831 | -120.5514 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005724 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1796132 | 0 | EPSS Ckt | N | 2023
72571 | STOCKTON | MOTHER LODE | STANISLAUS 1701 | 162821701 | FUSE | 1101 | 2023-01-04 | 1356 | 20230106 | 1035 | 1914288 | 2679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 42864 | 38.1781 | -120.3802 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006157 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1796476 | 1 | EPSS Ckt | N | 2023
72594 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | MTR#1004935666 | 2023-01-04 | 1708 | 20230106 | 1208 | 1914421 | 2580 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5160 | 38.4982 | -120.7093 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0006402 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796699 | 0 | EPSS Ckt | N | 2023
72602 | STOCKTON | MOTHER LODE | ELECTRA 1101 | 162161101 | TRANSFORMER | 223904526157 | 2023-01-04 | 2007 | 20230106 | 1520 | 1918158 | 2593 | Transformer only | Environmental/External | Lightning | 1 | 2593 | 38.3764 | -120.6391 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0006685 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1796986 | 0 | EPSS Ckt | N | 2023
72606 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | FUSE | 1065 | 2023-01-04 | 2037 | 20230105 | 1846 | 1918304 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19935 | 38.3787 | -120.6973 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0006823 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797125 | 0 | EPSS Ckt | N | 2023
72607 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L1259 | 2023-01-04 | 2037 | 20230105 | 1019 | 1918303 | 822 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 13974 | 38.403 | -120.5553 | Yes | Clear;32-90F |  |  | 23-0007236 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797507 | 0 | EPSS Ckt | N | 2023
72612 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1429 | 2023-01-04 | 2123 | 20230106 | 1045 | 1918780 | 2242 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9012 | 38.2059 | -120.5188 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0006955 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797257 | 0 | EPSS Ckt | N | 2023
72621 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | FUSE | L497 | 2023-01-04 | 2153 | 20230105 | 833 | 1921121 | 640 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 144 | 92206 | 38.1473 | -120.4732 | Yes | Clear;32-90F |  |  | 23-0007079 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797373 | 1 | EPSS Ckt | N | 2023
72643 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | FUSE | 1814 | 2023-01-05 | 942 | 20230106 | 1232 | 1921514 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 26850 | 38.1767 | -120.4481 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0007476 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1797701 | 0 | EPSS Ckt | N | 2023
72646 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | FUSE | L7131 | 2023-01-05 | 1101 | 20230106 | 800 | 1921851 | 1259 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 3777 | 38.1728 | -120.4666 | Yes | Clear;32-90F |  |  | 23-0007637 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797841 | 0 | EPSS Ckt | N | 2023
72656 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319963363140 | 2023-01-05 | 1841 | 20230106 | 1210 | 1923581 | 1049 | Transformer only | Environmental/External | Water | 1 | 1049 | 38.2339 | -120.5137 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0008002 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1798133 | 0 | EPSS Ckt | N | 2023
72667 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L1259 | 2023-01-06 | 1249 | 20230106 | 1607 | 1924785 | 195 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 3315 | 38.403 | -120.5553 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0008282 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1798316 | 0 | EPSS Ckt | N | 2023
72669 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJS 1 W/OF CGC 319725060055 | 2023-01-06 | 1554 | 20230106 | 1700 | 1925253 | 66 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 132 | 38.15 | -120.5973 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0008470 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1798406 | 0 | EPSS Ckt | N | 2023
72686 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1429 | 2023-01-07 | 1824 | 20230109 | 2116 | 1927542 | 3052 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18312 | 38.2059 | -120.5188 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010069 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1799913 | 0 | EPSS Ckt | N | 2023
72687 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | FUSE | L517 | 2023-01-07 | 1829 | 20230108 | 1836 | 1927559 | 1447 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 20258 | 38.2997 | -120.6833 | Yes | Clear;32-90 F |  |  | 23-0010414 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1800261 | 0 | EPSS Ckt | N | 2023
72688 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRIP-SAVER | L1697 | 2023-01-07 | 1832 | 20230108 | 2240 | 1927576 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 52024 | 38.3793 | -120.638 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009081 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1798910 | 0 | EPSS Ckt | N | 2023 | POS 1 AND 3
72689 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 675544 | 2023-01-07 | 1834 | 20230108 | 1620 | 1927589 | 1306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3918 | 38.3449 | -120.5685 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0010318 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1800165 | 0 | EPSS Ckt | N | 2023
72836 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | JUMPER | WIRE DOWN 2 SPANS E/OF L3635 | 2023-01-08 | 826 | 20230109 | 1024 | 1933375 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 68156 | 38.4969 | -120.7238 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010083 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1799929 | 0 | EPSS Ckt | N | 2023
72844 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320087260835 | 2023-01-08 | 1137 | 20230110 | 2124 | 1938900 | 3467 | Distribution Circuit | Environmental/External | Lightning | 2 | 6934 | 38.1706 | -120.4707 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0011436 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801195 | 0 | EPSS Ckt | N | 2023
72874 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | SWITCH | 1349 | 2023-01-08 | 2002 | 20230111 | 1240 | 1934637 | 3878 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 356776 | 38.2826 | -120.5286 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0010469 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1800317 | 0 | EPSS Ckt | N | 2023
72875 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRIP-SAVER | 5357 | 2023-01-08 | 2002 | 20230111 | 1621 | 1938071 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 209049 | 38.2819 | -120.5422 | Yes | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0010469 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1800969 | 0 | EPSS Ckt | N | 2023 | #1 AND #2 BLOWN
72878 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 1347 | 2023-01-08 | 2110 | 20230109 | 805 | 1934788 | 655 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 3275 | 38.2829 | -120.5262 | Yes | Clear;32-90 F |  |  | 23-0010860 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1800710 | 0 | EPSS Ckt | N | 2023
72901 | STOCKTON | MOTHER LODE | TIGER CREEK 0201 | 161380201 | SWITCH | 201/2 | 2023-01-09 | 715 | 20230109 | 1454 | 1936431 | 456 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1511 | 38.4489 | -120.4926 | Yes | Clear;32-90 F |  |  | 23-0010839 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1800695 | 0 | EPSS Ckt | N | 2023
72974 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 2023-01-10 | 418 | 20230111 | 2048 | 1941845 | 2430 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 659665 | 38.4069 | -120.6707 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011873 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1801640 | 0 | EPSS Ckt | N | 2023 | A B C
72981 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319673563450 | 2023-01-10 | 430 | 20230111 | 1553 | 1944811 | 2123 | Transformer only | Environmental/External | Lightning | 1 | 2123 | 38.2426 | -120.6147 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012973 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802536 | 0 | EPSS Ckt | N | 2023
72984 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3229 | 2023-01-10 | 432 | 20230112 | 1032 | 1942158 | 3239 | Distribution Circuit | Environmental/External | Lightning | 8 | 12042 | 38.242 | -120.6106 | Yes | Clear;32-90 F | Transformer (OH) | Burned/flashed | 23-0012132 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801902 | 0 | EPSS Ckt | N | 2023
72986 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 1093 | 2023-01-10 | 433 | 20230112 | 1204 | 1945750 | 3331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14979 | 38.3498 | -120.549 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0011905 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802330 | 0 | EPSS Ckt | N | 2023
72988 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | L3855 | 2023-01-10 | 435 | 20230110 | 1804 | 1942203 | 809 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 9708 | 38.3646 | -120.653 | Yes | Clear;32-90 F |  |  | 23-0012872 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802448 | 0 | EPSS Ckt | N | 2023
72991 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 2023-01-10 | 435 | 20230110 | 903 | 1943407 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 31624 | 38.413 | -120.55 | Yes | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | Yes | No | 1801788 | 0 | EPSS Ckt | N | 2023 | NONE
72996 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | L3857 | 2023-01-10 | 436 | 20230112 | 1237 | 1942222 | 3361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 57137 | 38.3497 | -120.6591 | Yes | Clear;32-90F | Insulator | Broken- wire on ground | 23-0013497 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1802999 | 0 | EPSS Ckt | N | 2023
72999 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L361 | 2023-01-10 | 437 | 20230110 | 1507 | 1942240 | 630 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 6930 | 38.396 | -120.6589 | Yes | Clear;32-90 F |  |  | 23-0012633 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802297 | 0 | EPSS Ckt | N | 2023
73001 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223832627014 | 2023-01-10 | 450 | 20230112 | 1102 | 1942463 | 3252 | Transformer only | Environmental/External | Lightning | 3 | 9756 | 38.4001 | -120.662 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0012720 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802348 | 0 | EPSS Ckt | N | 2023
73003 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1771 | 2023-01-10 | 521 | 20230111 | 1315 | 1943922 | 1914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11484 | 38.2056 | -120.5728 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012070 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1801847 | 0 | EPSS Ckt | N | 2023
73006 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | JUMPER | JPRS @ CGC# 320084555915 | 2023-01-10 | 709 | 20230112 | 1441 | 1945480 | 3332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6664 | 38.0362 | -120.4709 | Yes | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0012578 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802256 | 0 | EPSS Ckt | N | 2023
73012 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223810926762 | 2023-01-10 | 944 | 20230111 | 1641 | 1944273 | 1857 | Transformer only | Environmental/External | Lightning | 1 | 1857 | 38.3938 | -120.6716 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013100 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802655 | 0 | EPSS Ckt | N | 2023
73013 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | 1065 | 2023-01-10 | 949 | 20230110 | 1443 | 1944308 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4410 | 38.3787 | -120.6973 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012186 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1801949 | 0 | EPSS Ckt | N | 2023
73068 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223810026588 | 2023-01-11 | 1643 | 20230112 | 1132 | 1948669 | 1129 | Transformer only | Environmental/External | Lightning | 1 | 1129 | 38.389 | -120.672 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013961 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1803315 | 0 | EPSS Ckt | N | 2023
73090 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3229 | 2023-01-12 | 1529 | 20230112 | 1724 | 1950445 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 920 | 38.242 | -120.6106 | No | Clear;32-90F | Transformer (OH) | Normal | 23-0014653 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803822 | 0 | EPSS Ckt | N | 2023
73101 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223859225217 | 2023-01-13 | 921 | 20230113 | 1448 | 1951495 | 327 | Transformer only | Unknown Cause | Patrol - found nothing | 17 | 711 | 38.3509 | -120.6552 | No | Clear;32-90 F |  |  | 23-0015306 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1804265 | 0 | EPSS Ckt | N | 2023
73149 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | TRANSFORMER | 319487565550 | 2023-01-14 | 2242 | 20230115 | 1207 | 1955284 | 805 | Distribution Circuit | Environmental/External | Lightning | 1 | 805 | 38.3002 | -120.6794 | Yes | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0016557 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805307 | 0 | EPSS Ckt | N | 2023
73154 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223909526040 | 2023-01-15 | 557 | 20230115 | 1254 | 1955571 | 417 | Transformer only | Environmental/External | Lightning | 1 | 417 | 38.3735 | -120.6373 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0016602 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805349 | 0 | EPSS Ckt | N | 2023
73170 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | TRANSFORMER | 320115157689 | 2023-01-15 | 1342 | 20230115 | 1731 | 1956009 | 229 | Transformer only | Vegetation | Tree - fell into line | 2 | 458 | 38.0844 | -120.4614 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0016715 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805432 | 0 | EPSS Ckt | N | 2023
73267 | STOCKTON | MOTHER LODE | TIGER CREEK-0201 | 161380201 | FUSE | 1745 | 2023-01-19 | 1546 | 20230120 | 1348 | 1962590 | 1212 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 2025 | 38.4543 | -120.4756 | No | Clear;32-90 F |  |  | 23-0019013 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1806830 | 1 | EPSS Ckt | N | 2023
73268 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1631 | 2023-01-19 | 1646 | 20230120 | 1520 | 1962672 | 1354 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 15934 | 38.2652 | -120.5839 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0019072 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1806856 | 1 | EPSS Ckt | N | 2023
73291 | STOCKTON | MOTHER LODE | TIGER CREEK-0201 | 161380201 | FUSE | 1745 | 2023-01-22 | 1027 | 20230122 | 1127 | 1964668 | 60 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 60 | 38.4543 | -120.4756 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0019859 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807306 | 1 | EPSS Ckt | N | 2023
73322 | STOCKTON | MOTHER LODE | TIGER CREEK-0201 | 161380201 | FUSE | 1745 | 2023-01-26 | 956 | 20230126 | 1321 | 1968653 | 205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 205 | 38.4543 | -120.4756 | No | Clear;32-90F | Customer Equipment | Deteriorated | 23-0021617 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1808336 | 0 | EPSS Ckt | N | 2023
73358 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | FB'S 2 N/OF L5533 | 2023-02-03 | 838 | 20230203 | 1148 | 1975688 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 570 | 38.1789 | -120.5681 | No | Clear;32-90F | Pole-Wood | Deteriorated | 23-0024767 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1810210 | 0 | EPSS Ckt | N | 2023
73368 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L359 | 2023-02-05 | 611 | 20230205 | 1356 | 1977225 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 22785 | 38.3968 | -120.6591 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0025357 | OH | Sus | 31636190 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1810655 | 0 | EPSS Ckt | N | 2023
73370 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223708024675 | 2023-02-06 | 852 | 20230206 | 910 | 1977982 | 18 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 18 | 38.3366 | -120.7081 | No | Clear;32-90F | Transformer (OH) | Leaking | 23-0025589 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1810885 | 0 | EPSS Ckt | N | 2023
73391 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | TRANSFORMER | 319486265650 | 2023-02-10 | 107 | 20230210 | 940 | 1981406 | 513 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1539 | 38.3029 | -120.6801 | No | Clear;32-90 F | Transformer | Burned/flashed | 23-0027408 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812056 | 0 | EPSS Ckt | N | 2023
73397 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2897 | 2023-02-11 | 640 | 20230211 | 830 | 1982213 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 880 | 38.2121 | -120.5192 | No | Clear;32-90 F |  |  | 23-0027808 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1812380 | 1 | EPSS Ckt | N | 2023
73521 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | FUSE | 2401 | 2023-02-24 | 748 | 20230224 | 1111 | 2003951 | 203 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 2639 | 38.2061 | -120.4636 | Yes | Clear;32-90 F |  |  | 23-0034021 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1816984 | 0 | EPSS Ckt | N | 2023
73540 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | 53709 | 2023-02-24 | 2202 | 20230225 | 848 | 2007457 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 646 | 38.4756 | -120.7051 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035011 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1817878 | 0 | EPSS Ckt | N | 2023
73554 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 2023-02-27 | 1157 | 20230227 | 1425 | 2012136 | 148 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 3108 | 38.2085 | -120.3677 | Yes | Clear;32-90F |  |  | 23-0036513 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819111 | 0 | EPSS Ckt | N | 2023
73564 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L609 | 2023-02-27 | 1435 | 20230227 | 2104 | 2012700 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | 38.299 | -120.5037 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036613 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1819187 | 0 | EPSS Ckt | N | 2023
73566 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L1155 | 2023-02-27 | 1500 | 20230227 | 1704 | 2012760 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 18 | 2232 | 38.4639 | -120.5587 | Yes | Clear;32-90F |  |  | 23-0036643 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819214 | 0 | EPSS Ckt | N | 2023
73576 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L1155 | 2023-02-27 | 1707 | 20230304 | 1822 | 2013334 | 7235 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 25574 | 38.4639 | -120.5587 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036669 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | Yes | No | 1819253 | 0 | EPSS Ckt | N | 2023
73578 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 2023-02-27 | 1734 | 20230227 | 2102 | 2013328 | 208 | Distribution Circuit | Vegetation | Tree - branch fell on line | 292 | 60736 | 38.4739 | -120.6268 | Yes | Clear;Below 32 F | Conductor- Overhead | Normal | 23-0036687 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819248 | 0 | EPSS Ckt | N | 2023 | A & B
73589 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L1149 | 2023-02-27 | 2246 | 20230306 | 1550 | 2015922 | 9664 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 260928 | 38.4772 | -120.627 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1819866 | 0 | EPSS Ckt | N | 2023
73591 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 2023-02-28 | 544 | 20230302 | 1803 | 2014089 | 2145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 270266 | 38.4739 | -120.6268 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1819592 | 0 | EPSS Ckt | N | 2023 | sgf
73594 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | 369994 | 2023-02-28 | 544 | 20230305 | 1800 | 2018989 | 7936 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 31744 | 38.4848 | -120.5888 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1820625 | 0 | EPSS Ckt | N | 2023
73595 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L2133 | 2023-02-28 | 544 | 20230304 | 1201 | 2018990 | 6137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 159562 | 38.489 | -120.589 | Yes | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken | 23-0037060 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1820628 | 0 | EPSS Ckt | N | 2023
73598 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | SWITCH | 199507 | 2023-02-28 | 642 | 20230301 | 1057 | 2016754 | 1695 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 84750 | 38.4977 | -120.6868 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036767 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1820054 | 0 | EPSS Ckt | N | 2023
73599 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | JUMPER | OJ 3 S/OF CGC 223798030911 | 2023-02-28 | 642 | 20230304 | 1049 | 2017945 | 6007 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6007 | 38.5062 | -120.6734 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036767 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1820311 | 0 | EPSS Ckt | N | 2023
73607 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 5395 | 2023-02-28 | 1006 | 20230302 | 2226 | 2019703 | 3620 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 36200 | 38.1984 | -120.362 | Yes | Clear;32-90F | Service conductor | Broken- wire on ground | 23-0037575 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1820813 | 0 | EPSS Ckt | N | 2023
73617 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | JUMPER | FB @ CGC# 224143429390 | 2023-02-28 | 1013 | 20230304 | 1822 | 2021559 | 6249 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 350313 | 38.4642 | -120.5543 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039543 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1821345 | 0 | EPSS Ckt | N | 2023
73620 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | RECLOSER | 12256 | 2023-02-28 | 1014 | 20230304 | 1905 | 2014179 | 6291 | Distribution Circuit | Vegetation | Tree - fell into line | 3595 | 7938552 | 38.4437 | -120.5088 | Yes | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037218 | OH | Sus | 35427402 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1819673 | 0 | EPSS Ckt | N | 2023 | B TIMED
73623 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 36676 | 2023-02-28 | 1133 | 20230302 | 955 | 2015045 | 2782 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 397826 | 38.3724 | -120.5067 | Yes | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Normal | 23-0037286 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819714 | 0 | EPSS Ckt | N | 2023 | B & C PHASE
73625 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 2541 | 2023-02-28 | 1203 | 20230302 | 2226 | 2015176 | 3503 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 182156 | 38.1927 | -120.3629 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken | 23-0037405 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819813 | 0 | EPSS Ckt | N | 2023
73630 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 2023-02-28 | 1208 | 20230301 | 113 | 2016116 | 785 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 244 | 191540 | 38.4437 | -120.5088 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1819921 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
73633 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | FUSE | L1725 | 2023-02-28 | 1208 | 20230304 | 1445 | 2018962 | 5917 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 207095 | 38.4835 | -120.5485 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | Yes | No | 1820615 | 0 | EPSS Ckt | N | 2023
73637 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 2023-02-28 | 1208 | 20230301 | 1211 | 2016051 | 1443 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 170274 | 38.413 | -120.55 | Yes | Overcast-Snow;Below 32 F |  |  | 23-0037349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1819906 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
73640 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 77204 | 2023-02-28 | 1208 | 20230302 | 1215 | 2016175 | 2887 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 56 | 161672 | 38.3443 | -120.5829 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1819932 | 0 | EPSS Ckt | N | 2023 | N/A
73654 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 2023-02-28 | 1550 | 20230228 | 1714 | 2016092 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 9072 | 38.1832 | -120.3754 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037575 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1819919 | 0 | EPSS Ckt | N | 2023 | ABC- GRD
73656 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320362762183 | 2023-02-28 | 1550 | 20230302 | 1244 | 2016358 | 2694 | Transformer only | Vegetation | Tree - fell into line | 4 | 10776 | 38.2077 | -120.3747 | Yes | Clear;32-90F | Service conductor | Broken | 23-0037575 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1819972 | 0 | EPSS Ckt | N | 2023
73657 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | 69623 | 2023-02-28 | 1552 | 20230301 | 1809 | 2016066 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3154 | 38.3927 | -120.6397 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037977 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1820286 | 0 | EPSS Ckt | N | 2023
73663 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 2023-02-28 | 1929 | 20230302 | 2036 | 2016365 | 2947 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 318276 | 38.1832 | -120.3754 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037706 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1820037 | 0 | EPSS Ckt | N | 2023 | AB
73665 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 394499 | 2023-02-28 | 1938 | 20230301 | 1712 | 2018828 | 1294 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 58 | 75052 | 38.2635 | -120.4875 | Yes | Clear;32-90 F |  |  | 23-0038381 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1820569 | 0 | EPSS Ckt | N | 2023
73671 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | JUMPER | OJ ON HARD TAP 1 W/OH 69623 | 2023-02-28 | 2128 | 20230301 | 1434 | 2017511 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2052 | 38.393 | -120.6403 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037906 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1820241 | 0 | EPSS Ckt | N | 2023
73672 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 2023-02-28 | 2206 | 20230303 | 850 | 2017115 | 3524 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 74004 | 38.2085 | -120.3677 | Yes | Clear;32-90F |  |  | 23-0039268 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1821197 | 0 | EPSS Ckt | N | 2023
73673 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1101 | 2023-02-28 | 2240 | 20230303 | 507 | 2017161 | 3267 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 34865 | 38.1781 | -120.3802 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0037858 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1820186 | 1 | EPSS Ckt | N | 2023
73676 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | OTHER | WIRE DOWN 2 SPANS SS/OF CGC#320362060983 | 2023-03-01 | 713 | 20230302 | 1520 | 2017711 | 1927 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 34202 | 38.1729 | -120.3742 | No |  | Conductor- Overhead | Broken- wire on ground | 23-0038347 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1820539 | 0 | EPSS Ckt | N | 2023
73678 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 2127 | 2023-03-01 | 1058 | 20230301 | 1757 | 2018124 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 18855 | 38.4134 | -120.5509 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038453 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820641 | 0 | EPSS Ckt | N | 2023
73683 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223863529405 | 2023-03-01 | 1745 | 20230303 | 1603 | 2018902 | 2778 | Transformer only | Environmental/External | Ice or snow | 1 | 2778 | 38.4663 | -120.6513 | No | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0039496 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1821322 | 0 | EPSS Ckt | N | 2023
73685 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRIP-SAVER | 5357 | 2023-03-01 | 1916 | 20230301 | 2001 | 2019119 | 45 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 2295 | 38.2819 | -120.5422 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038469 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820660 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
73686 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | SWITCH | L2537 | 2023-03-01 | 1925 | 20230301 | 2000 | 2019118 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 679 | 23765 | 38.1736 | -120.3833 | No | Clear;32-90 F | Capacitor | Broken | 23-0038461 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820651 | 0 | EPSS Ckt | N | 2023
73689 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN @ CGC# 224205930163 | 2023-03-01 | 2145 | 20230304 | 1816 | 2021274 | 4111 | Distribution Circuit | Vegetation | Tree - fell into line | 632 | 175524 | 38.4857 | -120.5319 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039449 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1821296 | 0 | EPSS Ckt | N | 2023
73690 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN @ CGC# 224205930163 | 2023-03-01 | 2145 | 20230304 | 1816 | 2021274 | 4111 | Distribution Circuit | Vegetation | Tree - fell into line | 632 | 175524 | 38.4857 | -120.5319 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039449 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1821296 | 0 | EPSS Ckt | N | 2023
73693 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L5681 | 2023-03-02 | 1143 | 20230303 | 1646 | 2021552 | 1743 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 24402 | 38.3875 | -120.4463 | No | Clear;32-90F |  |  | 23-0039556 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1821354 | 0 | EPSS Ckt | N | 2023
73697 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1391 | 2023-03-02 | 1358 | 20230302 | 1633 | 2019962 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 6820 | 38.3307 | -120.5355 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038979 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820980 | 0 | EPSS Ckt | N | 2023
73698 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319840069365 | 2023-03-02 | 1546 | 20230302 | 1706 | 2020151 | 80 | Transformer only | Vegetation | Tree - fell into line | 1 | 80 | 38.405 | -120.5586 | No | Clear;32-90F | Service conductor | Normal | 23-0038922 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820939 | 0 | EPSS Ckt | N | 2023
73699 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | FUSE | 1117 | 2023-03-02 | 1610 | 20230303 | 1107 | 2020199 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 25014 | 38.1708 | -120.3789 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039196 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1821168 | 0 | EPSS Ckt | N | 2023
73700 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | FUSE | L3811 | 2023-03-02 | 1634 | 20230304 | 1326 | 2020233 | 2692 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 18844 | 38.347 | -120.5818 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039322 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1821226 | 0 | EPSS Ckt | N | 2023
73701 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 9881 | 2023-03-02 | 1640 | 20230304 | 1634 | 2021096 | 2874 | Distribution Circuit | Vegetation | Tree - grew into line | 11 | 31614 | 38.3517 | -120.5427 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039690 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1821445 | 0 | EPSS Ckt | N | 2023
73704 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L3767 | 2023-03-02 | 1825 | 20230303 | 1711 | 2020440 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10928 | 38.4787 | -120.6225 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039212 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1821179 | 0 | EPSS Ckt | N | 2023
73716 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319633564000 | 2023-03-04 | 1319 | 20230304 | 1759 | 2022460 | 280 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 560 | 38.2578 | -120.6281 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0040011 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821769 | 0 | EPSS Ckt | N | 2023
73756 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320411661542 | 2023-03-08 | 24 | 20230308 | 1520 | 2026121 | 896 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1792 | 38.1901 | -120.3578 | No | Clear;32-90F | Transformer (OH) | Broken | 23-0041455 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822785 | 0 | EPSS Ckt | N | 2023
73788 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L5783 | 2023-03-10 | 115 | 20230310 | 800 | 2029861 | 405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 4752 | 38.3456 | -120.5652 | No | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 23-0042742 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823556 | 0 | EPSS Ckt | N | 2023
73862 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1631 | 2023-03-14 | 1108 | 20230315 | 1453 | 2036739 | 1665 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 99900 | 38.2652 | -120.5839 | Yes | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0045411 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1825394 | 0 | EPSS Ckt | N | 2023
73918 | STOCKTON | MOTHER LODE | PEORIA FLAT-1704 | 163781704 | FUSE | 20193 | 2023-03-16 | 910 | 20230316 | 1610 | 2047892 | 420 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 420 | 37.9366 | -120.5319 | No | Clear;32-90 F |  |  | 23-0047110 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1826618 | 0 | EPSS Ckt | N | 2023
73946 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L1173 | 2023-03-20 | 1053 | 20230320 | 1324 | 2052907 | 151 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 7097 | 38.466 | -120.5497 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0048756 | OH | Sus | 45703232 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1827894 | 0 | EPSS Ckt | N | 2023
73990 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320392261695 | 2023-03-25 | 33 | 20230325 | 352 | 2066676 | 199 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 199 | 38.1943 | -120.3646 | No | Clear;Below 32 F | Fuse | Normal | 23-0052421 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1830383 | 0 | EPSS Ckt | N | 2023
74004 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 2023-03-28 | 938 | 20230328 | 1729 | 2070003 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 55374 | 38.4905 | -120.7137 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053435 | OH | Sus | 31640556 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1831101 | 0 | EPSS Ckt | N | 2023
74010 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1637 | 2023-03-28 | 1039 | 20230328 | 1902 | 2070348 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 17605 | 38.2444 | -120.512 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053500 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1831148 | 0 | EPSS Ckt | N | 2023
74011 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | FUSE | L7441 | 2023-03-28 | 1041 | 20230329 | 1034 | 2070527 | 1433 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1734 | 38.3873 | -120.6829 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0053747 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1831282 | 0 | EPSS Ckt | N | 2023
74019 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 2143 | 2023-03-28 | 1922 | 20230330 | 342 | 2071901 | 1940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 65235 | 38.2304 | -120.6004 | No | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken | 23-0053965 | OH | Sus | 31640705 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831445 | 0 | EPSS Ckt | N | 2023
74031 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 2023-03-30 | 1223 | 20230330 | 1244 | 2074362 | 21 | Distribution Circuit | Vegetation | Tree - grew into line | 335 | 7035 | 38.4069 | -120.6707 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0054999 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1831960 | 0 | EPSS Ckt | N | 2023 | N/A
74054 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | TRANSFORMER | 319921359543 | 2023-04-03 | 1850 | 20230404 | 10 | 2079271 | 320 | Transformer only | Vegetation | Tree - fell into line | 1 | 320 | 38.1356 | -120.5285 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0056704 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833068 | 0 | EPSS Ckt | N | 2023
74083 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | L3857 | 2023-04-07 | 623 | 20230407 | 814 | 2082336 | 109 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 17 | 1853 | 38.3497 | -120.6591 | No | Overcast;32-90 F |  |  | 23-0058354 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | No | No | 1834011 | 0 | EPSS Ckt | N | 2023
74092 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | FUSE | L7429 | 2023-04-07 | 1758 | 20230407 | 1907 | 2082877 | 69 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 6 | 414 | 38.3925 | -120.6767 | No | Partly Cloudy;32-90 F |  |  | 23-0058689 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834126 | 0 | EPSS Ckt | N | 2023
74098 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5339 | 2023-04-08 | 1706 | 20230408 | 2033 | 2083450 | 207 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1035 | 38.2159 | -120.5285 | No | Partly Cloudy;32-90 F |  |  | 23-0058811 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834263 | 0 | EPSS Ckt | N | 2023
74109 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 2121 | 2023-04-10 | 857 | 20230410 | 1516 | 2084210 | 379 | Distribution Circuit | 3rd Party | Vehicle | 91 | 13396 | 38.4725 | -120.5271 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0059069 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1834530 | 0 | EPSS Ckt | N | 2023
74111 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5533 | 2023-04-10 | 925 | 20230410 | 1017 | 2084181 | 52 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 156 | 38.1786 | -120.5682 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0058998 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834456 | 0 | EPSS Ckt | N | 2023
74135 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | 1363 | 2023-04-14 | 1219 | 20230414 | 1303 | 2088660 | 44 | Distribution Circuit | Equipment Failure/Involved | Overhead | 514 | 22616 | 38.2177 | -120.5523 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0061149 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1835884 | 0 | EPSS Ckt | N | 2023
74162 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319840569325 | 2023-04-20 | 920 | 20230420 | 1048 | 2093108 | 88 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 264 | 38.4039 | -120.5577 | No | Clear;32-90 F | Service conductor | Broken | 23-0062912 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837233 | 0 | EPSS Ckt | N | 2023
74179 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223933625884 | 2023-04-22 | 1628 | 20230422 | 1729 | 2094756 | 61 | Transformer only | Animal | Squirrel | 6 | 366 | 38.3692 | -120.629 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Burned/flashed | 23-0063782 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1837797 | 0 | EPSS Ckt | N | 2023
74190 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 2023-04-25 | 1307 | 20230425 | 1400 | 2096733 | 53 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 212 | 38.2674 | -120.5854 | No | Clear;32-90 F | Insulator | Broken | 23-0064527 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838438 | 0 | EPSS Ckt | N | 2023
74260 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319888561331 | 2023-05-02 | 1950 | 20230503 | 225 | 2103214 | 395 | Transformer only | Environmental/External | Lightning | 1 | 395 | 38.1844 | -120.5399 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0067384 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840286 | 0 | EPSS Ckt | N | 2023
74264 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320156561620 | 2023-05-03 | 835 | 20230503 | 1402 | 2103446 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 654 | 38.1922 | -120.4467 | No | Clear;32-90 F | Transformer | Broken | 23-0067712 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840538 | 0 | EPSS Ckt | N | 2023
74271 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320104562316 | 2023-05-03 | 1826 | 20230504 | 638 | 2104097 | 732 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 732 | 38.2112 | -120.4649 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 23-0067868 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1840599 | 0 | EPSS Ckt | N | 2023
74299 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJS 2/W/OF 319823862269 | 2023-05-08 | 1430 | 20230508 | 1855 | 2107542 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 265 | 38.2103 | -120.5626 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 23-0069550 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1841730 | 0 | EPSS Ckt | N | 2023
74309 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1771 | 2023-05-10 | 1435 | 20230510 | 1459 | 2109644 | 24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 144 | 38.2056 | -120.5728 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0070534 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842345 | 0 | EPSS Ckt | N | 2023
74336 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1429 | 2023-05-13 | 1920 | 20230513 | 2117 | 2111943 | 117 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 702 | 38.2059 | -120.5188 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0071604 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843054 | 0 | EPSS Ckt | N | 2023
74355 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-05-16 | 1706 | 20230517 | 818 | 2114369 | 912 | Distribution Circuit | Company Initiated | Personnel- company | 895 | 240938 | 38.1743 | -120.3834 | No | Clear;32-90 F | Recloser | Normal | 23-0072444 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843673 | 0 | EPSS Ckt | Y | 2023 | SGF AND DCD
74369 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1845 | 2023-05-18 | 1618 | 20230518 | 1853 | 2116337 | 155 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 775 | 38.2414 | -120.6485 | No | Clear;32-90 F |  |  | 23-0073270 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1844278 | 0 | EPSS Ckt | N | 2023
74413 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319864066640 | 2023-05-24 | 2018 | 20230524 | 2156 | 2120818 | 98 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 196 | 38.3319 | -120.5489 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0075320 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1845723 | 0 | EPSS Ckt | N | 2023
74422 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 2023-05-26 | 1429 | 20230526 | 1514 | 2122273 | 45 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 28080 | 38.364 | -120.6467 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0076168 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1846221 | 0 | EPSS Ckt | N | 2023 | ABC GRD
74437 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223842026742 | 2023-05-30 | 1145 | 20230530 | 1319 | 2123993 | 94 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 188 | 38.3931 | -120.6604 | No | Partly Cloudy;32-90 F | Service conductor | Broken | 23-0076782 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1846744 | 0 | EPSS Ckt | N | 2023
74470 | STOCKTON | MOTHER LODE | TIGER CREEK-0201 | 161380201 | RECLOSER | 320746 | 2023-06-06 | 1351 | 20230606 | 1752 | 2130724 | 241 | Distribution Circuit | Environmental/External | Lightning | 3 | 723 | 38.4495 | -120.4908 | No | Partly Cloudy;32-90 F | Recloser | Normal | 23-0079441 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848425 | 0 | EPSS Ckt | N | 2023 | B PH & GRD
74472 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5249 | 2023-06-06 | 1500 | 20230606 | 1513 | 2130722 | 13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 52 | 38.2754 | -120.5921 | No | Partly Cloudy;32-90 F |  |  | 23-0079488 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1848443 | 0 | EPSS Ckt | N | 2023
74499 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L3643 | 2023-06-09 | 917 | 20230609 | 1440 | 2133450 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1938 | 38.2655 | -120.5104 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 23-0080795 | OH | Sus | 45838172 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1849381 | 0 | EPSS Ckt | N | 2023
74501 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | TRANSFORMER | 224222730237 | 2023-06-09 | 1206 | 20230609 | 1301 | 2133610 | 55 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 55 | 38.485 | -120.5263 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0080827 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849397 | 0 | EPSS Ckt | N | 2023
74510 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223804226121 | 2023-06-11 | 1114 | 20230611 | 1202 | 2134614 | 48 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 48 | 38.3763 | -120.674 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0081274 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849715 | 0 | EPSS Ckt | N | 2023
74518 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223906826558 | 2023-06-14 | 122 | 20230614 | 347 | 2136506 | 145 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 435 | 38.3876 | -120.6381 | No | Partly Cloudy;32-90 F | Secondary | Deteriorated | 23-0082107 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850417 | 0 | EPSS Ckt | N | 2023
74527 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319748064590 | 2023-06-16 | 2239 | 20230617 | 105 | 2139093 | 146 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 146 | 38.2742 | -120.589 | No | Clear;32-90 F |  |  | 23-0083318 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1851238 | 0 | EPSS Ckt | N | 2023
74559 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | RECLOSER | 6014 | 2023-06-22 | 923 | 20230622 | 1058 | 2143029 | 95 | Distribution Circuit | Animal | Bird found | 806 | 72598 | 38.3157 | -120.7125 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0084593 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1852398 | 0 | EPSS Ckt | Y | 2023 | B & C
74561 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | TRANSFORMER | 223777026545 | 2023-06-22 | 1254 | 20230622 | 1337 | 2143203 | 43 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 43 | 38.388 | -120.683 | No | Partly Cloudy;32-90 F | Secondary | Broken | 23-0084699 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852457 | 0 | EPSS Ckt | N | 2023
74569 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-06-24 | 27 | 20230624 | 831 | 2144476 | 484 | Distribution Circuit | Equipment Failure/Involved | Underground | 895 | 433180 | 38.1743 | -120.3834 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0073777 | UG | Sus | 35279122 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852796 | 0 | EPSS Ckt | Y | 2023 | SGF
74573 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | RECLOSER | 7144 | 2023-06-24 | 845 | 20230624 | 2122 | s1852884 | 757 | Distribution Circuit | Equipment Failure/Involved | Underground | 895 | 267685 | 38.1743 | -120.3834 | No | Partly Cloudy;32-90 F | Conductor- Underground | Broken | 23-0073777 | UG | Sus | 35279122 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852884 | 0 | EPSS Ckt | Y | 2023 | B GRD
74589 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | TRANSFORMER | 224211330013 | 2023-06-27 | 1809 | 20230627 | 2320 | 2147274 | 311 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 622 | 38.481 | -120.5299 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0086310 | OH | Sus | 31653804 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1853541 | 0 | EPSS Ckt | N | 2023
74596 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | 319833562015 | 2023-06-28 | 1735 | 20230628 | 1910 | 2148309 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 251 | 38.2034 | -120.5584 | No | Clear;32-90 F | Other | Broken | 23-0086839 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853857 | 0 | EPSS Ckt | N | 2023
74624 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-07-01 | 1756 | 20230702 | 1406 | 2151143 | 937 | Distribution Circuit | Equipment Failure/Involved | Underground | 894 | 330162 | 38.1743 | -120.3834 | No | Clear-Heat Wave;Above 90 | Switch (UG) | Failed/Faulted | 23-0087976 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1854621 | 0 | EPSS Ckt | Y | 2023 | A GRD
74697 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-07-13 | 458 | 20230713 | 649 | 2161291 | 111 | Distribution Circuit | Company Initiated | Coordination failure | 895 | 99345 | 38.1743 | -120.3834 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0091589 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1856971 | 0 | EPSS Ckt | Y | 2023 | DCD- SGF
74701 | STOCKTON | MOTHER LODE | MARTELL-1101 | 163011101 | TRANSFORMER | 223558628857 | 2023-07-13 | 1647 | 20230714 | 230 | 2161911 | 583 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 1166 | 38.4524 | -120.7587 | No | Clear;Above 90 | Transformer (OH) | Broken- wire on ground | 23-0092057 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | Yes | No | 1857248 | 0 | EPSS Ckt | N | 2023
74702 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-07-13 | 1726 | 20230713 | 1801 | 2161942 | 35 | Distribution Circuit | Company Initiated | Coordination failure | 895 | 31325 | 38.1743 | -120.3834 | No | Clear;32-90 F | Recloser | Normal | 23-0092030 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857237 | 0 | EPSS Ckt | Y | 2023 | DCD
74711 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-07-14 | 2127 | 20230714 | 2158 | 2162970 | 31 | Distribution Circuit | Company Initiated | Coordination failure | 895 | 27745 | 38.1743 | -120.3834 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0092487 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857557 | 0 | EPSS Ckt | Y | 2023 | DCD & SGF
74740 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 1101/2 | 2023-07-19 | 744 | 20230719 | 845 | 2167444 | 61 | Distribution Circuit | Company Initiated | Personnel- company | 1102 | 64294 | 38.3311 | -120.6725 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0086272 | OH | Sus | 35268594 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1858657 | 0 | EPSS Ckt | Y | 2023 | SGF
74745 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320061257872 | 2023-07-20 | 1249 | 20230720 | 1927 | 2168939 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1194 | 38.089 | -120.4802 | No | Clear;Above 90 | Transformer | Failed/Faulted | 23-0094810 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1859139 | 0 | EPSS Ckt | N | 2023
74765 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319923566060 | 2023-07-24 | 904 | 20230724 | 1001 | 2172256 | 57 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 57 | 38.314 | -120.5275 | No | Clear;32-90 F | Bushing | Deteriorated | 23-0095833 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859944 | 0 | EPSS Ckt | N | 2023
74785 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320325260597 | 2023-07-27 | 945 | 20230727 | 1145 | 2175248 | 120 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 120 | 38.1647 | -120.3951 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0097493 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860952 | 0 | EPSS Ckt | N | 2023
74798 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-07-29 | 234 | 20230729 | 311 | 2176880 | 20 | Distribution Circuit | 3rd Party | Other | 2749 | 59190 | 38.1743 | -120.3834 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0098261 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861375 | 0 | EPSS Ckt | Y | 2023 | C & SGF
74800 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 320062068355 | 2023-07-29 | 1014 | 20230730 | 1950 | 2177067 | 2016 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2016 | 38.3768 | -120.4783 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0098341 | OH | Sus | 45905973 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1861480 | 0 | EPSS Ckt | N | 2023
74822 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320353261191 | 2023-08-02 | 900 | 20230802 | 1320 | 2180236 | 260 | Transformer only | 3rd Party | Gun Shot | 1 | 260 | 38.1801 | -120.3782 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0099444 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862338 | 0 | EPSS Ckt | N | 2023
74823 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223923826844 | 2023-08-02 | 1238 | 20230802 | 1259 | 2180668 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 42 | 38.3956 | -120.6321 | No | Clear;32-90 F | Secondary | Broken | 23-0099613 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1862492 | 0 | EPSS Ckt | N | 2023
74846 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2023-08-06 | 1155 | 20230806 | 1312 | 2183607 | 77 | Distribution Circuit | Animal | Squirrel | 691 | 51927 | 38.4151 | -120.6853 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0101008 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1863420 | 0 | EPSS Ckt | Y | 2023 | B C GRD
74855 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319908566760 | 2023-08-07 | 1148 | 20230807 | 1452 | 2184565 | 184 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 184 | 38.3334 | -120.5332 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0101255 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1863699 | 0 | EPSS Ckt | N | 2023
74858 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2023-08-07 | 1619 | 20230807 | 1748 | 2184913 | 89 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 691 | 39099 | 38.4151 | -120.6853 | No | Clear;Above 90 |  |  | 23-0101409 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863765 | 0 | EPSS Ckt | Y | 2023 | B- C
74886 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 2023-08-13 | 2346 | 20230814 | 1001 | 2189915 | 615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 914 | 522851 | 38.1832 | -120.3754 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103828 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865406 | 0 | EPSS Ckt | Y | 2023 | B PHASE INST
74900 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 2023-08-15 | 1134 | 20230815 | 1318 | 2191649 | 104 | Distribution Circuit | Company Initiated | Personnel- company | 1809 | 174746 | 38.1832 | -120.3754 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0104530 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1865909 | 0 | EPSS Ckt | Y | 2023 | DCD AND SGF
74914 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | TRANSFORMER | 224183829650 | 2023-08-16 | 1127 | 20230816 | 1150 | 2192835 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 69 | 38.4713 | -120.5394 | No | Partly Cloudy;32-90 F | Lightning Arrestor | Broken | 23-0105036 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866244 | 0 | EPSS Ckt | N | 2023
74929 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1635 | 2023-08-18 | 1505 | 20230818 | 1627 | 2195064 | 82 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 5904 | 38.2398 | -120.5143 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 23-0106189 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1866893 | 0 | EPSS Ckt | N | 2023
74930 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2023-08-18 | 1522 | 20230818 | 1544 | 2195115 | 22 | Distribution Circuit | Company Initiated | Coordination failure | 691 | 15202 | 38.4151 | -120.6853 | No | Clear;32-90 F | Customer Equipment | Normal | 23-0106223 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866904 | 0 | EPSS Ckt | Y | 2023 | SGF AND DCD
74969 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 2337 | 2023-08-22 | 2332 | 20230823 | 417 | 2199736 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 223 | 24246 | 38.1742 | -120.3895 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107835 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1868146 | 0 | EPSS Ckt | Y | 2023 | A & B PHASE
74980 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 2023-08-24 | 922 | 20230824 | 950 | 2201092 | 28 | Distribution Circuit | Company Initiated | Personnel- company | 1778 | 47534 | 38.4437 | -120.5088 | No | Clear;32-90 F | Regulator | Normal | 23-0108503 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1868627 | 0 | EPSS Ckt | Y | 2023 | A- C
74983 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2023-08-25 | 816 | 20230825 | 1437 | 2201895 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 374 | 109800 | 38.3633 | -120.6486 | No | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0108955 | OH | Sus | 31664814 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | Yes | No | 1868921 | 0 | EPSS Ckt | Y | 2023 | A & B
75002 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2023-08-29 | 1405 | 20230829 | 1427 | 2205136 | 22 | Distribution Circuit | Company Initiated | Coordination failure | 692 | 15224 | 38.4151 | -120.6853 | No | Clear;32-90 F | Recloser | Normal | 23-0110340 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869963 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
75003 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2023-08-29 | 1457 | 20230829 | 1513 | 2205189 | 16 | Distribution Circuit | Company Initiated | Coordination failure | 692 | 11072 | 38.4151 | -120.6853 | No | Clear;32-90 F | Recloser | Normal | 23-0110384 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869972 | 0 | EPSS Ckt | Y | 2023 | SGF & DCD
75016 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320408261526 | 2023-08-31 | 1010 | 20230831 | 1038 | 2206944 | 28 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 28 | 38.1896 | -120.359 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0111204 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1870527 | 0 | EPSS Ckt | N | 2023
75025 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-09-02 | 212 | 20230902 | 907 | 2208299 | 415 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 895 | 369917 | 38.1743 | -120.3834 | No | Overcast-Fog;32-90 F |  |  | 23-0112037 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1870895 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
75030 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-09-02 | 956 | 20230902 | 1009 | 2208578 | 13 | Distribution Circuit | Company Initiated | Coordination failure | 895 | 11635 | 38.1743 | -120.3834 | No | Overcast-Fog;32-90 F | Recloser | Normal | 23-0112096 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1870947 | 0 | EPSS Ckt | Y | 2023 | DCD
75031 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2023-09-02 | 1809 | 20230903 | 410 | 2208846 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 374 | 116340 | 38.3633 | -120.6486 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0112170 | OH | Sus | 31667424 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1870976 | 0 | EPSS Ckt | Y | 2023 | A- B
75037 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223819526126 | 2023-09-03 | 930 | 20230903 | 1136 | 2209050 | 126 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 252 | 38.3761 | -120.6689 | No | Overcast-Fog;32-90 F |  |  | 23-0112235 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1871048 | 0 | EPSS Ckt | N | 2023
75052 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 2023-09-06 | 1751 | 20230906 | 1759 | 2211223 | 8 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1586 | 10502 | 38.4437 | -120.5088 | No | Clear;32-90 F | Switch (OH) | Broken | 23-0103002 | OH | Sus | 31454134 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871686 | 0 | EPSS Ckt | Y | 2023 | NA
75059 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320104062260 | 2023-09-08 | 1601 | 20230908 | 2225 | 2212942 | 384 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1152 | 38.2097 | -120.4651 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114305 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872225 | 0 | EPSS Ckt | N | 2023
75061 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 2023-09-09 | 1228 | 20230909 | 1634 | 2213718 | 246 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 699 | 171954 | 38.1945 | -120.5846 | Yes | Clear;32-90 F |  |  | 23-0114454 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872400 | 0 | EPSS Ckt | Y | 2023 | A- B
75064 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 2023-09-10 | 809 | 20230910 | 1106 | 2214561 | 177 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 339 | 60003 | 38.4069 | -120.6707 | No | Clear;32-90 F |  |  | 23-0114632 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872580 | 0 | EPSS Ckt | Y | 2023 | A- B- 50RLY
75074 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-09-12 | 701 | 20230912 | 726 | 2216115 | 25 | Distribution Circuit | 3rd Party | Customer Equipment | 895 | 22375 | 38.1743 | -120.3834 | No | Clear;32-90 F | Relay | Normal | 23-0115303 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873150 | 0 | EPSS Ckt | Y | 2023 | SGF/DCD
75110 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | JUMPER | OJ'S 3 SPANS E/OF CGC# 223716026570 | 2023-09-20 | 809 | 20230920 | 1445 | 2222961 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 396 | 38.3894 | -120.7024 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0118571 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875378 | 0 | EPSS Ckt | N | 2023
75132 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319895862218 | 2023-09-25 | 1358 | 20230925 | 1515 | 2226736 | 77 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 77 | 38.2086 | -120.5374 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Deteriorated | 23-0120486 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1876639 | 0 | EPSS Ckt | N | 2023
75133 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | RECLOSER | 6014 | 2023-09-26 | 649 | 20230926 | 837 | 2227204 | 108 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 3996 | 38.3157 | -120.7125 | No | Overcast;32-90 F |  |  | 23-0120752 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1876764 | 0 | EPSS Ckt | Y | 2023 | A & B
75157 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L5223 | 2023-09-30 | 720 | 20230930 | 1142 | 2231355 | 262 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 786 | 38.2831 | -120.5047 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0122879 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1878138 | 0 | EPSS Ckt | N | 2023
75186 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 2023-10-07 | 439 | 20231007 | 912 | 2237298 | 273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 623 | 133499 | 38.364 | -120.6467 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0125668 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1880116 | 0 | EPSS Ckt | Y | 2023 | A- B - INST
75205 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-10-11 | 1306 | 20231011 | 1348 | 2240948 | 42 | Distribution Circuit | Company Initiated | Coordination failure | 895 | 37590 | 38.1743 | -120.3834 | No | Clear;32-90 F | Recloser | Normal | 23-0127061 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1881344 | 0 | EPSS Ckt | Y | 2023 | DCD
75220 | STOCKTON | MOTHER LODE | TIGER CREEK-0201 | 161380201 | RECLOSER | 320746 | 2023-10-13 | 836 | 20231013 | 1445 | 2242388 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1107 | 38.4495 | -120.4908 | No | Partly Cloudy;32-90 F | Other | Broken | 23-0127856 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1881810 | 0 | EPSS Ckt | N | 2023 | NONE
75225 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-10-14 | 1304 | 20231014 | 1526 | 2243405 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 895 | 127090 | 38.1743 | -120.3834 | No | Partly Cloudy;32-90 F |  |  | 23-0128308 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882176 | 0 | EPSS Ckt | Y | 2023 | DCD
75232 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 2023-10-17 | 924 | 20231017 | 1346 | 2245180 | 262 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 696 | 182352 | 38.1945 | -120.5846 | No | Clear;32-90 F |  |  | 23-0129044 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1882794 | 0 | EPSS Ckt | Y | 2023 | A- GRD
75235 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223798530475 | 2023-10-18 | 1342 | 20231018 | 1401 | 2246044 | 19 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 19 | 38.496 | -120.6741 | No | Clear;32-90 F | Secondary | Broken | 23-0129517 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1883123 | 0 | EPSS Ckt | N | 2023
75271 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 2023-10-26 | 420 | 20231026 | 936 | 2251998 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 143544 | 38.364 | -120.6467 | No | Overcast;32-90 F | Conductor- Overhead | Normal | 23-0132674 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885085 | 0 | EPSS Ckt | Y | 2023 | A&C INSTANT
75287 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2023-10-28 | 1743 | 20231029 | 906 | 2254425 | 923 | Distribution Circuit | Vegetation | Tree - branch fell on line | 894 | 821392 | 38.1743 | -120.3834 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0133597 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1885892 | 0 | EPSS Ckt | Y | 2023 | SGF- DCD
75310 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 2023-11-01 | 2307 | 20231102 | 321 | 2257888 | 254 | Distribution Circuit | 3rd Party | Vehicle | 1782 | 370846 | 38.4437 | -120.5088 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0134951 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | Yes | No | 1886999 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
75318 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320305059553 | 2023-11-03 | 818 | 20231103 | 1431 | 2259099 | 373 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1841 | 93665 | 38.1355 | -120.3945 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0135588 | OH | Sus | 31675050 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887538 | 0 | EPSS Ckt | Y | 2023
75320 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | L3873 | 2023-11-03 | 847 | 20231103 | 1016 | 2258907 | 89 | Distribution Circuit | Animal | Squirrel | 17 | 1543 | 38.3949 | -120.6452 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0135557 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887523 | 1 | EPSS Ckt | N | 2023
75323 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223881826709 | 2023-11-03 | 1120 | 20231103 | 1135 | s1887554 | 15 | Transformer only | Company Initiated | Other Circuits | 1 | 15 | 38.3918 | -120.6462 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0135557 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1887554 | 1 | EPSS Ckt | N | 2023
75341 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320070657603 | 2023-11-07 | 1359 | 20231107 | 1501 | 2262987 | 62 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 124 | 38.0833 | -120.4756 | No | Clear;32-90 F | Lightning Arrestor | Failed/Faulted | 23-0136829 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888624 | 0 | EPSS Ckt | N | 2023
75416 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | TRANSFORMER | 224212929800 | 2023-11-19 | 1131 | 20231119 | 1233 | 2273546 | 62 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 124 | 38.4753 | -120.5296 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0141087 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891758 | 0 | EPSS Ckt | N | 2023
75497 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 224198420066 | 2023-12-07 | 909 | 20231207 | 1028 | 2285970 | 79 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 79 | 38.4827 | -120.5341 | No | Clear;32-90 F |  |  | 23-0146169 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1895926 | 0 | EPSS Ckt | N | 2023
75567 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320066060096 | 2023-12-22 | 801 | 20231222 | 1423 | 2298150 | 382 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 764 | 38.151 | -120.4779 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0148575 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1899600 | 0 | EPSS Ckt | N | 2023
75604 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN @ CGC# 224209230010 | 2024-01-03 | 441 | 20240103 | 1300 | 2305725 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 681 | 29751 | 38.4812 | -120.5306 | No | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0006332 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | Yes | 1901213 | 0 | EPSS Ckt | N | 2024
75635 | STOCKTON | MOTHER LODE | VALLEY SPRINGS-1101 | 168891101 | TRANSFORMER | 319930762624 | 2024-01-10 | 2156 | 20240111 | 1115 | 2312432 | 799 | Transformer only | Vegetation | Tree - fell into line | 1 | 799 | 38.2184 | -120.5252 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken | 24-0009379 | OH | Sus | 46140997 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903131 | 0 | EPSS Ckt | N | 2024
75681 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 36676 | 2024-01-21 | 238 | 20240121 | 1158 | 2320255 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 48910 | 38.3724 | -120.5067 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0013046 | OH | Sus | 35525361 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1905317 | 0 | EPSS Ckt | N | 2024 | SGF
75700 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319974065364 | 2024-01-24 | 806 | 20240124 | 1644 | 2322885 | 518 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 518 | 38.295 | -120.5102 | No | Overcast-Fog;32-90 F | Transformer (OH) | Failed/Faulted | 24-0014487 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906083 | 0 | EPSS Ckt | N | 2024
75730 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2897 | 2024-01-31 | 1722 | 20240131 | 1857 | 2330099 | 95 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 1140 | 38.2121 | -120.5192 | No | Clear-Strong Winds;32-90 F |  |  | 24-0017597 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908013 | 0 | EPSS Ckt | N | 2024
75743 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2897 | 2024-01-31 | 1935 | 20240201 | 1317 | 2330358 | 1062 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 12744 | 38.2121 | -120.5192 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0017680 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908077 | 0 | EPSS Ckt | N | 2024
75976 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2897 | 2024-02-04 | 1943 | 20240205 | 125 | 2352977 | 342 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 4104 | 38.2121 | -120.5192 | Yes | Clear-Strong Winds;32-90 F |  |  | 24-0021395 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911229 | 0 | EPSS Ckt | N | 2024
75977 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2939 | 2024-02-04 | 1951 | 20240205 | 1957 | 2353157 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4338 | 38.2071 | -120.5372 | Yes | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021823 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1911569 | 0 | EPSS Ckt | N | 2024
75979 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRIP-SAVER | L1697 | 2024-02-04 | 1959 | 20240205 | 1820 | 2353343 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 77508 | 38.3793 | -120.638 | Yes | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021230 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1911058 | 1 | EPSS Ckt | N | 2024 | #1 TRIPPED
76054 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319633066345 | 2024-02-10 | 1357 | 20240210 | 1816 | 2372798 | 259 | Transformer only | Vegetation | Tree - fell into line | 1 | 259 | 38.322 | -120.6271 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0027453 | OH | Sus | 46189564 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915893 | 0 | EPSS Ckt | N | 2024
76079 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | JUMPER | OJ 2 W/OF CGC # 320124057245 | 2024-02-16 | 1415 | 20240216 | 1820 | 2378322 | 245 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 245 | 38.0737 | -120.4572 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0030017 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1917392 | 0 | EPSS Ckt | N | 2024
76122 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | SWITCH | 765817 | 2024-02-20 | 1648 | 20240220 | 2351 | 2383229 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4372 | 1797861 | 38.1753 | -120.3827 | No | Overcast;32-90 F | Insulator | Broken- wire on object | 24-0031308 | OH | Sus | 35532217 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1918479 | 0 | EPSS Ckt | N | 2024
76171 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 2024-03-02 | 2 | 20240302 | 1442 | 2394080 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 1781 | 619148 | 38.4437 | -120.5088 | No | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036613 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | Yes | No | 1921654 | 0 | EPSS Ckt | N | 2024 | A- B- C- TIME
76251 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 394499 | 2024-03-15 | 7 | 20240316 | 356 | 2405604 | 1669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 59622 | 38.2634 | -120.4874 | No | Clear-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0042533 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1925325 | 0 | EPSS Ckt | N | 2024
76284 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | OTHER | 1 PH WIRE DOWN 1 POLE SS OF R242 | 2024-03-20 | 416 | 20240320 | 1033 | 2409816 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 27802 | 38.3849 | -120.6936 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0044415 | OH | Sus | 46214024 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1926746 | 1 | EPSS Ckt | N | 2024
76294 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 985567 | 2024-03-22 | 2013 | 20240323 | 951 | 2412376 | 818 | Distribution Circuit | Environmental/External | Lightning | 17 | 5490 | 38.314 | -120.5459 | No | Clear-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 24-0045885 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927620 | 0 | EPSS Ckt | N | 2024
76302 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | FUSE | 767179 | 2024-03-22 | 2038 | 20240323 | 1032 | 2412395 | 834 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 19182 | 38.0281 | -120.4809 | No | Overcast-Rain-Lightning;32-90 F |  |  | 24-0045976 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927722 | 0 | EPSS Ckt | N | 2024
76313 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319523064930 | 2024-03-23 | 1238 | 20240323 | 1534 | 2412855 | 176 | Transformer only | Environmental/External | Lightning | 2 | 352 | 38.2831 | -120.6677 | No | Overcast;32-90 F | Transformer | Failed/Faulted | 24-0046041 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1927758 | 0 | EPSS Ckt | N | 2024
76315 | STOCKTON | MOTHER LODE | OLETA-1102 | 163541102 | FUSE | 782947 | 2024-03-23 | 1623 | 20240323 | 1834 | 2412977 | 131 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 13 | 1703 | 38.4868 | -120.7575 | No | Partly Cloudy-Fog;32-90 F |  |  | 24-0046085 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1927792 | 0 | EPSS Ckt | N | 2024
76355 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319490064935 | 2024-04-01 | 1651 | 20240401 | 2302 | 2420482 | 371 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 371 | 38.2832 | -120.6789 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0049409 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930036 | 0 | EPSS Ckt | N | 2024
76374 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2897 | 2024-04-04 | 1541 | 20240404 | 1703 | 2422896 | 82 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 12 | 984 | 38.2121 | -120.5192 | No | Overcast-Fog;32-90 F |  |  | 24-0051004 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1930934 | 0 | EPSS Ckt | N | 2024
76378 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 303856 | 2024-04-05 | 208 | 20240405 | 544 | 2423358 | 216 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 6288 | 38.4126 | -120.5523 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 24-0051106 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931032 | 0 | EPSS Ckt | N | 2024 | BC
76381 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | OTHER | WIRE DOWN 1 POLE N/OF CGC#320048357412 | 2024-04-05 | 357 | 20240405 | 1953 | 2423890 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3824 | 38.078 | -120.4835 | No | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051244 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931189 | 0 | EPSS Ckt | N | 2024
76383 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | FUSE | L2657 | 2024-04-05 | 357 | 20240405 | 1839 | 2424239 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 24654 | 38.0915 | -120.4711 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0051483 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | Yes | No | 1931297 | 0 | EPSS Ckt | N | 2024
76386 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRIP-SAVER | 1419 | 2024-04-05 | 415 | 20240406 | 1500 | 2423386 | 2085 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 158539 | 38.213 | -120.5589 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051542 | OH | Sus | 0 | CENTRAL VALLEY | APR | Three Phase Fault | 0 | No | Yes | No | 1931332 | 0 | EPSS Ckt | N | 2024 | ABC
76389 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L609 | 2024-04-05 | 553 | 20240405 | 1326 | 2423530 | 453 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 7701 | 38.299 | -120.5037 | No | Overcast-Fog-Snow;Below 32 F | Insulator | Broken- wire on ground | 24-0051204 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | Yes | 1931131 | 0 | EPSS Ckt | N | 2024
76408 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | TRANSFORMER | 223824627473 | 2024-04-07 | 213 | 20240407 | 2021 | 2425539 | 1088 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1088 | 38.4133 | -120.6662 | No | Overcast;32-90 F | Bushing | Broken | 24-0051886 | OH | Sus | 35542441 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931639 | 0 | EPSS Ckt | N | 2024
76422 | STOCKTON | MOTHER LODE | STANISLAUS-1702 | 162821702 | TRANSFORMER | 320070657603 | 2024-04-10 | 952 | 20240410 | 1510 | 2427752 | 318 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 636 | 38.0833 | -120.4756 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053049 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932505 | 0 | EPSS Ckt | N | 2024
76425 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | FUSE | L653 | 2024-04-10 | 2311 | 20240411 | 52 | 2428181 | 101 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 3 | 303 | 38.1381 | -120.4718 | No | Clear;32-90 F |  |  | 24-0053348 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932604 | 0 | EPSS Ckt | N | 2024
76431 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | SWITCH | L5733 | 2024-04-11 | 1703 | 20240411 | 1926 | 2428834 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 29601 | 38.1579 | -120.4789 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0053758 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932844 | 0 | EPSS Ckt | N | 2024
76444 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5253 | 2024-04-13 | 1506 | 20240414 | 30 | 2430774 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 564 | 38.2829 | -120.5818 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0054528 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1933391 | 0 | EPSS Ckt | N | 2024
76452 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 2024-04-15 | 1303 | 20240415 | 1612 | 2431981 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 180 | 34020 | 38.4069 | -120.6707 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0054913 | OH | Sus | 35276857 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933828 | 0 | EPSS Ckt | N | 2024 | N/A
76458 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 224144629436 | 2024-04-16 | 1530 | 20240417 | 10 | 2432871 | 520 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1040 | 38.4656 | -120.5535 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 24-0055600 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1934210 | 0 | EPSS Ckt | N | 2024
76470 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | JUMPER | BURNT OPEN JUMPER @ CGC 320238859231 | 2024-04-18 | 1700 | 20240418 | 2218 | 2434359 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 2988 | 38.1272 | -120.4175 | No | Partly Cloudy;32-90 F | Jumper | Broken | 24-0056605 | OH | Sus | 46230936 | CENTRAL VALLEY | APR | Open Circuit | 0 | No | No | No | 1934797 | 0 | EPSS Ckt | N | 2024
76486 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319860065900 | 2024-04-22 | 1151 | 20240422 | 1653 | 2436614 | 302 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 302 | 38.3097 | -120.5499 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0057655 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1935572 | 0 | EPSS Ckt | N | 2024
76499 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | JUMPER | FB 2 S/OF CGC# 320157068830 | 2024-04-25 | 1302 | 20240425 | 1530 | 2438988 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 740 | 38.3892 | -120.4457 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 24-0058914 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936441 | 0 | EPSS Ckt | N | 2024
76503 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 320205870809 | 2024-04-26 | 1303 | 20240426 | 1344 | 2439834 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 164 | 38.4446 | -120.4293 | No | Overcast-Drizzle;32-90 F | Secondary | Broken | 24-0059327 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1936737 | 0 | EPSS Ckt | N | 2024
76507 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 837804 | 2024-04-26 | 1906 | 20240427 | 658 | 2440183 | 712 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 93576 | 38.2857 | -120.5082 | No | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0059509 | OH | Sus | 0 | CENTRAL VALLEY | APR | Multi-Fault | 0 | No | Yes | No | 1936823 | 0 | EPSS Ckt | N | 2024 | ABC- GROUND- SGF- TIME OC
76508 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320106762295 | 2024-04-26 | 1913 | 20240427 | 210 | 2440192 | 417 | Transformer only | Environmental/External | Lightning | 6 | 2502 | 38.2107 | -120.4641 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059534 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936842 | 0 | EPSS Ckt | N | 2024
76509 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320106862258 | 2024-04-26 | 1913 | 20240427 | 100 | 2440193 | 347 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 694 | 38.2096 | -120.4641 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059538 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936847 | 0 | EPSS Ckt | N | 2024
76511 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 1839 | 2024-04-26 | 1938 | 20240427 | 305 | 2440210 | 442 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 21 | 9282 | 38.3939 | -120.5675 | No | Partly Cloudy-Lightning;32-90 F |  |  | 24-0059573 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1936887 | 0 | EPSS Ckt | N | 2024
76516 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319872564910 | 2024-04-27 | 208 | 20240427 | 1246 | 2440350 | 638 | Transformer only | Environmental/External | Lightning | 1 | 638 | 38.2828 | -120.5422 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059602 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936952 | 0 | EPSS Ckt | N | 2024
76517 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319875065038 | 2024-04-27 | 504 | 20240427 | 1329 | 2440368 | 505 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1010 | 38.287 | -120.541 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0059606 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936955 | 0 | EPSS Ckt | N | 2024
76518 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319868064910 | 2024-04-27 | 928 | 20240427 | 1417 | 2440390 | 289 | Transformer only | Environmental/External | Lightning | 1 | 289 | 38.2829 | -120.5436 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059605 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1936954 | 0 | EPSS Ckt | N | 2024
76530 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | FUSE | 1443 | 2024-04-29 | 1535 | 20240429 | 1720 | 2441936 | 105 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1365 | 38.3635 | -120.7255 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0060152 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1937404 | 0 | EPSS Ckt | N | 2024
76558 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 2024-05-04 | 1851 | 20240504 | 2031 | 2446129 | 100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 21 | 2100 | 38.2085 | -120.3677 | No | Clear;Below 32 F |  |  | 24-0062225 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1939001 | 0 | EPSS Ckt | N | 2024
76578 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | JUMPER | OJ 1P W/OF 86883 | 2024-05-08 | 1100 | 20240508 | 1715 | 2448460 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2625 | 38.4449 | -120.4289 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0063445 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939918 | 0 | EPSS Ckt | N | 2024
76607 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1801 | 2024-05-13 | 2123 | 20240514 | 1503 | 2453124 | 1060 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 16934 | 38.1675 | -120.5714 | No | Partly Cloudy;32-90 F | Fuse | Broken | 24-0065627 | OH | Sus | 31694191 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1941421 | 0 | EPSS Ckt | N | 2024
76612 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | TRANSFORMER | 224150530027 | 2024-05-14 | 1805 | 20240514 | 1858 | 2453836 | 53 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 53 | 38.4814 | -120.5511 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0066018 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941660 | 0 | EPSS Ckt | N | 2024
76613 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | TRANSFORMER | 223832227251 | 2024-05-14 | 2018 | 20240514 | 2108 | 2453915 | 50 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 150 | 38.4068 | -120.6636 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0066043 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1941677 | 0 | EPSS Ckt | N | 2024
76617 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223882526775 | 2024-05-16 | 1417 | 20240516 | 1447 | 2460765 | 30 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 90 | 38.3936 | -120.6461 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0066888 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942111 | 0 | EPSS Ckt | N | 2024
76618 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | TRANSFORMER | 223923626051 | 2024-05-16 | 1428 | 20240516 | 1600 | 2460778 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 276 | 38.3738 | -120.6324 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0066897 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942118 | 0 | EPSS Ckt | N | 2024
76639 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | SWITCH | L5835 | 2024-05-20 | 932 | 20240520 | 953 | 2463103 | 21 | Distribution Circuit | Animal | Bird found | 2 | 42 | 38.022 | -120.5272 | No | Clear;32-90 F | Pole-Wood | Normal | 24-0067796 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1942855 | 0 | EPSS Ckt | N | 2024
76649 | STOCKTON | MOTHER LODE | WEST POINT-1101 | 163201101 | JUMPER | OJ 2 POLES NE OF CGC#224202130003 | 2024-05-21 | 1910 | 20240521 | 2350 | 2464577 | 280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1960 | 38.4813 | -120.5316 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0068513 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943265 | 0 | EPSS Ckt | N | 2024
76721 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3659 | 2024-06-03 | 644 | 20240603 | 845 | 2473636 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 26 | 3146 | 38.1955 | -120.5699 | No | Partly Cloudy;32-90 F |  |  | 24-0072442 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1946003 | 0 | EPSS Ckt | N | 2024
76731 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320089557615 | 2024-06-04 | 1505 | 20240604 | 1605 | 2475257 | 60 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 120 | 38.0834 | -120.471 | No | Clear;32-90 F |  |  | 24-0073230 | OH | Sus | 0 | CENTRAL VALLEY | JUN | None | 0 | No | No | No | 1946528 | 0 | EPSS Ckt | N | 2024
76742 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 2024-06-05 | 1319 | 20240605 | 1455 | 2476293 | 96 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2016 | 38.2085 | -120.3677 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0073639 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946854 | 0 | EPSS Ckt | N | 2024
76745 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 862450 | 2024-06-05 | 1822 | 20240606 | 802 | 2476656 | 820 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 272240 | 38.1369 | -120.3706 | No | Clear;32-90 F |  |  | 24-0073792 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1946922 | 0 | EPSS Ckt | Y | 2024 | G INST
76758 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 224208129942 | 2024-06-06 | 1419 | 20240606 | 1852 | 2477983 | 273 | Transformer only | Vegetation | Tree - fell into line | 1 | 273 | 38.4791 | -120.5309 | No | Clear;Above 90 | Transformer | Failed/Faulted | 24-0074326 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947284 | 0 | EPSS Ckt | N | 2024
76779 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2024-06-08 | 433 | 20240608 | 1240 | 2479865 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 693 | 96123 | 38.4151 | -120.6853 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0074916 | OH | Sus | 31696506 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | Yes | No | 1947669 | 0 | EPSS Ckt | Y | 2024 | B- C- SGF
76780 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 2024-06-08 | 713 | 20240608 | 1242 | s1948074 | 329 | Distribution Circuit | 3rd Party | Customer Equipment | 678 | 221808 | 38.4151 | -120.6853 | No | Clear;32-90 F | Customer Equipment | Normal | 24-0075271 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948074 | 0 | EPSS Ckt | Y | 2024 | SGF/DCD
76796 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 77229 | 2024-06-11 | 1126 | 20240611 | 1519 | 2482225 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2330 | 38.3717 | -120.508 | No | Clear;32-90 F | Conductor- Overhead | Deteriorated | 24-0075739 | OH | Sus | 46262131 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948437 | 0 | EPSS Ckt | N | 2024
76807 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | FUSE | 64129 | 2024-06-12 | 2050 | 20240613 | 1042 | 2484048 | 832 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2048 | 38.0272 | -120.48 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076493 | OH | Sus | 35560304 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1948883 | 1 | EPSS Ckt | N | 2024
76812 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OPEN JUMPERS AT TAKE OFF POLE | 2024-06-13 | 1509 | 20240613 | 1817 | 2484849 | 188 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 376 | 38.1475 | -120.584 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0076901 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949153 | 0 | EPSS Ckt | N | 2024
76888 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 100000077100 | 2024-06-27 | 859 | 20240627 | 2024 | 2497747 | 685 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 685 | 38.1768 | -120.4424 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081535 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952575 | 0 | EPSS Ckt | N | 2024
76896 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 862450 | 2024-06-28 | 1813 | 20240628 | 1822 | 2498832 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 330 | 2970 | 38.1369 | -120.3706 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0081963 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952900 | 0 | EPSS Ckt | N | 2024 | GRD INST OC
76902 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | BROKEN WIRE 4 SPANS N/OF CGC# 319776563830 | 2024-06-29 | 1123 | 20240629 | 1635 | 2499286 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 220 | 28177 | 38.2563 | -120.5792 | No | Clear;32-90 F | Conductor- Overhead | Broken | 24-0082054 | OH | Sus | 46270256 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1952989 | 0 | EPSS Ckt | N | 2024
76946 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319840569325 | 2024-07-03 | 1503 | 20240703 | 1921 | 2503876 | 258 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 516 | 38.4039 | -120.5577 | No | Heat Wave-Clear;Above 90 | Transformer | Failed/Faulted | 24-0083681 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1953939 | 0 | EPSS Ckt | N | 2024
76991 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2024-07-07 | 1600 | 20240707 | 1707 | 2509082 | 67 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 375 | 25125 | 38.3633 | -120.6486 | No | Clear-Heat Wave;Above 90 |  |  | 24-0084901 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1954767 | 0 | EPSS Ckt | Y | 2024 | AC
77017 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 224204429637 | 2024-07-11 | 1824 | 20240711 | 2252 | 2514265 | 268 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 804 | 38.4708 | -120.5326 | No | Clear-Heat Wave;Above 90 | Other | Leaking | 24-0086941 | OH | Sus | 46278823 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956028 | 0 | EPSS Ckt | N | 2024
77051 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319764161730 | 2024-07-19 | 1225 | 20240719 | 1241 | 2521103 | 16 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 16 | 38.1944 | -120.583 | No | Clear;Above 90 | Secondary | Broken | 24-0089750 | OH | Sus | 0 | CENTRAL VALLEY | JUL | None | 0 | No | No | No | 1957947 | 0 | EPSS Ckt | N | 2024
77067 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | RECLOSER | 6014 | 2024-07-21 | 1008 | 20240721 | 1237 | 2522377 | 149 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 38 | 5662 | 38.3157 | -120.7125 | No | Clear;32-90 F |  |  | 24-0090171 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1958242 | 0 | EPSS Ckt | Y | 2024 | B & C
77101 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | JUMPER | FB LD SIDE OF CGC # 223772026250 | 2024-07-26 | 810 | 20240726 | 1256 | 2527226 | 286 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1716 | 38.3798 | -120.6854 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0092282 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959654 | 0 | EPSS Ckt | N | 2024
77150 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | L2927 | 2024-08-02 | 1303 | 20240802 | 1558 | 2533060 | 175 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 8575 | 38.4632 | -120.6556 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0095215 | OH | Sus | 31703257 | CENTRAL VALLEY | AUG | Force Out | 0 | No | Yes | Yes | 1961619 | 0 | EPSS Ckt | N | 2024
77177 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJ 1P N/OF L5795 | 2024-08-08 | 1031 | 20240808 | 1201 | 2537604 | 90 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 90 | 38.3312 | -120.6254 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0097184 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963003 | 0 | EPSS Ckt | N | 2024
77208 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2024-08-18 | 2105 | 20240819 | 906 | 2544945 | 721 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 894 | 119790 | 38.1743 | -120.3834 | No | Clear;32-90 F |  |  | 24-0100437 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1965128 | 0 | EPSS Ckt | Y | 2024 | A- GRD
77263 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | JUMPER | OJS 1 S/OF CCGC 319849769661 | 2024-08-30 | 1248 | 20240830 | 1451 | 2555980 | 123 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 246 | 38.4125 | -120.5529 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105344 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1968540 | 0 | EPSS Ckt | N | 2024
77267 | STOCKTON | MOTHER LODE | FROGTOWN-1702 | 163451702 | FUSE | 767179 | 2024-08-31 | 1455 | 20240831 | 1722 | 2556575 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 22 | 3234 | 38.0281 | -120.4809 | No | Clear;Above 90 |  |  | 24-0105618 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968670 | 0 | EPSS Ckt | N | 2024
77293 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 7144 | 2024-09-05 | 1654 | 20240905 | 1700 | 2560550 | 6 | Distribution Circuit | Company Initiated | Personnel- company | 894 | 5364 | 38.1743 | -120.3834 | No | Clear;Above 90 | Recloser | Normal | 24-0107544 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969809 | 0 | EPSS Ckt | Y | 2024 | DCD
77295 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 862450 | 2024-09-06 | 641 | 20240906 | 1109 | 2560754 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 332 | 80500 | 38.1369 | -120.3706 | No | Clear;32-90 F |  |  | 24-0107655 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1969869 | 0 | EPSS Ckt | Y | 2024 | AC PH INST
77302 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | JUMPER | OJS 1 E/OF CGC 223845626752 | 2024-09-07 | 1206 | 20240907 | 1518 | 2562005 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 576 | 38.3934 | -120.6586 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0108238 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1970276 | 0 | EPSS Ckt | N | 2024
77314 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2024-09-10 | 38 | 20240910 | 814 | 2564015 | 456 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 375 | 105825 | 38.3633 | -120.6486 | No | Clear;32-90 F |  |  | 24-0108962 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1970751 | 0 | EPSS Ckt | Y | 2024 | A- C INST OC
77322 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | RECLOSER | 862450 | 2024-09-11 | 1003 | 20240911 | 1401 | 2565348 | 238 | Distribution Circuit | Company Initiated | Contact with High Voltage- company | 332 | 48716 | 38.1369 | -120.3706 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0109600 | OH | Sus | 31708112 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1971297 | 0 | EPSS Ckt | Y | 2024 | SGF
77327 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJ 1 E/OF 319712560400 | 2024-09-11 | 1753 | 20240911 | 2150 | 2565898 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 5709 | 38.1586 | -120.5998 | No | Clear;32-90 F | Jumper | Normal | 24-0109975 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Open Circuit | 0 | No | No | No | 1971441 | 1 | EPSS Ckt | N | 2024
77367 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | FUSE | 1065 | 2024-09-18 | 1545 | 20240918 | 1759 | 2571829 | 134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 2010 | 38.3787 | -120.6973 | No | Overcast;32-90 F | Pole-Wood | Broken | 24-0112654 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1973338 | 0 | EPSS Ckt | N | 2024
77375 | STOCKTON | MOTHER LODE | ELECTRA-1102 | 162161102 | RECLOSER | 1102/2 | 2024-09-20 | 1934 | 20240921 | 856 | 2573749 | 802 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 702 | 113233 | 38.3311 | -120.6726 | No | Clear;32-90 F |  |  | 24-0113887 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1973954 | 0 | EPSS Ckt | Y | 2024 | AB
77393 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2024-09-25 | 737 | 20240925 | 1111 | 2577012 | 214 | Distribution Circuit | Animal | Squirrel | 375 | 80250 | 38.3633 | -120.6486 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0115226 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1975056 | 0 | EPSS Ckt | Y | 2024 | A-C- INST OC
77479 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 2024-10-11 | 528 | 20241011 | 1550 | 2591978 | 622 | Distribution Circuit | Animal | Squirrel | 623 | 43402 | 38.364 | -120.6467 | No | Clear;32-90 F | Transformer (OH) | Normal | 24-0122047 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1979639 | 0 | EPSS Ckt | Y | 2024 | A & B
77491 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 2024-10-14 | 734 | 20241014 | 754 | 2593902 | 20 | Distribution Circuit | Company Initiated | Personnel- company | 302 | 6040 | 38.4069 | -120.6707 | No | Clear;32-90 F | Fuse | Normal | 24-0122776 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1980201 | 0 | EPSS Ckt | Y | 2024 | SGF
77512 | STOCKTON | MOTHER LODE | FROGTOWN-1701 | 163451701 | TRANSFORMER | 320116560925 | 2024-10-17 | 1358 | 20241018 | 146 | 2597333 | 708 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 708 | 38.1736 | -120.4601 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0124778 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1981500 | 0 | EPSS Ckt | N | 2024
77517 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | TRANSFORMER | 319950065750 | 2024-10-18 | 1714 | 20241018 | 1924 | 2598909 | 130 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 130 | 38.3058 | -120.5186 | No | Clear;32-90 F |  |  | 24-0125276 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1981869 | 0 | EPSS Ckt | N | 2024
77522 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L3285 | 2024-10-19 | 1822 | 20241019 | 2028 | 2599556 | 126 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 504 | 38.2531 | -120.5195 | No | Clear;32-90 F |  |  | 24-0125481 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1982041 | 0 | EPSS Ckt | N | 2024
77546 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 2024-10-26 | 1052 | 20241026 | 1429 | 2604789 | 217 | Distribution Circuit | Animal | Bird found | 375 | 59808 | 38.3633 | -120.6486 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128160 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983767 | 0 | EPSS Ckt | Y | 2024 | A & C
77558 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | FUSE | 286833 | 2024-10-28 | 1412 | 20241028 | 1425 | 2606374 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 39 | 507 | 38.4727 | -120.6261 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0116513 | OH | Sus | 35555032 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984210 | 0 | EPSS Ckt | N | 2024
77562 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 1425 | 2024-10-29 | 801 | 20241029 | 1055 | 2606912 | 174 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 49 | 8526 | 38.2708 | -120.4943 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128924 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1984495 | 0 | EPSS Ckt | N | 2024
77564 | STOCKTON | MOTHER LODE | OLETA-1102 | 163541102 | RECLOSER | 4088 | 2024-10-29 | 1012 | 20241029 | 1028 | 2607185 | 16 | Distribution Circuit | Company Initiated | Personnel- company | 38 | 608 | 38.4904 | -120.7135 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0128930 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1984501 | 0 | EPSS Ckt | Y | 2024 | C
77757 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 550341 | 2024-11-28 | 1646 | 20241129 | 44 | 2639947 | 478 | Distribution Circuit | 3rd Party | Vehicle | 59 | 13670 | 38.3345 | -120.5331 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0141234 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1993280 | 0 | EPSS Ckt | N | 2024
77790 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | JUMPER | CUST MOVED TO T281751 | 2024-12-04 | 2229 | 20241205 | 1112 | 2644316 | 763 | Transformer only | Equipment Failure/Involved | Underground | 2 | 1526 | 38.4155 | -120.6855 | No | Clear;32-90 F | Transformer (UG) | Failed/Faulted | 24-0142754 | UG | Sus | 35396762 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1994555 | 0 | EPSS Ckt | N | 2024
77797 | STOCKTON | MOTHER LODE | MARTELL-1101 | 163011101 | SWITCH | 405091 | 2024-12-05 | 2225 | 20241205 | 2238 | 2645487 | 13 | Distribution Circuit | Company Initiated | Return Circuit Normal | 3 | 39 | 38.4152 | -120.6866 | No | Clear;32-90 F | Conductor- Underground | Normal | 24-0133317 | UG | Sus | 35396762 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1994937 | 0 | EPSS Ckt | N | 2024
77824 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | TRANSFORMER | 319912562060 | 2024-12-13 | 918 | 20241213 | 1335 | 2651639 | 257 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 257 | 38.204 | -120.5312 | No | Overcast-Fog-Drizzle;32-90 F | Transformer (OH) | Burned/flashed | 24-0144883 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1997180 | 0 | EPSS Ckt | N | 2024
77845 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3219 | 2024-12-14 | 651 | 20241215 | 854 | 2653749 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12504 | 38.2385 | -120.5817 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0145249 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1997559 | 0 | EPSS Ckt | N | 2024
77855 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | 1093 | 2024-12-14 | 723 | 20241215 | 1547 | 2660374 | 1944 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27830 | 38.3498 | -120.549 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145298 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998331 | 0 | EPSS Ckt | N | 2024
77862 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | FUSE | L1641 | 2024-12-14 | 727 | 20241214 | 2010 | 2658192 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 95375 | 38.2679 | -120.5026 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | No | 1997881 | 0 | EPSS Ckt | N | 2024
77865 | STOCKTON | MOTHER LODE | WEST POINT-1102 | 163201102 | RECLOSER | 837804 | 2024-12-14 | 727 | 20241214 | 2252 | 2659825 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 103424 | 38.2857 | -120.5082 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | No | 1998186 | 0 | EPSS Ckt | N | 2024 | NONE
77875 | STOCKTON | MOTHER LODE | PINE GROVE-1102 | 163751102 | JUMPER | OJ 2/W/OF CGC# 223717030655 | 2024-12-14 | 756 | 20241214 | 1826 | 2659155 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5670 | 38.5016 | -120.7041 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145217 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998033 | 0 | EPSS Ckt | N | 2024
77881 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320410961845 | 2024-12-14 | 815 | 20241215 | 1535 | 2661381 | 1880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3760 | 38.1985 | -120.3583 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Secondary | Broken- wire on ground | 24-0146235 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998606 | 0 | EPSS Ckt | N | 2024
77890 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 2024-12-14 | 826 | 20241215 | 852 | 2657826 | 1466 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 462 | 665224 | 38.1945 | -120.5846 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145279 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1997827 | 0 | EPSS Ckt | N | 2024 | SGF
77891 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | L3467 | 2024-12-14 | 826 | 20241214 | 1704 | 2658567 | 518 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 171 | 88578 | 38.1943 | -120.5842 | Yes | Overcast-Rain-Strong Winds;32-90 F |  |  | 24-0145279 | OH | Sus | 0 | CENTRAL VALLEY | DEC | None | 0 | No | No | No | 1997933 | 0 | EPSS Ckt | N | 2024
77892 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 2024-12-14 | 826 | 20241215 | 1505 | 2660302 | 1839 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5517 | 38.2674 | -120.5854 | Yes | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken | 24-0145279 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998315 | 0 | EPSS Ckt | N | 2024
77903 | STOCKTON | MOTHER LODE | ELECTRA-1101 | 162161101 | RECLOSER | 1101/2 | 2024-12-14 | 832 | 20241214 | 1553 | 2655432 | 441 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1043 | 436023 | 38.3311 | -120.6725 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145310 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1997623 | 0 | EPSS Ckt | N | 2024 | ABC GRD TIME
77911 | STOCKTON | MOTHER LODE | STANISLAUS-1701 | 162821701 | FUSE | 1681 | 2024-12-14 | 904 | 20241215 | 1535 | 2660356 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38451 | 38.1989 | -120.3646 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146093 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | Yes | No | 1998436 | 0 | EPSS Ckt | N | 2024
77945 | STOCKTON | MOTHER LODE | CALAVERAS CEMENT-1101 | 162211101 | OTHER | WIRE DOWN 2/E/OF L2201 | 2024-12-15 | 854 | 20241215 | 1920 | 2661336 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 674 | 16166 | 38.249 | -120.6179 | No | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146227 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1998588 | 0 | EPSS Ckt | N | 2024
77968 | STOCKTON | MOTHER LODE | PINE GROVE-1101 | 163751101 | FUSE | L6371 | 2024-12-18 | 810 | 20241218 | 1452 | 2664767 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4422 | 38.3887 | -120.6813 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 24-0137706 | OH | Sus | 35402643 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999421 | 0 | EPSS Ckt | N | 2024
78031 | YOSEMITE | STANISLAUS | PEORIA 1705 | 163781705 | TRANSFORMER | 320305050250 | 2023-01-01 | 941 | 20230101 | 1247 | 1908154 | 186 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 372 | 37.8799 | -120.3954 | No | Clear;32-90 F | Jumper | Broken | 23-0004375 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1794969 | 0 | EPSS Ckt | N | 2023
78042 | YOSEMITE | STANISLAUS | CURTIS 1703 | 163351703 | TRANSFORMER | 320589050680 | 2023-01-02 | 1909 | 20230103 | 944 | 1910554 | 875 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 1750 | 37.891 | -120.2972 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0004857 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1795462 | 0 | EPSS Ckt | N | 2023
78050 | YOSEMITE | STANISLAUS | MIWUK 1701 | 163661701 | RECLOSER | 11800 | 2023-01-04 | 1522 | 20230104 | 1556 | 1914779 | 34 | Distribution Circuit | Vegetation | Tree - branch fell on line | 683 | 23222 | 38.0243 | -120.2213 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0006121 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1796443 | 0 | EPSS Ckt | N | 2023 | A & B
78059 | YOSEMITE | YOSEMITE | COARSEGOLD 2104 | 254432104 | FUSE | 10557 | 2023-01-04 | 2115 | 20230105 | 42 | 1918783 | 207 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 5 | 1035 | 37.2799 | -119.6664 | Yes | Clear;32-90F |  |  | 23-0006872 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797173 | 0 | EPSS Ckt | N | 2023
78064 | YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | OCB | 1701/2 | 2023-01-04 | 2140 | 20230105 | 738 | 1919033 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 2176 | 1196055 | 38.1401 | -120.3697 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006702 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797003 | 0 | EPSS Ckt | N | 2023 | PH TIME OC
78065 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2023-01-04 | 2148 | 20230105 | 726 | 1919077 | 578 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 40 | 23120 | 37.9718 | -120.2261 | Yes | Clear;32-90F |  |  | 23-0007034 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797334 | 0 | EPSS Ckt | N | 2023
78078 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2153 | 2023-01-04 | 2216 | 20230105 | 320 | 1919323 | 304 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 11856 | 37.9491 | -120.2657 | Yes | Clear;32-90F |  |  | 23-0006964 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1797267 | 0 | EPSS Ckt | N | 2023
78090 | YOSEMITE | YOSEMITE | BEAR VALLEY 2101 | 252192101 | RECLOSER | 90550 | 2023-01-04 | 2342 | 20230106 | 1413 | 1919862 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 95040 | 37.5151 | -120.052 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006883 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797183 | 0 | EPSS Ckt | N | 2023 | SGF
78101 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322444028370 | 2023-01-05 | 543 | 20230105 | 1504 | 1920665 | 561 | Transformer only | Equipment Failure/Involved | Electrical Overload | 1 | 561 | 37.2773 | -119.6621 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0007132 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1797418 | 0 | EPSS Ckt | N | 2023
78104 | YOSEMITE | YOSEMITE | MARIPOSA 2102 | 254452102 | FUSE | 10317 | 2023-01-05 | 653 | 20230105 | 2000 | 1920796 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 21458 | 37.4653 | -119.7357 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0007187 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1797467 | 1 | EPSS Ckt | N | 2023
78119 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23937 | 2023-01-05 | 1424 | 20230106 | 1443 | 1922708 | 1459 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2918 | 37.7145 | -120.1145 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0007563 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1797776 | 0 | EPSS Ckt | N | 2023
78180 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2023-01-07 | 2251 | 20230108 | 333 | 1928589 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 24534 | 37.7148 | -120.0964 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0009784 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1799620 | 0 | EPSS Ckt | N | 2023
78203 | YOSEMITE | STANISLAUS | MIWUK 1702 | 163661702 | RECLOSER | 1808 | 2023-01-08 | 31 | 20230109 | 1254 | 1931025 | 2183 | Distribution Circuit | Vegetation | Tree - fell into line | 272 | 362083 | 38.03 | -120.2447 | Yes | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0009574 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1799406 | 0 | EPSS Ckt | N | 2023 | B & C
78204 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1217 | 2023-01-08 | 31 | 20230110 | 1145 | 1931007 | 3554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 62269 | 38.0469 | -120.2017 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010444 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1800288 | 0 | EPSS Ckt | N | 2023
78210 | YOSEMITE | YOSEMITE | MARIPOSA 2101 | 254452101 | FUSE | 23856 | 2023-01-08 | 142 | 20230108 | 755 | 1931827 | 373 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 90 | 33570 | 37.496 | -119.9755 | Yes | Clear;32-90F |  |  | 23-0009873 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1799724 | 0 | EPSS Ckt | N | 2023
78213 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2023-01-08 | 209 | 20230109 | 1453 | 1931995 | 2204 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 88160 | 37.9718 | -120.2261 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010270 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1800119 | 0 | EPSS Ckt | N | 2023
78218 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | OTHER | WIRE DOWN 1 E/OF 27331 | 2023-01-08 | 454 | 20230109 | 1508 | 1934232 | 2054 | Distribution Circuit | Vegetation | Tree - fell into line | 606 | 1151622 | 37.8323 | -120.2093 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010362 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1800210 | 0 | EPSS Ckt | N | 2023
78229 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | MTR#1006384740 | 2023-01-08 | 1017 | 20230109 | 1055 | 1933084 | 1478 | Transformer only | Environmental/External | Water | 1 | 1478 | 37.7207 | -120.1169 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0010068 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1799912 | 0 | EPSS Ckt | N | 2023
78232 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | JUMPER | WIRE DOWN HOT SS/OF CGC# 320867040230 | 2023-01-08 | 1101 | 20230108 | 1815 | 1933237 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 258 | 1462 | 37.6049 | -120.197 | Yes | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0010219 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | Yes | 1800070 | 0 | EPSS Ckt | N | 2023
78272 | YOSEMITE | YOSEMITE | INDIAN FLAT 1104 | 252691104 | FUSE | 26947 | 2023-01-09 | 934 | 20230111 | 1308 | 1937328 | 3094 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 46410 | 37.6611 | -119.8543 | Yes | Clear;32-90F | Crossarm- Wood | Broken | 23-0011420 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801183 | 0 | EPSS Ckt | N | 2023
78276 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10313 | 2023-01-09 | 1029 | 20230109 | 1301 | 1937635 | 152 | Distribution Circuit | Vegetation | Tree - grew into line | 52 | 7904 | 37.4648 | -119.7399 | Yes | Clear;32-90F | Conductor- Overhead | Normal | 23-0011208 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1801008 | 0 | EPSS Ckt | N | 2023
78277 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 2023-01-09 | 1030 | 20230109 | 1456 | 1937640 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20482 | 37.2869 | -119.6558 | Yes | Clear;32-90F | Conductor- Overhead | On Ground | 23-0011139 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1800947 | 0 | EPSS Ckt | N | 2023
78284 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320890543478 | 2023-01-09 | 1258 | 20230109 | 1525 | 1938191 | 147 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 147 | 37.6964 | -120.1931 | Yes | Clear;32-90F | Jumper | Broken | 23-0011380 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801148 | 0 | EPSS Ckt | N | 2023
78289 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320837148526 | 2023-01-09 | 1722 | 20230111 | 1753 | 1939121 | 2911 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2911 | 37.8323 | -120.2113 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0011697 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1801457 | 0 | EPSS Ckt | N | 2023
78290 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 2023-01-09 | 1732 | 20230109 | 2003 | 1939056 | 151 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2416 | 37.5054 | -120.0424 | Yes | Clear;32-90F | Pole-Wood | Deteriorated | 23-0011474 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1801232 | 0 | EPSS Ckt | N | 2023
78305 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | FUSE | S2139 | 2023-01-10 | 339 | 20230112 | 1431 | 1942721 | 3532 | Distribution Circuit | Environmental/External | Lightning | 10 | 12190 | 37.9901 | -120.2227 | Yes | Clear;32-90 F | Transformer (OH) | Broken | 23-0012961 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802528 | 0 | EPSS Ckt | N | 2023
78325 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | S1965 | 2023-01-10 | 445 | 20230111 | 1728 | 1946385 | 2203 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 40649 | 37.8919 | -120.2973 | Yes | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken | 23-0012955 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802522 | 1 | EPSS Ckt | N | 2023
78326 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320684652310 | 2023-01-10 | 445 | 20230110 | 2143 | 1946663 | 1018 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1018 | 37.9363 | -120.2742 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0013090 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1802645 | 0 | EPSS Ckt | N | 2023
78332 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2023-01-10 | 447 | 20230110 | 1640 | 1942834 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 55614 | 37.7148 | -120.0964 | Yes | Clear;32-90F | Secondary | Broken | 23-0012597 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802269 | 0 | EPSS Ckt | N | 2023
78336 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320614555004 | 2023-01-10 | 448 | 20230111 | 1436 | 1944929 | 2028 | Transformer only | Vegetation | Tree - branch fell on line | 3 | 6084 | 38.0107 | -120.2875 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0011904 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1802085 | 0 | EPSS Ckt | N | 2023
78343 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 98683 | 2023-01-10 | 530 | 20230111 | 1327 | 1942705 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19170 | 37.4849 | -119.9672 | Yes | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0012009 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1801787 | 0 | EPSS Ckt | N | 2023
78345 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10714 | 2023-01-10 | 543 | 20230111 | 1044 | 1945908 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15669 | 37.7202 | -120.094 | Yes | Clear;32-90F | Conductor- Overhead | Together | 23-0012597 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802384 | 0 | EPSS Ckt | N | 2023
78346 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 2023-01-10 | 546 | 20230111 | 1643 | 1942774 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 354393 | 37.5637 | -119.8544 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012258 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Three Phase Fault | 0 | No | Yes | No | 1802015 | 0 | EPSS Ckt | N | 2023
78350 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10409 | 2023-01-10 | 600 | 20230111 | 1148 | 1942948 | 1788 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 25992 | 37.3673 | -119.6083 | Yes | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012096 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | Yes | No | 1801870 | 0 | EPSS Ckt | N | 2023
78365 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 19163 | 2023-01-10 | 1148 | 20230110 | 2008 | 1944896 | 500 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 3500 | 37.5133 | -119.9152 | Yes | Clear;32-90 F |  |  | 23-0012974 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802537 | 0 | EPSS Ckt | N | 2023
78375 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322445429093 | 2023-01-10 | 1333 | 20230112 | 1636 | 1947337 | 3063 | Distribution Circuit | Environmental/External | Lightning | 3 | 9189 | 37.2962 | -119.6605 | Yes | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013437 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1802960 | 0 | EPSS Ckt | N | 2023
78376 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5673 | 2023-01-10 | 1336 | 20230111 | 933 | 1945292 | 1197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 28728 | 37.2893 | -119.6522 | Yes | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0013009 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1802567 | 0 | EPSS Ckt | N | 2023
78399 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320809054290 | 2023-01-11 | 704 | 20230112 | 1407 | 1947049 | 1863 | Transformer only | Environmental/External | Lightning | 1 | 1863 | 37.9907 | -120.2204 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0013858 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1803226 | 0 | EPSS Ckt | N | 2023
78417 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5673 | 2023-01-12 | 844 | 20230112 | 1636 | 1949592 | 472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 11328 | 37.2893 | -119.6522 | No | Clear;32-90F | Transformer (OH) | Failed/Faulted | 23-0014293 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803630 | 0 | EPSS Ckt | N | 2023
78421 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 93062 | 2023-01-12 | 1112 | 20230112 | 1235 | 1949934 | 83 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 13861 | 38.0204 | -120.2222 | No | Clear;32-90F | Recloser | Malfunctioning | 23-0014421 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1803716 | 0 | EPSS Ckt | N | 2023 | NONE
78427 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20327 | 2023-01-12 | 1717 | 20230112 | 2050 | 1950702 | 213 | Distribution Circuit | Vegetation | Tree - grew into line | 13 | 2769 | 38.0262 | -120.223 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0014733 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1803870 | 0 | EPSS Ckt | N | 2023
78444 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | JUMPER | OJ JUMPER 6/N/OF 10966 | 2023-01-13 | 1549 | 20230114 | 1038 | 1952512 | 1129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 469 | 172008 | 37.527 | -119.917 | No | Overcast-Rain;32-90 F | Jumper | Arcing | 23-0015526 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1804386 | 1 | EPSS Ckt | N | 2023
78455 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320098654405 | 2023-01-14 | 1211 | 20230114 | 1841 | 1954273 | 390 | Transformer only | Vegetation | Tree - fell into line | 2 | 780 | 37.9949 | -120.466 | Yes | Clear;32-90F | Secondary | Broken- wire on ground | 23-0016240 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1805000 | 0 | EPSS Ckt | N | 2023
78460 | YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | TRANSFORMER | 320555147023 | 2023-01-14 | 1642 | 20230114 | 1748 | 1954785 | 66 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 66 | 37.7908 | -120.3083 | Yes | Clear;32-90F | Fuse | Broken | 23-0016359 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1805114 | 0 | EPSS Ckt | N | 2023
78485 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1217 | 2023-01-15 | 857 | 20230115 | 1057 | 1955644 | 120 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 5280 | 38.0469 | -120.2017 | No | Clear;32-90F |  |  | 23-0016636 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1805375 | 0 | EPSS Ckt | N | 2023
78496 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 2023-01-15 | 2306 | 20230116 | 1317 | 1956437 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 65527 | 37.2869 | -119.6558 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0016857 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1805555 | 0 | EPSS Ckt | N | 2023
78516 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | SWITCH | 10216 | 2023-01-16 | 911 | 20230116 | 1544 | 1957433 | 393 | Distribution Circuit | 3rd Party | Vehicle | 115 | 45195 | 37.4639 | -119.7369 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0017059 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1805757 | 0 | EPSS Ckt | N | 2023
78521 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 2023-01-16 | 1103 | 20230117 | 1124 | 1957761 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15639 | 38.0185 | -120.2184 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017339 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | Yes | No | 1806013 | 0 | EPSS Ckt | N | 2023
78528 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 2023-01-16 | 1205 | 20230116 | 1615 | 1957953 | 250 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 500 | 37.7222 | -120.1193 | Yes | Clear;32-90 F |  |  | 23-0017306 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1805982 | 0 | EPSS Ckt | N | 2023
78529 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | JUMPER | OJ'S @ CGC# 320792753537 | 2023-01-16 | 1220 | 20230117 | 1425 | 1958018 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2675 | 37.9701 | -120.2262 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017273 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Open Circuit | 0 | No | Yes | Yes | 1805950 | 0 | EPSS Ckt | N | 2023
78530 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2155 | 2023-01-16 | 1303 | 20230116 | 1621 | 1958110 | 198 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 3168 | 37.9492 | -120.2562 | Yes | Clear;32-90 F |  |  | 23-0017309 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1805985 | 0 | EPSS Ckt | N | 2023
78532 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1217 | 2023-01-16 | 1340 | 20230116 | 1728 | 1958182 | 228 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 44 | 10032 | 38.0469 | -120.2017 | Yes | Clear;32-90 F |  |  | 23-0017326 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1806003 | 0 | EPSS Ckt | N | 2023
78543 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320790748336 | 2023-01-17 | 1218 | 20230117 | 1542 | 1959631 | 204 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 204 | 37.8269 | -120.2276 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0017732 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1806233 | 0 | EPSS Ckt | N | 2023
78547 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 7214 | 2023-01-17 | 1552 | 20230118 | 25 | 1960050 | 513 | Distribution Circuit | Equipment Failure/Involved | Underground | 63 | 31791 | 37.4845 | -119.9661 | No | Partly Cloudy-Drizzle;32-90 F | Conductor- Underground | Deteriorated | 23-0017849 | UG | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1806273 | 1 | EPSS Ckt | N | 2023
78576 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 408227 | 2023-01-22 | 34 | 20230122 | 1250 | 1964413 | 736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2208 | 37.7244 | -120.2582 | No | Clear;32-90F | Insulator | Broken | 23-0019814 | OH | Sus | 45647022 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1807274 | 0 | EPSS Ckt | N | 2023
78577 | YOSEMITE | YOSEMITE | SO. CAL. EDISON #3 1101 | 258861101 | RECLOSER | 43806 | 2023-01-22 | 730 | 20230122 | 1138 | 1964492 | 248 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 744 | 37.1649 | -119.4387 | No | Clear;32-90F |  |  | 23-0019824 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1807281 | 0 | EPSS Ckt | N | 2023 | C- INST
78587 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321231937339 | 2023-01-23 | 950 | 20230123 | 1211 | 1965633 | 141 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 282 | 37.5224 | -120.0774 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0020104 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1807543 | 0 | EPSS Ckt | N | 2023
78639 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321771537486 | 2023-01-31 | 1033 | 20230131 | 1515 | 1972745 | 282 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 282 | 37.5294 | -119.89 | No | Clear;32-90F | Transformer (OH) | Burned/flashed | 23-0023450 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1809480 | 0 | EPSS Ckt | N | 2023
78670 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 9879 | 2023-02-05 | 1337 | 20230205 | 1620 | 1977404 | 163 | Distribution Circuit | 3rd Party | Vehicle | 75 | 12225 | 37.8278 | -120.2578 | No | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0025386 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1810679 | 0 | EPSS Ckt | N | 2023
78698 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322474128853 | 2023-02-08 | 1507 | 20230208 | 1717 | 1980230 | 130 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 260 | 37.2896 | -119.6505 | No | Clear;32-90 F | Fuse | Broken | 23-0026807 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1811656 | 0 | EPSS Ckt | N | 2023
78706 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322546528421 | 2023-02-09 | 1301 | 20230209 | 1411 | 1981038 | 70 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 70 | 37.2778 | -119.6261 | No | Clear;32-90F |  |  | 23-0027183 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1811956 | 0 | EPSS Ckt | N | 2023
78837 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 19153 | 2023-02-22 | 1554 | 20230222 | 1624 | 1998136 | 30 | Distribution Circuit | Animal | Squirrel | 34 | 1020 | 37.4956 | -119.9728 | No | Clear;32-90 F | Cutout- fuse holder | Normal | 23-0032581 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816001 | 0 | EPSS Ckt | N | 2023
78847 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | S2149 | 2023-02-23 | 1036 | 20230223 | 1147 | 1999259 | 71 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 4 | 284 | 37.9995 | -120.4748 | Yes | Clear;32-90F |  |  | 23-0033100 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1816286 | 0 | EPSS Ckt | N | 2023
78855 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 2841 | 2023-02-23 | 2149 | 20230224 | 1146 | 2000723 | 837 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 30132 | 37.5325 | -120.0518 | Yes | Overcast-Fog;Below 32 F |  |  | 23-0033476 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1816506 | 1 | EPSS Ckt | N | 2023
78877 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | OTHER | WIRE DOWN 9/S/SS/293732 | 2023-02-24 | 737 | 20230224 | 1520 | 2004044 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 687 | 317435 | 37.6786 | -120.1234 | Yes | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033790 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1816809 | 1 | EPSS Ckt | N | 2023
78892 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321667636295 | 2023-02-24 | 1517 | 20230228 | 1653 | 2006457 | 5856 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 5856 | 37.4935 | -119.9255 | Yes | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0034440 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817294 | 0 | EPSS Ckt | N | 2023
78898 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 9400 | 2023-02-24 | 1558 | 20230224 | 1910 | 2006126 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2257 | 419001 | 37.5218 | -119.9174 | Yes | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken | 23-0034350 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1817229 | 0 | EPSS Ckt | N | 2023 | B PHASE & GRD
78903 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4575 | 2023-02-24 | 1652 | 20230228 | 1054 | 2006303 | 5402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 59422 | 37.5438 | -119.9152 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1818651 | 0 | EPSS Ckt | N | 2023
78926 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 2075 | 2023-02-24 | 1711 | 20230226 | 808 | 2006387 | 2337 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 11 | 25707 | 37.2731 | -119.6892 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0034536 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1817388 | 0 | EPSS Ckt | N | 2023
78933 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 2023-02-24 | 1740 | 20230226 | 1547 | 2008229 | 2767 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 213059 | 37.2869 | -119.6558 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken | 23-0034442 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1818000 | 0 | EPSS Ckt | N | 2023
78934 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 789923 | 2023-02-24 | 1740 | 20230226 | 1756 | 2008734 | 2896 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14480 | 37.2962 | -119.6484 | Yes | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1818150 | 0 | EPSS Ckt | N | 2023
78935 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6196 | 2023-02-24 | 1740 | 20230227 | 1409 | 2008826 | 4109 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 764274 | 37.2936 | -119.6478 | Yes | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1818185 | 0 | EPSS Ckt | N | 2023
78943 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322241031169 | 2023-02-24 | 1800 | 20230226 | 1635 | 2008029 | 2795 | Transformer only | Vegetation | Tree - fell into line | 4 | 11180 | 37.3545 | -119.7305 | Yes | Overcast-Fog-Snow;32-90 F | Secondary | Broken | 23-0034517 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817963 | 0 | EPSS Ckt | N | 2023
78945 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 90180 | 2023-02-24 | 1808 | 20230303 | 1836 | 2006573 | 10106 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 535618 | 37.5577 | -120.0138 | Yes | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034464 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817317 | 0 | EPSS Ckt | N | 2023 | C & GRD
78946 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 2023-02-24 | 1808 | 20230227 | 1751 | s1817991 | 4303 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25818 | 37.5386 | -119.9184 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817991 | 0 | EPSS Ckt | N | 2023
78948 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 100000075513 | 2023-02-24 | 1814 | 20230226 | 1134 | 2008189 | 2480 | Transformer only | Vegetation | Tree - branch fell on line | 2 | 4960 | 37.3554 | -119.7199 | Yes | Overcast-Fog-Snow;Below 32 F | Transformer | Broken | 23-0035129 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817994 | 0 | EPSS Ckt | N | 2023
78954 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | 322199231193 | 2023-02-24 | 1829 | 20230228 | 2105 | 2011908 | 5916 | Transformer only | Vegetation | Tree - fell into line | 1 | 5916 | 37.355 | -119.745 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036285 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1818979 | 0 | EPSS Ckt | N | 2023
78964 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 21549 | 2023-02-24 | 1842 | 20230303 | 1453 | 2006715 | 9851 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 82 | 807782 | 37.3739 | -119.6112 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0039227 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1821182 | 0 | EPSS Ckt | N | 2023
78966 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 636067 | 2023-02-24 | 1846 | 20230302 | 1124 | 2007401 | 8198 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24594 | 37.3657 | -119.6163 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1817863 | 0 | EPSS Ckt | N | 2023
78980 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 54749 | 2023-02-24 | 1847 | 20230304 | 1031 | 2007340 | 11024 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 88192 | 37.365 | -119.6221 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0034502 | OH | Sus | 45604552 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1817784 | 0 | EPSS Ckt | N | 2023
78981 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 6322 | 2023-02-24 | 1847 | 20230228 | 1821 | 2007341 | 5734 | Distribution Circuit | Environmental/External | Ice or snow | 11 | 63074 | 37.3654 | -119.62 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1817786 | 0 | EPSS Ckt | N | 2023
78983 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10288 | 2023-02-24 | 1847 | 20230227 | 1812 | 2012945 | 4285 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 64 | 274240 | 37.3568 | -119.6054 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0034502 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1819183 | 0 | EPSS Ckt | N | 2023
78993 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 10374 | 2023-02-24 | 1851 | 20230225 | 1311 | 2006762 | 1100 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 41 | 45100 | 37.4586 | -119.9015 | Yes | Clear;32-90 F |  |  | 23-0034556 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1817411 | 0 | EPSS Ckt | N | 2023
79002 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 5671 | 2023-02-24 | 1906 | 20230226 | 1635 | 2008226 | 2729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 275629 | 37.3592 | -119.7304 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035140 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1818002 | 0 | EPSS Ckt | N | 2023
79013 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 10585 | 2023-02-24 | 1906 | 20230228 | 1205 | 2010367 | 5339 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 69407 | 37.4218 | -119.7291 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1818667 | 0 | EPSS Ckt | N | 2023
79023 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 2023-02-24 | 1939 | 20230226 | 1758 | 2006883 | 2779 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 156394 | 37.5637 | -119.8544 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken | 23-0035212 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818062 | 1 | EPSS Ckt | N | 2023
79024 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | OCB | 1104/2 | 2023-02-24 | 1941 | 20230227 | 1335 | 2006899 | 2842 | Distribution Circuit | Equipment Failure/Involved | Overhead | 630 | 2377205 | 37.6655 | -119.8413 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034539 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817392 | 0 | EPSS Ckt | N | 2023 | B & GRD INSTANT
79025 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 2023-02-24 | 1942 | 20230228 | 1730 | 2006950 | 5628 | Distribution Circuit | Environmental/External | Ice or snow | 449 | 2105529 | 37.5251 | -119.9181 | Yes | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034552 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1817406 | 0 | EPSS Ckt | N | 2023 | BC & GRD
79030 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4677 | 2023-02-24 | 1942 | 20230228 | 1038 | 2010311 | 5216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 31296 | 37.5195 | -119.9168 | Yes | Clear;32-90F | Conductor- Overhead | Broken | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818645 | 0 | EPSS Ckt | N | 2023
79032 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | JUMPER | JMPRS 3 POLES N/OF CGC 321696536341 | 2023-02-24 | 1942 | 20230228 | 1740 | 2010317 | 5638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16914 | 37.497 | -119.9166 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | Yes | No | 1818648 | 0 | EPSS Ckt | N | 2023
79045 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4709 | 2023-02-24 | 1942 | 20230302 | 1337 | 2015030 | 8275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 24825 | 37.5715 | -119.9926 | Yes | Overcast-Fog;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0034552 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1819710 | 0 | EPSS Ckt | N | 2023
79048 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 151918 | 2023-02-24 | 1950 | 20230228 | 1315 | 2006967 | 5365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1324 | 5285932 | 37.4926 | -119.9657 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817410 | 0 | EPSS Ckt | N | 2023 | C & GRD
79052 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 2023-02-24 | 1952 | 20230226 | 1617 | 2006940 | 2665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3073 | 639314 | 37.8844 | -120.3058 | Yes | Clear;32-90 F | Insulator | Broken- wire on ground | 23-0034549 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817402 | 0 | EPSS Ckt | N | 2023 | C PH INST SGF
79062 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 2023-02-25 | 27 | 20230226 | 825 | 2008741 | 1918 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 3836 | 37.7222 | -120.1193 | Yes | Clear;32-90 F |  |  | 23-0035095 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818148 | 0 | EPSS Ckt | N | 2023
79063 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 13485 | 2023-02-25 | 38 | 20230227 | 1636 | 2009765 | 3838 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7676 | 37.5335 | -120.0516 | Yes | Clear;32-90F | Pole-Wood | Broken | 23-0035026 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818472 | 1 | EPSS Ckt | N | 2023
79068 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321015544998 | 2023-02-25 | 215 | 20230226 | 1800 | 2007502 | 2385 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2385 | 37.7371 | -120.15 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0035313 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818160 | 0 | EPSS Ckt | N | 2023
79068 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321015544998 | 2023-02-25 | 215 | 20230226 | 1800 | 2007502 | 2385 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2385 | 37.7371 | -120.15 | Yes | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0035313 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818160 | 0 | EPSS Ckt | N | 2023
79072 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 2023-02-25 | 316 | 20230301 | 1555 | 2007575 | 6519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 231960 | 37.5151 | -120.052 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035026 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817892 | 0 | EPSS Ckt | N | 2023 | A & GRD
79074 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 2023-02-25 | 346 | 20230225 | 1804 | 2007612 | 858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 185328 | 37.5079 | -119.9962 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035032 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1817899 | 0 | EPSS Ckt | N | 2023 | C & GRD
79075 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321529237933 | 2023-02-25 | 346 | 20230302 | 1620 | 2009080 | 7954 | Transformer only | Vegetation | Tree - fell into line | 1 | 7954 | 37.5395 | -119.9736 | Yes | Clear;32-90 F | Secondary | Broken | 23-0035424 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818270 | 0 | EPSS Ckt | N | 2023
79076 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321517137906 | 2023-02-25 | 358 | 20230304 | 1529 | 2009081 | 10771 | Transformer only | Vegetation | Tree - fell into line | 1 | 10771 | 37.5392 | -119.9778 | Yes | Snow-Clear;32-90 F | Service conductor | Broken | 23-0035431 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818279 | 0 | EPSS Ckt | N | 2023
79078 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2023-02-25 | 413 | 20230226 | 1557 | 2007625 | 2144 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 150080 | 37.7148 | -120.0964 | Yes |  | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1818142 | 0 | EPSS Ckt | N | 2023
79081 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 2023-02-25 | 513 | 20230228 | 1615 | 2007661 | 4247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 725 | 568423 | 37.4963 | -120.0432 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035035 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Multi-Fault | 0 | No | Yes | No | 1817905 | 0 | EPSS Ckt | N | 2023 | AB & GRD
79082 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 10347 | 2023-02-25 | 513 | 20230227 | 1649 | 2008824 | 3576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 46488 | 37.4768 | -120.051 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0035035 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818184 | 0 | EPSS Ckt | N | 2023
79083 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321631737634 | 2023-02-25 | 550 | 20230227 | 1431 | 2009318 | 3401 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 3401 | 37.5328 | -119.9363 | Yes | Clear;32-90 F | Other | Broken | 23-0035471 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Open Circuit | 0 | No | No | No | 1818318 | 0 | EPSS Ckt | N | 2023
79085 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 14542 | 2023-02-25 | 608 | 20230226 | 848 | 2009380 | 1600 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3200 | 37.5233 | -119.9221 | Yes | Clear;32-90 F | Conductor- Overhead | Normal | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818340 | 0 | EPSS Ckt | N | 2023
79086 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10408 | 2023-02-25 | 638 | 20230228 | 1758 | 2008350 | 5000 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 133192 | 37.3671 | -119.6088 | Yes | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken | 23-0036533 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819123 | 0 | EPSS Ckt | N | 2023
79089 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4631 | 2023-02-25 | 733 | 20230226 | 1702 | 2008745 | 2009 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 12054 | 37.7324 | -120.1227 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818152 | 0 | EPSS Ckt | N | 2023
79095 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | JUMPER | OJ'S 1 S/OF CGC# 321767535110 | 2023-02-25 | 837 | 20230226 | 1421 | 2008761 | 1784 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14272 | 37.46 | -119.8911 | Yes | Clear;32-90 F | Pole-Wood | Broken | 23-0035102 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1818161 | 0 | EPSS Ckt | N | 2023
79096 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 11947 | 2023-02-25 | 837 | 20230226 | 1421 | 2007897 | 1784 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 21408 | 37.4611 | -119.896 | Yes | Overcast-Fog;32-90 F |  |  | 23-0035782 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818609 | 0 | EPSS Ckt | N | 2023
79098 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 151918 | 2023-02-25 | 902 | 20230225 | 2202 | 2008330 | 780 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 85800 | 37.4926 | -119.9657 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0035102 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818028 | 0 | EPSS Ckt | N | 2023 | N/A
79100 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 2023-02-25 | 902 | 20230225 | 1816 | 2008347 | 554 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 414 | 223064 | 37.4593 | -119.8997 | Yes | Overcast-Fog;32-90 F |  |  | 23-0035102 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818034 | 0 | EPSS Ckt | N | 2023 | N/A
79101 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 1960 | 2023-02-25 | 902 | 20230225 | 1330 | 2008352 | 268 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 195 | 52260 | 37.4587 | -119.9001 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0035102 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1818037 | 0 | EPSS Ckt | N | 2023 | N/A
79106 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 2023-02-25 | 1334 | 20230225 | 1517 | 2008552 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 2369 | 38.0185 | -120.2184 | Yes | Clear;32-90 F |  |  | 23-0035320 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1818169 | 0 | EPSS Ckt | N | 2023
79111 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 19153 | 2023-02-25 | 1452 | 20230226 | 1321 | 2008756 | 1349 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 34 | 45866 | 37.4956 | -119.9728 | Yes | Clear;32-90F |  |  | 23-0035743 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818576 | 0 | EPSS Ckt | N | 2023
79112 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321126844175 | 2023-02-25 | 1542 | 20230227 | 1630 | 2008828 | 2928 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 2928 | 37.7149 | -120.1118 | Yes | Overcast-Snow;32-90 F | Service conductor | Broken- wire on ground | 23-0035598 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1818449 | 0 | EPSS Ckt | N | 2023
79142 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 2023-02-27 | 847 | 20230228 | 1418 | 2014900 | 1771 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 169 | 299299 | 37.5637 | -119.8544 | Yes | Overcast-Fog-Snow;Below 32 F |  |  | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1819687 | 0 | EPSS Ckt | N | 2023
79143 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 9400 | 2023-02-27 | 848 | 20230227 | 1136 | s1818911 | 168 | Distribution Circuit | 3rd Party | Vehicle | 387 | 65016 | 37.5218 | -119.9174 | Yes | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1818911 | 0 | EPSS Ckt | N | 2023 | B & C
79148 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 2023-02-27 | 1124 | 20230227 | 1434 | 2011991 | 190 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 524 | 52814 | 37.4593 | -119.8997 | Yes | Overcast-Rain;32-90 F |  |  | 23-0036349 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819022 | 0 | EPSS Ckt | N | 2023 | C & GRD
79151 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27337 | 2023-02-27 | 1203 | 20230227 | 1334 | 2012150 | 91 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 819 | 37.8143 | -120.0619 | Yes | Clear;32-90 F |  |  | 23-0036444 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1819077 | 0 | EPSS Ckt | N | 2023
79160 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2023-02-27 | 1642 | 20230228 | 1539 | 2013122 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 609 | 639207 | 37.8306 | -120.2367 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Together | 23-0036647 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1819219 | 0 | EPSS Ckt | N | 2023 | B & C
79161 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | JUMPER | WIREDOWN SRC SIDE OF CGC 321776434736 | 2023-02-27 | 1731 | 20230305 | 1049 | 2022840 | 8238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 19788 | 37.4497 | -119.8889 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040070 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1821815 | 0 | EPSS Ckt | N | 2023
79162 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 2023-02-27 | 1814 | 20230228 | 1859 | 2013520 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 53460 | 37.5512 | -119.9231 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036824 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1819367 | 0 | EPSS Ckt | N | 2023
79172 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 2093 | 2023-02-28 | 1059 | 20230305 | 1700 | 2021702 | 7561 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 75610 | 38.0336 | -120.326 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039613 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1821396 | 0 | EPSS Ckt | N | 2023
79175 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | SWITCH | L1475 | 2023-02-28 | 1136 | 20230313 | 1700 | 2015047 | 19044 | Distribution Circuit | Environmental/External | Ice or snow | 15 | 104850 | 38.0545 | -120.3584 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037287 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | Yes | 1819715 | 0 | EPSS Ckt | N | 2023
79182 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 2023-02-28 | 1320 | 20230304 | 16 | 2021688 | 4976 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 114448 | 38.0185 | -120.2184 | Yes | Overcast-Snow-Strong Winds;Below 32 F |  |  | 23-0038155 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1821389 | 0 | EPSS Ckt | N | 2023
79188 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 2023-02-28 | 1443 | 20230302 | 2005 | 2015678 | 3202 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 121676 | 37.6105 | -120.1339 | Yes | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1819869 | 0 | EPSS Ckt | N | 2023 | NONE
79189 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | SWITCH | 4632 | 2023-02-28 | 1443 | 20230306 | 1741 | 2016422 | 8818 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 1168987 | 37.7317 | -120.1227 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | Yes | No | 1819994 | 0 | EPSS Ckt | N | 2023
79190 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4629 | 2023-02-28 | 1443 | 20230307 | 1716 | 2016508 | 10233 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 1291275 | 37.7103 | -120.111 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken | 23-0037680 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1820019 | 0 | EPSS Ckt | N | 2023
79191 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | SWITCH | 10261 | 2023-02-28 | 1443 | 20230304 | 1605 | s1820092 | 5842 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 268732 | 37.7128 | -120.1139 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1820092 | 0 | EPSS Ckt | N | 2023
79192 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23944 | 2023-02-28 | 1443 | 20230303 | 1322 | 2020466 | 4239 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 33912 | 37.7066 | -120.1141 | Yes | Overcast-Heavy Rain;32-90 F | Secondary | Normal | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1821033 | 0 | EPSS Ckt | N | 2023
79193 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23943 | 2023-02-28 | 1443 | 20230303 | 1539 | 2020468 | 4376 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 52512 | 37.7081 | -120.1136 | Yes | Overcast-Heavy Rain;32-90 F |  |  | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1821035 | 0 | EPSS Ckt | N | 2023
79194 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23938 | 2023-02-28 | 1443 | 20230303 | 1528 | 2020474 | 4365 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 48015 | 37.7123 | -120.1136 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1821038 | 0 | EPSS Ckt | N | 2023
79197 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 67697 | 2023-02-28 | 1443 | 20230305 | 1431 | 2022392 | 7188 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 35940 | 37.7399 | -120.1374 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1821720 | 0 | EPSS Ckt | N | 2023
79198 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4635 | 2023-02-28 | 1443 | 20230305 | 1052 | 2022491 | 6969 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27876 | 37.7165 | -120.1151 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1821753 | 0 | EPSS Ckt | N | 2023
79199 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 44573 | 2023-02-28 | 1443 | 20230307 | 1518 | 2022499 | 10115 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10115 | 37.7131 | -120.1143 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1821755 | 0 | EPSS Ckt | N | 2023
79200 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4631 | 2023-02-28 | 1443 | 20230306 | 1826 | 2023818 | 8863 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 53178 | 37.7324 | -120.1227 | Yes | Overcast-Heavy Rain;32-90 F | Service conductor | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1822099 | 0 | EPSS Ckt | N | 2023
79201 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10708 | 2023-02-28 | 1443 | 20230306 | 1537 | 2023839 | 8694 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 104328 | 37.7399 | -120.1253 | Yes | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1822111 | 0 | EPSS Ckt | N | 2023
79202 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10709 | 2023-02-28 | 1443 | 20230307 | 1311 | 2023840 | 9988 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 129844 | 37.7363 | -120.1266 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Normal | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1822112 | 0 | EPSS Ckt | N | 2023
79203 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10404 | 2023-02-28 | 1443 | 20230307 | 1549 | 2023856 | 10146 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 172482 | 37.7655 | -120.1527 | Yes | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1822119 | 0 | EPSS Ckt | N | 2023
79208 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | JMPRS @ HARD TAP 2 N/OF 4632 | 2023-02-28 | 1443 | 20230305 | 1821 | 2024004 | 7418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7418 | 37.7332 | -120.1234 | Yes | Clear;32-90 F | Conductor- Overhead | Broken | 23-0037496 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1822167 | 0 | EPSS Ckt | N | 2023
79213 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S1575 | 2023-02-28 | 1511 | 20230304 | 1500 | 2020218 | 5749 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 15006 | 38.0288 | -120.2514 | Yes | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | Yes | No | 1820965 | 0 | EPSS Ckt | N | 2023
79228 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 20419 | 2023-02-28 | 1601 | 20230304 | 2038 | 2016113 | 6036 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 411938 | 37.8258 | -120.2347 | Yes | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037873 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1820847 | 1 | EPSS Ckt | N | 2023
79235 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRIP-SAVER | 19772 | 2023-02-28 | 1608 | 20230304 | 1547 | 2021978 | 5739 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 723114 | 38.0261 | -120.2523 | Yes | Overcast-Snow-Strong Winds;32-90 F | Other | Broken | 23-0037588 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1821591 | 0 | EPSS Ckt | N | 2023 | N/A
79237 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 2023-02-28 | 1644 | 20230303 | 2030 | 2018843 | 4546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 72736 | 37.4684 | -119.7375 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1820577 | 0 | EPSS Ckt | N | 2023
79240 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 79097 | 2023-02-28 | 1644 | 20230304 | 1631 | 2021750 | 5747 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 68964 | 37.5864 | -119.8513 | Yes | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1821409 | 0 | EPSS Ckt | N | 2023
79251 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 93062 | 2023-02-28 | 1916 | 20230303 | 2015 | 2016531 | 4222 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 621818 | 38.0204 | -120.2222 | Yes | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Normal | 23-0038155 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1820389 | 0 | EPSS Ckt | N | 2023 | A & B
79252 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320799755182 | 2023-02-28 | 1916 | 20230304 | 935 | 2021734 | 5179 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 5179 | 38.0146 | -120.2239 | Yes | Clear;32-90 F | Customer Equipment | Broken | 23-0038155 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1821407 | 0 | EPSS Ckt | N | 2023
79254 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L877 | 2023-02-28 | 1958 | 20230304 | 1024 | 2016682 | 5186 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 233370 | 38.0374 | -120.3501 | Yes | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037895 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1820446 | 0 | EPSS Ckt | N | 2023
79259 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 921 | 2023-02-28 | 2217 | 20230306 | 1413 | 2017125 | 8156 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 157540 | 38.0203 | -120.3351 | Yes | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken | 23-0038639 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1820768 | 0 | EPSS Ckt | N | 2023
79268 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2153 | 2023-02-28 | 2236 | 20230302 | 1923 | 2018838 | 2687 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 104793 | 37.9491 | -120.2657 | Yes | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037846 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1820572 | 0 | EPSS Ckt | N | 2023
79271 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 44913 | 2023-02-28 | 2237 | 20230303 | 1538 | 2018121 | 3901 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19505 | 37.5186 | -119.9171 | Yes | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1820348 | 0 | EPSS Ckt | N | 2023
79275 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10353 | 2023-02-28 | 2237 | 20230304 | 1602 | 2021745 | 5365 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 96570 | 37.576 | -119.8535 | Yes | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | Yes | No | 1821408 | 0 | EPSS Ckt | N | 2023
79276 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 9400 | 2023-02-28 | 2238 | 20230301 | 1400 | 2017177 | 922 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 119 | 109718 | 37.5218 | -119.9174 | Yes | Overcast-Fog-Snow;32-90 F |  |  | 23-0037849 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1820179 | 0 | EPSS Ckt | N | 2023 | B- GRD TIME OC
79295 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 2023-03-01 | 23 | 20230302 | 1120 | 2017291 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 173914 | 37.5079 | -119.9962 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037868 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1820197 | 0 | EPSS Ckt | N | 2023 | B PH & GRD
79302 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2023-03-01 | 48 | 20230302 | 1551 | 2017310 | 2343 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 292875 | 37.8306 | -120.2367 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0037873 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820202 | 0 | EPSS Ckt | N | 2023 | A & B
79303 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | JUMPER | 320767648369 | 2023-03-01 | 48 | 20230304 | 1405 | 2019698 | 5117 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14213 | 37.8277 | -120.2355 | No | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037873 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1820810 | 0 | EPSS Ckt | N | 2023
79308 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 22287 | 2023-03-01 | 53 | 20230304 | 1330 | 2017314 | 5077 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 50770 | 37.5354 | -119.9493 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0039991 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821747 | 0 | EPSS Ckt | N | 2023
79312 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 20261 | 2023-03-01 | 204 | 20230302 | 1228 | 2017398 | 2064 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 97008 | 37.8487 | -120.2085 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0038745 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820832 | 0 | EPSS Ckt | N | 2023
79314 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 2023-03-01 | 227 | 20230302 | 1218 | 2017845 | 2031 | Distribution Circuit | Environmental/External | Ice or snow | 36 | 73116 | 37.5512 | -119.9231 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037975 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1820284 | 0 | EPSS Ckt | N | 2023
79315 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 752630 | 2023-03-01 | 235 | 20230302 | 1304 | 2017431 | 2069 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 310540 | 37.5697 | -119.942 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037893 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820226 | 0 | EPSS Ckt | N | 2023 | A & GRD
79315 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 752630 | 2023-03-01 | 235 | 20230302 | 1304 | 2017431 | 2069 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 310540 | 37.5697 | -119.942 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037893 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820226 | 0 | EPSS Ckt | N | 2023 | A & GRD
79318 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-03-01 | 247 | 20230301 | 1750 | 2017439 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 1145 | 1033935 | 38.0063 | -120.3474 | No | Overcast-Snow;Below 32 F | Conductor- Overhead | Together | 23-0037895 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820228 | 0 | EPSS Ckt | N | 2023 | BC
79319 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 1691 | 2023-03-01 | 247 | 20230302 | 1325 | 2018385 | 2078 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 143382 | 38.0211 | -120.3575 | No | Clear-Strong Winds;Below 32 F | Secondary | Normal | 23-0037895 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820442 | 0 | EPSS Ckt | N | 2023
79320 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20775 | 2023-03-01 | 247 | 20230302 | 1808 | 2018906 | 2361 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4722 | 38.0166 | -120.3559 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0037895 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1820596 | 0 | EPSS Ckt | N | 2023
79322 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | SWITCH | 10357 | 2023-03-01 | 248 | 20230302 | 1117 | 2018196 | 1949 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 179308 | 37.3371 | -119.7671 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037896 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1820372 | 0 | EPSS Ckt | N | 2023
79324 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 2023-03-01 | 305 | 20230302 | 1524 | 2017577 | 2179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 13074 | 37.5386 | -119.9184 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | Yes | No | 1820602 | 0 | EPSS Ckt | N | 2023
79330 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | JUMPER | 320930649234 | 2023-03-01 | 337 | 20230303 | 1519 | 2018277 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 84136 | 37.8516 | -120.1787 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037912 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | Yes | No | 1820403 | 0 | EPSS Ckt | N | 2023
79332 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320765548586 | 2023-03-01 | 347 | 20230307 | 1407 | 2023795 | 9260 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 18520 | 37.8337 | -120.2357 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 23-0040372 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822095 | 0 | EPSS Ckt | N | 2023
79336 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJS 2 W/OF 4626 | 2023-03-01 | 437 | 20230307 | 1222 | 2021915 | 9105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 63735 | 37.7777 | -120.1779 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken | 23-0037909 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1821465 | 0 | EPSS Ckt | N | 2023
79340 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 14572 | 2023-03-01 | 511 | 20230302 | 1238 | 2019004 | 1887 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 107559 | 37.5704 | -119.9418 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820631 | 0 | EPSS Ckt | N | 2023
79340 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 14572 | 2023-03-01 | 511 | 20230302 | 1238 | 2019004 | 1887 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 57 | 107559 | 37.5704 | -119.9418 | No | Overcast-Fog-Snow;Below 32 F |  |  | 23-0038012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820631 | 0 | EPSS Ckt | N | 2023
79342 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320842449192 | 2023-03-01 | 523 | 20230303 | 923 | 2021273 | 3120 | Transformer only | Unknown Cause | Patrol - found nothing | 4 | 12480 | 37.8509 | -120.2094 | No | Clear;32-90 F |  |  | 23-0039450 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1821297 | 0 | EPSS Ckt | N | 2023
79347 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 10642 | 2023-03-01 | 723 | 20230303 | 1705 | 2018270 | 3462 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 159252 | 37.4212 | -119.7249 | No | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037944 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1820401 | 0 | EPSS Ckt | N | 2023
79351 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 2023-03-01 | 741 | 20230301 | 1317 | 2017270 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 434 | 145824 | 37.4593 | -119.8997 | No | Partly Cloudy-Fog;Below 32 F | Pole-Wood | Broken | 23-0037949 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820271 | 0 | EPSS Ckt | N | 2023 | C & GRD
79355 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20327 | 2023-03-01 | 833 | 20230301 | 1334 | 2017849 | 301 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 3913 | 38.0262 | -120.223 | No | Clear;32-90F |  |  | 23-0038158 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1820391 | 0 | EPSS Ckt | N | 2023
79358 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 10546 | 2023-03-01 | 901 | 20230302 | 1512 | 2017885 | 1811 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 48897 | 37.4933 | -119.9751 | No | Partly Cloudy-Fog;Below 32 F |  |  | 23-0038886 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820916 | 0 | EPSS Ckt | N | 2023
79361 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 2023-03-01 | 930 | 20230302 | 1218 | 2017663 | 1608 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 258888 | 37.5251 | -119.9181 | No | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038012 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | Yes | No | 1820307 | 0 | EPSS Ckt | N | 2023 | A & B
79368 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 13485 | 2023-03-01 | 1255 | 20230301 | 1804 | 2018313 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 412 | 37.5335 | -120.0516 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0038374 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820562 | 1 | EPSS Ckt | N | 2023
79371 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 4636 | 2023-03-01 | 1331 | 20230303 | 1232 | 2018377 | 2821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 93093 | 37.7183 | -120.1892 | No | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0038242 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1820465 | 0 | EPSS Ckt | N | 2023
79372 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | JUMPER | OJ'S 1 S/OF CGC# 320811155314 | 2023-03-01 | 1331 | 20230305 | 1535 | 2021680 | 5884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 11768 | 38.0177 | -120.22 | No | Overcast-Snow-Strong Winds;Below 32 F | Insulator | Normal | 23-0038155 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821386 | 0 | EPSS Ckt | N | 2023
79381 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10602 | 2023-03-01 | 1600 | 20230303 | 1208 | 2010306 | 2648 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 10592 | 37.272 | -119.6711 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038362 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | Yes | 1820552 | 0 | EPSS Ckt | N | 2023
79384 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 493137 | 2023-03-01 | 1649 | 20230302 | 1028 | 2018793 | 1059 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 88956 | 37.2859 | -119.6313 | No |  | Conductor- Overhead | Normal | 23-0038397 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1820589 | 0 | EPSS Ckt | N | 2023
79399 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | MTR#1006382614 | 2023-03-02 | 714 | 20230305 | 1001 | 2019390 | 4487 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 4487 | 37.467 | -119.9032 | No | Clear;32-90 F | Transformer | Broken | 23-0039851 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821626 | 0 | EPSS Ckt | N | 2023
79408 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4575 | 2023-03-02 | 1403 | 20230304 | 1013 | 2019968 | 2650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 29150 | 37.5438 | -119.9152 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039599 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1821378 | 0 | EPSS Ckt | N | 2023
79413 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321461238911 | 2023-03-02 | 1508 | 20230305 | 1910 | 2020084 | 4562 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 9124 | 37.5661 | -119.9967 | No | Clear;32-90 F | Other | Normal | 23-0040123 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821870 | 0 | EPSS Ckt | N | 2023
79417 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | JUMPER | OJ 3 W/OF 10948 | 2023-03-02 | 1747 | 20230303 | 935 | 2020576 | 948 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 948 | 37.5619 | -119.9681 | No | Clear;32-90 F | Jumper | Burned Open | 23-0039078 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1821068 | 0 | EPSS Ckt | N | 2023
79419 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321667636295 | 2023-03-02 | 1805 | 20230304 | 1624 | 2022594 | 2779 | Transformer only | Vegetation | Tree - fell into line | 1 | 2779 | 37.4935 | -119.9255 | No | Clear;32-90 F | Service conductor | Broken | 23-0040013 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1821771 | 0 | EPSS Ckt | N | 2023
79427 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10338 | 2023-03-03 | 900 | 20230303 | 1200 | 2020849 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 3600 | 37.2814 | -119.6699 | No | Clear;32-90 F | Insulator | Broken | 23-0039260 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1821196 | 0 | EPSS Ckt | N | 2023
79429 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320843149232 | 2023-03-03 | 941 | 20230307 | 1436 | 2021283 | 6055 | Transformer only | Vegetation | Tree - fell into line | 4 | 24220 | 37.8521 | -120.2091 | No | Clear;32-90 F | Transformer | Broken | 23-0039452 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1821299 | 0 | EPSS Ckt | N | 2023
79436 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320430655825 | 2023-03-03 | 1254 | 20230306 | 1338 | 2021348 | 4364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 26184 | 38.0311 | -120.352 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0040440 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822173 | 0 | EPSS Ckt | N | 2023
79438 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320908648835 | 2023-03-03 | 1459 | 20230304 | 833 | 2021562 | 1054 | Transformer only | Unknown Cause | Patrol - found nothing | 2 | 2108 | 37.8409 | -120.1868 | No | Clear;32-90 F |  |  | 23-0039683 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1821439 | 0 | EPSS Ckt | N | 2023
79444 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | S1767 | 2023-03-03 | 2105 | 20230305 | 1717 | 2021955 | 2652 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 18564 | 38.0147 | -120.2262 | No | Overcast-Fog;32-90 F | Conductor- Overhead | Normal | 23-0039890 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1821653 | 0 | EPSS Ckt | N | 2023
79450 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10226 | 2023-03-04 | 945 | 20230304 | 1040 | 2022212 | 53 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 371 | 37.457 | -119.737 | No | Clear;32-90F | Conductor- Overhead | Normal | 23-0039913 | OH | Sus | 0 | CENTRAL VALLEY | MAR |  | 0 | No | No | No | 1821668 | 0 | EPSS Ckt | N | 2023
79456 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321631737634 | 2023-03-04 | 1239 | 20230305 | 1812 | 2022420 | 1773 | Transformer only | Environmental/External | Ice or snow | 67 | 12333 | 37.5328 | -119.9363 | No | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken | 23-0039984 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821740 | 0 | EPSS Ckt | N | 2023
79468 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 2023-03-05 | 212 | 20230306 | 1506 | 2023129 | 2214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 29850 | 37.5151 | -120.052 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken | 23-0040195 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1821943 | 0 | EPSS Ckt | N | 2023 | A PH AND GROUND
79473 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 9400 | 2023-03-05 | 928 | 20230305 | 1526 | 2023516 | 358 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2252 | 719356 | 37.5218 | -119.9174 | No | Overcast-Fog-Snow;32-90 F |  |  | 23-0040282 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822019 | 0 | EPSS Ckt | N | 2023 | B & GRD
79476 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | TRANSFORMER | 322587231774 | 2023-03-05 | 1048 | 20230306 | 1340 | 2023638 | 1612 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1612 | 37.3693 | -119.6101 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040407 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822141 | 0 | EPSS Ckt | N | 2023
79481 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 2023-03-05 | 1123 | 20230306 | 1024 | 2023649 | 1381 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 31763 | 38.0185 | -120.2184 | No | Clear;32-90F |  |  | 23-0040596 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822304 | 0 | EPSS Ckt | N | 2023
79485 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | TRANSFORMER | 320712055599 | 2023-03-05 | 1206 | 20230307 | 1126 | 2023696 | 2840 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 2840 | 38.0267 | -120.2533 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040412 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822146 | 0 | EPSS Ckt | N | 2023
79490 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1547 | 2023-03-05 | 1352 | 20230306 | 1708 | 2023800 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5222 | 37.812 | -120.0649 | No | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0040406 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1822140 | 0 | EPSS Ckt | N | 2023
79491 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320776248241 | 2023-03-05 | 1439 | 20230307 | 1721 | 2023852 | 3042 | Transformer only | Environmental/External | Ice or snow | 3 | 9126 | 37.8242 | -120.2326 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0040447 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822181 | 0 | EPSS Ckt | N | 2023
79492 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321893739107 | 2023-03-05 | 1449 | 20230306 | 1642 | 2024605 | 1553 | Transformer only | Vegetation | Tree - branch fell on line | 1 | 1553 | 37.5724 | -119.8472 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0040678 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822349 | 0 | EPSS Ckt | N | 2023
79496 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4707 | 2023-03-05 | 1800 | 20230307 | 1144 | 2024010 | 2504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 145232 | 37.5588 | -119.9703 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040437 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | Yes | No | 1822169 | 0 | EPSS Ckt | N | 2023
79499 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 2023-03-05 | 2051 | 20230306 | 815 | 2024143 | 684 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 10944 | 37.5054 | -120.0424 | No | Overcast-Snow;32-90 F |  |  | 23-0040582 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822292 | 0 | EPSS Ckt | N | 2023
79511 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321121544300 | 2023-03-06 | 1240 | 20230308 | 955 | 2023788 | 2715 | Transformer only | Vegetation | Tree - fell into line | 2 | 5430 | 37.7182 | -120.1139 | No | Clear;32-90 F | Service conductor | Broken | 23-0040749 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1822382 | 0 | EPSS Ckt | N | 2023
79513 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10494 | 2023-03-06 | 1305 | 20230306 | 1315 | 2024730 | 10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 20 | 37.5858 | -119.8517 | No | Clear;32-90F |  |  | 23-0040751 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1822383 | 0 | EPSS Ckt | N | 2023
79517 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10353 | 2023-03-06 | 1758 | 20230308 | 950 | 2025026 | 2392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 43056 | 37.576 | -119.8535 | No | Clear;32-90 F | Jumper | Burned Open | 23-0041509 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Open Circuit | 0 | No | No | No | 1822817 | 0 | EPSS Ckt | N | 2023
79527 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 20775 | 2023-03-07 | 1337 | 20230307 | 1410 | 2025619 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 66 | 38.0166 | -120.3559 | No | Clear;32-90F | Cutout- fuse holder | Failed/Faulted | 23-0041196 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1822627 | 0 | EPSS Ckt | N | 2023
79553 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 2023-03-09 | 1143 | 20230310 | 1053 | 2027583 | 1390 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 52518 | 37.5151 | -120.052 | Yes | Clear;32-90 F | Conductor- Overhead | Together | 23-0042106 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1823128 | 0 | EPSS Ckt | N | 2023 | A/GRD
79592 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320430655825 | 2023-03-11 | 1514 | 20230313 | 1110 | 2032587 | 2636 | Distribution Circuit | Environmental/External | Lightning | 6 | 15816 | 38.0311 | -120.352 | No | Strong Winds; | Transformer (OH) | Failed/Faulted | 23-0043633 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824174 | 0 | EPSS Ckt | N | 2023
79594 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2155 | 2023-03-11 | 1519 | 20230311 | 1943 | 2032586 | 264 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 4224 | 37.9492 | -120.2562 | No | Strong Winds; |  |  | 23-0043570 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824109 | 0 | EPSS Ckt | N | 2023
79599 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | S1491 | 2023-03-11 | 1551 | 20230311 | 1835 | 2032628 | 164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4100 | 38.0177 | -120.3276 | No | Clear-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0043547 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1824087 | 0 | EPSS Ckt | N | 2023
79602 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320718052741 | 2023-03-11 | 1713 | 20230313 | 1023 | 2032732 | 2470 | Transformer only | Environmental/External | Lightning | 3 | 7410 | 37.9487 | -120.2514 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043617 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824158 | 0 | EPSS Ckt | N | 2023
79611 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320560250460 | 2023-03-11 | 2046 | 20230313 | 1042 | 2032899 | 2276 | Transformer only | Environmental/External | Lightning | 2 | 4552 | 37.8858 | -120.3061 | No | Strong Winds;32-90 F | Transformer | Failed/Faulted | 23-0043619 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824159 | 0 | EPSS Ckt | N | 2023
79614 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320560450512 | 2023-03-12 | 313 | 20230313 | 1044 | 2033001 | 1891 | Transformer only | Environmental/External | Lightning | 1 | 1891 | 37.8872 | -120.3063 | No | Strong Winds;32-90 F | Transformer | Broken | 23-0043620 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824160 | 0 | EPSS Ckt | N | 2023
79629 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | TRANSFORMER | 320702052655 | 2023-03-12 | 1855 | 20230313 | 1040 | 2033588 | 945 | Transformer only | Environmental/External | Lightning | 1 | 945 | 37.946 | -120.2577 | No | Heavy Rain;32-90 F | Transformer | Failed/Faulted | 23-0043804 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824318 | 0 | EPSS Ckt | N | 2023
79651 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4642 | 2023-03-14 | 717 | 20230314 | 816 | 2035217 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1475 | 37.5583 | -119.9304 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0044540 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824758 | 0 | EPSS Ckt | N | 2023
79651 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4642 | 2023-03-14 | 717 | 20230314 | 816 | 2035217 | 59 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 1475 | 37.5583 | -119.9304 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 23-0044540 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1824758 | 0 | EPSS Ckt | N | 2023
79652 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321511038218 | 2023-03-14 | 816 | 20230314 | 1044 | 2035310 | 148 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 444 | 37.5473 | -119.9802 | Yes | Clear;32-90F |  |  | 23-0044718 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1824859 | 0 | EPSS Ckt | N | 2023
79702 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321669838319 | 2023-03-14 | 2336 | 20230314 | 2345 | 2044861 | 9 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 36 | 37.5514 | -119.9249 | Yes | Overcast-Fog-Drizzle;32-90 F | Customer Equipment | Deteriorated | 23-0046006 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1825930 | 0 | EPSS Ckt | N | 2023
79705 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | S1577 | 2023-03-15 | 308 | 20230315 | 1041 | 2045144 | 453 | Distribution Circuit | Environmental/External | Flood/Erosion | 94 | 20022 | 38.0269 | -120.2468 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046057 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 22080 | No | Yes | No | 1825976 | 0 | EPSS Ckt | N | 2023
79740 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | FUSE | S285 | 2023-03-18 | 1559 | 20230320 | 1318 | 2051403 | 2719 | Distribution Circuit | 3rd Party | Other | 1 | 2719 | 37.4931 | -121.3034 | No | Overcast;32-90 F | Anchor or Guy | Broken | 23-0048521 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1827727 | 0 | EPSS Ckt | N | 2023
79783 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321754235327 | 2023-03-21 | 1429 | 20230321 | 1510 | 2057025 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 123 | 37.4663 | -119.8957 | Yes | Overcast-Rain;32-90 F | Secondary | Broken- wire on ground | 23-0049729 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1828448 | 0 | EPSS Ckt | N | 2023
79785 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 7423 | 2023-03-21 | 1437 | 20230321 | 1516 | 2056590 | 39 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 74 | 2886 | 37.4218 | -119.9717 | Yes | Clear-Strong Winds;32-90 F |  |  | 23-0049722 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1828444 | 0 | EPSS Ckt | N | 2023
79805 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 6196 | 2023-03-21 | 1822 | 20230322 | 1209 | 2059831 | 1067 | Distribution Circuit | Equipment Failure/Involved | Overhead | 186 | 15947 | 37.2936 | -119.6478 | Yes | Overcast-Rain;32-90 F | Pole-Wood | Broken | 23-0050001 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1828686 | 0 | EPSS Ckt | N | 2023
79831 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317530435792 | 2023-03-23 | 1730 | 20230323 | 2332 | 2065181 | 362 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 362 | 37.4793 | -121.3521 | No | Clear;32-90 F | Transformer (OH) |  | 23-0051566 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829737 | 0 | EPSS Ckt | N | 2023
79831 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317530435792 | 2023-03-23 | 1730 | 20230323 | 2332 | 2065181 | 362 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 362 | 37.4793 | -121.3521 | No | Clear;32-90 F | Transformer (OH) |  | 23-0051566 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1829737 | 0 | EPSS Ckt | N | 2023
79898 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 2023-03-29 | 2352 | 20230330 | 301 | 2073798 | 189 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 6804 | 37.5512 | -119.9231 | No | Overcast-Fog;32-90 F |  |  | 23-0054725 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831813 | 0 | EPSS Ckt | N | 2023
79901 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27337 | 2023-03-30 | 108 | 20230330 | 418 | 2073824 | 190 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 1710 | 37.8143 | -120.0619 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Normal | 23-0054728 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831816 | 0 | EPSS Ckt | N | 2023
79902 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 13485 | 2023-03-30 | 227 | 20230330 | 1355 | 2073837 | 688 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 916 | 37.5335 | -120.0516 | No | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Deteriorated | 23-0054731 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831819 | 1 | EPSS Ckt | N | 2023
79903 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 2023-03-30 | 347 | 20230330 | 1251 | 2073843 | 544 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 19584 | 37.5512 | -119.9231 | No | Overcast-Fog;32-90 F |  |  | 23-0055016 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1831969 | 0 | EPSS Ckt | N | 2023
79906 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 2023-03-30 | 714 | 20230330 | 1501 | 2073888 | 467 | Distribution Circuit | Environmental/External | Ice or snow | 523 | 77481 | 37.4593 | -119.8997 | No | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken | 23-0054760 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831828 | 0 | EPSS Ckt | N | 2023 | B & GRD
79911 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 2023-03-30 | 903 | 20230330 | 1120 | 2073977 | 137 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 297 | 40689 | 37.5079 | -119.9962 | No | Overcast-Fog;32-90 F |  |  | 23-0054832 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831872 | 0 | EPSS Ckt | N | 2023 | B & GRD
79915 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 90550 | 2023-03-30 | 1039 | 20230330 | 1322 | 2074285 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 53 | 7721 | 37.5151 | -120.052 | No | Overcast;32-90 F |  |  | 23-0054922 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1831935 | 0 | EPSS Ckt | N | 2023 | A & GRD
79977 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 2023-04-07 | 303 | 20230407 | 601 | 2082256 | 178 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 948 | 37.5054 | -120.0424 | No | Overcast;32-90 F |  |  | 23-0058291 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1833980 | 1 | EPSS Ckt | N | 2023
79981 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 24003 | 2023-04-07 | 849 | 20230407 | 917 | 2082463 | 28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 149 | 37.5054 | -120.0424 | No | Overcast;32-90 F |  |  | 23-0058390 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834041 | 1 | EPSS Ckt | N | 2023
79989 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 2023-04-08 | 622 | 20230408 | 820 | 2083032 | 118 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1888 | 37.4684 | -119.7375 | No | Clear;32-90 F |  |  | 23-0058740 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1834185 | 0 | EPSS Ckt | N | 2023
80010 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321737935613 | 2023-04-10 | 1525 | 20230411 | 403 | 2084695 | 758 | Transformer only | Animal | Bird found | 2 | 1516 | 37.4752 | -119.9013 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0059384 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1834694 | 0 | EPSS Ckt | N | 2023
80027 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 2075 | 2023-04-11 | 1837 | 20230412 | 253 | 2085985 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 5456 | 37.2731 | -119.6892 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0059794 | OH | Sus | 31641978 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1834958 | 0 | EPSS Ckt | N | 2023
80028 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 2023-04-12 | 619 | 20230412 | 845 | 2086162 | 146 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 469 | 68474 | 37.5251 | -119.9181 | No | Partly Cloudy;32-90 F |  |  | 23-0059871 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835022 | 0 | EPSS Ckt | N | 2023 | A & B PHASE
80046 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7293 | 2023-04-14 | 802 | 20230414 | 1006 | 2088323 | 124 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 7 | 868 | 37.541 | -119.9184 | No | Clear;32-90 F |  |  | 23-0061069 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1835847 | 0 | EPSS Ckt | N | 2023
80056 | YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | FUSE | 731 | 2023-04-15 | 219 | 20230415 | 501 | 2089017 | 162 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 486 | 37.8824 | -120.401 | No | Clear;32-90 F |  |  | 23-0061302 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1835959 | 0 | EPSS Ckt | N | 2023
80073 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 2023-04-16 | 1948 | 20230416 | 2131 | 2089806 | 103 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 1648 | 37.4684 | -119.7375 | No | Clear;32-90 F |  |  | 23-0061502 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1836192 | 0 | EPSS Ckt | N | 2023
80175 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 1719 | 2023-04-26 | 1701 | 20230426 | 1850 | 2097517 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1090 | 37.9038 | -120.3637 | No | Clear;32-90 F | Circuit Breaker | Normal | 23-0065173 | OH | Sus | 45741474 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1838796 | 0 | EPSS Ckt | N | 2023
80192 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-04-28 | 1517 | 20230428 | 1742 | 2099531 | 145 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1307 | 65621 | 38.0063 | -120.3474 | No | Clear;32-90 F |  |  | 23-0066135 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1839354 | 0 | EPSS Ckt | Y | 2023 | A&B PHASE
80202 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321697437852 | 2023-04-29 | 1847 | 20230430 | 9 | s1839550 | 322 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 644 | 37.5384 | -119.9162 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0066331 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839550 | 0 | EPSS Ckt | N | 2023
80203 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 2023-04-29 | 1856 | 20230430 | 9 | s1839551 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1252 | 37.5386 | -119.9184 | No | Clear;32-90 F | Connector or Splice (OH) | Arcing | 23-0066332 | OH | Sus | 45745152 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1839551 | 0 | EPSS Ckt | N | 2023
80213 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322091842979 | 2023-05-01 | 1307 | 20230502 | 653 | 2101628 | 1066 | Transformer only | Vegetation | Tree - fell into line | 7 | 7462 | 37.6777 | -119.778 | No | Clear;32-90 F | Service conductor | Broken- wire on ground | 23-0066771 | OH | Sus | 45745946 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1839941 | 0 | EPSS Ckt | N | 2023
80239 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | SWITCH | PS0295 | 2023-05-03 | 813 | 20230503 | 1438 | 2103416 | 385 | Distribution Circuit | 3rd Party | Other | 6 | 2310 | 37.1477 | -119.4623 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 23-0067651 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1840512 | 0 | EPSS Ckt | N | 2023
80240 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 2023-05-03 | 813 | 20230504 | 116 | 2103920 | 1023 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7161 | 37.1556 | -119.4744 | No | Partly Cloudy;32-90 F | Insulator | Broken | 23-0067748 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1840550 | 0 | EPSS Ckt | N | 2023 | FORCE OUT
80340 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 22402 | 2023-05-11 | 1623 | 20230511 | 2320 | 2110577 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 222 | 37.8904 | -120.3063 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0071107 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1842645 | 0 | EPSS Ckt | N | 2023
80349 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321709538394 | 2023-05-12 | 920 | 20230512 | 1053 | 2111108 | 93 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 186 | 37.5525 | -119.9112 | No | Clear;32-90 F | Other | Broken | 23-0071290 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1842841 | 0 | EPSS Ckt | N | 2023
80368 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L1227 | 2023-05-16 | 1258 | 20230516 | 1422 | 2114200 | 84 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 84 | 37.9327 | -120.2534 | No | Clear;32-90 F |  |  | 23-0072390 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1843658 | 0 | EPSS Ckt | N | 2023
80372 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 2311 | 2023-05-16 | 1951 | 20230517 | 47 | 2114461 | 296 | Distribution Circuit | Equipment Failure/Involved | Underground | 123 | 36408 | 37.3383 | -119.7083 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0072485 | UG | Sus | 31645733 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1843705 | 1 | EPSS Ckt | N | 2023
80389 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321444536688 | 2023-05-17 | 1620 | 20230517 | 2147 | 2115240 | 327 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 981 | 37.505 | -120.003 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0072891 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1844024 | 0 | EPSS Ckt | N | 2023
80410 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ 2 S/E OF 23936 | 2023-05-20 | 1247 | 20230520 | 1534 | 2117640 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 4509 | 37.7214 | -120.1175 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0073820 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1844692 | 0 | EPSS Ckt | N | 2023
80431 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 5673 | 2023-05-23 | 1218 | 20230523 | 1309 | 2119755 | 51 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 1428 | 37.2893 | -119.6522 | No | Clear;32-90 F | Conductor- Overhead | Broken | 23-0074666 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845358 | 0 | EPSS Ckt | N | 2023
80436 | YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | JUMPER | PRIMARY METERING FUSES | 2023-05-23 | 1945 | 20230523 | 2057 | 2120070 | 72 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 72 | 38.1451 | -120.3799 | No | Clear;32-90 F | Other | Malfunctioning | 23-0074872 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845431 | 0 | EPSS Ckt | N | 2023
80438 | YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | TRANSFORMER | 320347559920 | 2023-05-23 | 2235 | 20230524 | 52 | 2120164 | 137 | Transformer only | 3rd Party | Customer Equipment | 1 | 137 | 38.1451 | -120.38 | No | Clear;32-90 F | Other | Malfunctioning | 23-0074905 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1845461 | 0 | EPSS Ckt | N | 2023
80456 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | OCB | 1104/2 | 2023-05-27 | 406 | 20230528 | 1858 | 2122481 | 1460 | Distribution Circuit | Equipment Failure/Involved | Underground | 629 | 213599 | 37.6655 | -119.8413 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0076259 | UG | Sus | 0 | CENTRAL VALLEY | MAY | Three Phase Fault | 0 | No | No | No | 1846279 | 0 | EPSS Ckt | Y | 2023 | A- B- C
80502 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 2023-06-04 | 1031 | 20230604 | 1403 | 2128386 | 212 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 48548 | 37.7156 | -120.1933 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078696 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1847806 | 0 | EPSS Ckt | Y | 2023 | A&C PH
80503 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320932244803 | 2023-06-04 | 1825 | 20230605 | 1417 | 2128610 | 1192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1192 | 37.7318 | -120.1787 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078775 | OH | Sus | 35452855 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847876 | 0 | EPSS Ckt | N | 2023
80503 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320932244803 | 2023-06-04 | 1825 | 20230605 | 1417 | 2128610 | 1192 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 1192 | 37.7318 | -120.1787 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0078775 | OH | Sus | 35452855 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1847876 | 0 | EPSS Ckt | N | 2023
80554 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27343 | 2023-06-09 | 1219 | 20230609 | 1830 | 2133627 | 371 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 742 | 37.824 | -119.9633 | No | Clear;32-90 F | Insulator | Broken | 23-0080844 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1849404 | 0 | EPSS Ckt | N | 2023
80567 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322164243810 | 2023-06-12 | 1322 | 20230612 | 1508 | 2135405 | 106 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 742 | 37.6992 | -119.753 | No | Overcast-Rain;32-90 F | Secondary | Broken | 23-0081584 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850030 | 0 | EPSS Ckt | N | 2023
80569 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321543748307 | 2023-06-13 | 1500 | 20230613 | 1541 | 2136257 | 41 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 41 | 37.825 | -119.966 | No | Partly Cloudy;32-90 F | Crossarm- Wood | Broken | 23-0082003 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1850354 | 0 | EPSS Ckt | N | 2023
80574 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | FUSE | 10408 | 2023-06-14 | 56 | 20230614 | 1426 | 2136504 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 15900 | 37.3671 | -119.6088 | No | Clear;32-90 F | Crossarm- Wood | Broken | 23-0082122 | OH | Sus | 31652264 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1850431 | 0 | EPSS Ckt | N | 2023
80621 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320356549565 | 2023-06-21 | 830 | 20230621 | 903 | 2142031 | 33 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 66 | 37.8616 | -120.3773 | No | Clear;32-90 F | Insulator | Burned/flashed | 23-0084168 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852085 | 0 | EPSS Ckt | N | 2023
80626 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2023-06-22 | 152 | 20230622 | 942 | 2142809 | 470 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 608 | 285760 | 37.8306 | -120.2367 | No | Clear;32-90 F |  |  | 23-0084507 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1852285 | 0 | EPSS Ckt | Y | 2023 | B- GRD
80630 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | FUSE | 20435 | 2023-06-22 | 1500 | 20230622 | 1820 | 2143293 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 800 | 37.8588 | -120.3871 | No | Clear;32-90 F | Pole-Wood | Broken | 23-0084767 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852480 | 0 | EPSS Ckt | N | 2023
80631 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | SWITCH | 10351 | 2023-06-23 | 930 | 20230623 | 1325 | 2143870 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 14335 | 37.6775 | -119.7744 | No | Clear;32-90 F | Insulator | Broken | 23-0084951 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1852628 | 0 | EPSS Ckt | N | 2023
80676 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | JUMPER | OJ 2 N/OF MTR# 1007092897 | 2023-06-27 | 2013 | 20230627 | 2232 | 2147320 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 834 | 37.7582 | -120.1483 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 23-0086319 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1853554 | 0 | EPSS Ckt | N | 2023
80698 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320419456018 | 2023-06-30 | 1204 | 20230630 | 2022 | 2149925 | 498 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 498 | 38.0381 | -120.3554 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0087643 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1854398 | 0 | EPSS Ckt | N | 2023
80785 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321116744048 | 2023-07-07 | 2005 | 20230708 | 300 | 2156582 | 415 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 415 | 37.7113 | -120.1151 | No | Clear;32-90 F | Transformer (OH) | Leaking | 23-0090028 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1855772 | 0 | EPSS Ckt | N | 2023
80801 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 2023-07-09 | 1742 | 20230710 | 906 | 2157812 | 924 | Distribution Circuit | Animal | Bird found | 2674 | 936774 | 37.4831 | -119.9631 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0090255 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Multi-Fault | 0 | No | No | No | 1855985 | 0 | EPSS Ckt | Y | 2023 | GRD INST
80837 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321472439015 | 2023-07-13 | 1500 | 20230714 | 517 | 2161844 | 857 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 857 | 37.5692 | -119.9938 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0092092 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1857282 | 0 | EPSS Ckt | N | 2023
80843 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 26467 | 2023-07-14 | 1744 | 20230714 | 2027 | 2162880 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 326 | 38.0245 | -120.3342 | No | Clear;Above 90 | Pole-Wood | Deteriorated | 23-0092442 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1857544 | 0 | EPSS Ckt | N | 2023
80901 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4707 | 2023-07-20 | 1410 | 20230720 | 1551 | 2168945 | 101 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 6161 | 37.5588 | -119.9703 | No | Clear;Above 90 | Insulator | Broken | 23-0094764 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859129 | 0 | EPSS Ckt | N | 2023
80911 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320858544478 | 2023-07-21 | 1945 | 20230721 | 2037 | 2170343 | 52 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 52 | 37.7238 | -120.2044 | No | Clear;Above 90 | Transformer (OH) | Failed/Faulted | 23-0095433 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1859499 | 0 | EPSS Ckt | N | 2023
80936 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320860356323 | 2023-07-25 | 933 | 20230725 | 1034 | 2173336 | 61 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 61 | 38.046 | -120.2018 | No | Clear;32-90 F | Cutout- fuse holder | Failed/Faulted | 23-0096379 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1860328 | 0 | EPSS Ckt | N | 2023
81008 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-08-05 | 710 | 20230805 | 1031 | 2182853 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1310 | 262358 | 38.0063 | -120.3474 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0100845 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1863228 | 0 | EPSS Ckt | Y | 2023 | B & C
81016 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | TRANSFORMER | 322476628875 | 2023-08-06 | 1559 | 20230806 | 1703 | 2183714 | 64 | Transformer only | Vegetation | Tree - fell into line | 1 | 64 | 37.2903 | -119.6498 | No | Clear;Above 90 | Transformer (OH) | Broken | 23-0101033 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1863433 | 0 | EPSS Ckt | N | 2023
81046 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 2023-08-11 | 1002 | 20230811 | 1020 | 2188528 | 18 | Distribution Circuit | Company Initiated | Personnel- company | 502 | 9036 | 37.4593 | -119.8997 | No | Partly Cloudy;32-90 F | Fuse | Normal | 23-0103200 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1864951 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
81059 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320118054188 | 2023-08-13 | 1505 | 20230813 | 2204 | 2189687 | 419 | Transformer only | Vegetation | Tree - fell into line | 1 | 419 | 37.9884 | -120.4609 | No | Partly Cloudy;32-90 F | Transformer (OH) | Leaking | 23-0103773 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1865358 | 0 | EPSS Ckt | N | 2023
81060 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | OCB | 1104/2 | 2023-08-13 | 1525 | 20230814 | 45 | 2189680 | 560 | Distribution Circuit | Environmental/External | Lightning | 630 | 50310 | 37.6655 | -119.8413 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Burned/flashed | 23-0103765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Multi-Fault | 0 | No | No | No | 1865351 | 0 | EPSS Ckt | Y | 2023 | BC&GRD
81064 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-08-13 | 1802 | 20230814 | 1044 | 2189730 | 1002 | Distribution Circuit | Environmental/External | Lightning | 2013 | 888641 | 38.0063 | -120.3474 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 23-0103777 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1865363 | 0 | EPSS Ckt | Y | 2023 | B&C PHASE
81106 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | OCB | 2102/2 | 2023-08-17 | 1647 | 20230817 | 2011 | 2194001 | 204 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3330 | 567418 | 37.5045 | -120.0076 | No | Clear;Above 90 | Jumper | Burned Open | 23-0105744 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1866586 | 0 | EPSS Ckt | Y | 2023 | PH- GRD- INSTANTANEOUS
81107 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 2023-08-17 | 1727 | 20230818 | 114 | 2194055 | 467 | Distribution Circuit | 3rd Party | Vehicle | 1871 | 451625 | 37.8308 | -120.2369 | No | Clear;Above 90 | Pole-Wood | Broken | 23-0105765 | OH | Sus | 35481654 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1866593 | 0 | EPSS Ckt | Y | 2023 | B & C
81128 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 929360 | 2023-08-19 | 1921 | 20230819 | 2031 | 2196275 | 70 | Distribution Circuit | Vegetation | Tree - fell into line | 2863 | 197604 | 37.4926 | -119.9661 | No | Overcast-Drizzle-Lightning;32-90 F | Pole-Wood | Broken | 23-0106462 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1867128 | 0 | EPSS Ckt | Y | 2023 | A B INST
81143 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10952 | 2023-08-19 | 2110 | 20230820 | 2108 | 2196479 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4314 | 37.5622 | -119.9626 | No | Overcast-Drizzle;32-90 F | Pole-Wood | Broken | 23-0106716 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867364 | 0 | EPSS Ckt | N | 2023
81186 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 2023-08-22 | 1017 | 20230822 | 1050 | 2199199 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2666 | 84564 | 37.4831 | -119.9631 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0107498 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1867994 | 0 | EPSS Ckt | Y | 2023 | A- GRD
81187 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 2023-08-22 | 1057 | 20230822 | 1336 | 2199234 | 159 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 159 | 37.4496 | -119.8923 | No | Clear;32-90 F | Transformer (OH) | Broken | 23-0107533 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868010 | 0 | EPSS Ckt | N | 2023
81202 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10506 | 2023-08-24 | 1102 | 20230824 | 1726 | 2201242 | 384 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 21 | 8064 | 37.5019 | -119.9772 | No | Clear;32-90 F | Conductor- Underground | Broken | 23-0108615 | UG | Sus | 45940200 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868691 | 0 | EPSS Ckt | N | 2023
81203 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320865756210 | 2023-08-24 | 1148 | 20230824 | 1427 | 2201281 | 159 | Transformer only | Unknown Cause | Patrol - found nothing | 3 | 477 | 38.0429 | -120.2001 | No | Clear;32-90 F |  |  | 23-0108715 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1868735 | 0 | EPSS Ckt | N | 2023
81206 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | SWITCH | 929360 | 2023-08-25 | 854 | 20230825 | 1041 | 2201948 | 107 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2876 | 112968 | 37.4926 | -119.9661 | No | Clear;32-90 F |  |  | 23-0108983 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Three Phase Fault | 0 | No | No | No | 1868960 | 0 | EPSS Ckt | Y | 2023
81207 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 7204 | 2023-08-25 | 859 | 20230825 | 1616 | 2201997 | 437 | Distribution Circuit | Equipment Failure/Involved | Underground | 227 | 10383 | 37.4953 | -119.9805 | No | Clear;32-90 F | Conductor- Underground | Deteriorated | 23-0109106 | UG | Sus | 45941259 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869022 | 0 | EPSS Ckt | N | 2023
81215 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | TRANSFORMER | 322153043779 | 2023-08-27 | 1107 | 20230828 | 1101 | 2203300 | 1434 | Transformer only | Equipment Failure/Involved | Overhead | 7 | 10038 | 37.6984 | -119.757 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0109554 | OH | Sus | 35484262 | CENTRAL VALLEY | AUG | Line to Ground | 0 | No | No | No | 1869346 | 0 | EPSS Ckt | N | 2023
81300 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | JUMPER | OJ @ HARDTAP SOURCE SIDE MTR 1011054998 | 2023-09-07 | 1105 | 20230907 | 1225 | 2211743 | 80 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 80 | 37.9973 | -120.4501 | No | Clear;32-90 F | Bushing | Broken | 23-0113607 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1871898 | 0 | EPSS Ckt | N | 2023
81338 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 2023-09-09 | 1310 | 20230910 | 100 | 2213752 | 710 | Distribution Circuit | Environmental/External | Lightning | 229 | 43188 | 37.7156 | -120.1933 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114468 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872410 | 0 | EPSS Ckt | Y | 2023 | A & C
81369 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-09-09 | 1708 | 20230910 | 2205 | 2213971 | 1737 | Distribution Circuit | Environmental/External | Lightning | 1298 | 1100374 | 38.0063 | -120.3474 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114521 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872451 | 0 | EPSS Ckt | Y | 2023 | BC
81370 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L1411 | 2023-09-09 | 1708 | 20230910 | 2208 | 2214521 | 1740 | Distribution Circuit | Environmental/External | Lightning | 13 | 16249 | 38.0384 | -120.3554 | Yes | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114521 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872561 | 0 | EPSS Ckt | N | 2023
81410 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 2023-09-10 | 444 | 20230911 | 1617 | 2214448 | 2133 | Distribution Circuit | Environmental/External | Lightning | 139 | 131160 | 38.0064 | -120.3467 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114613 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872551 | 0 | EPSS Ckt | Y | 2023 | B GRD
81416 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 100000056020 | 2023-09-10 | 753 | 20230911 | 1821 | 2214546 | 2068 | Transformer only | Environmental/External | Lightning | 1 | 2068 | 38.0355 | -120.3504 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114943 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872963 | 0 | EPSS Ckt | N | 2023
81418 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320426855933 | 2023-09-10 | 808 | 20230911 | 1715 | 2214596 | 1987 | Transformer only | Environmental/External | Lightning | 1 | 1987 | 38.0358 | -120.3528 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114913 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872943 | 0 | EPSS Ckt | N | 2023
81420 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | FUSE | L443 | 2023-09-10 | 830 | 20230910 | 1456 | 2214581 | 386 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 108 | 41688 | 37.9891 | -120.4626 | No | Clear;32-90 F |  |  | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1872642 | 0 | EPSS Ckt | N | 2023
81422 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320123254232 | 2023-09-10 | 830 | 20230911 | 1040 | 2214787 | 1570 | Transformer only | Equipment Failure/Involved | Electrical Overload | 4 | 6280 | 37.9892 | -120.4593 | No | Clear;32-90 F | Transformer | Broken | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872647 | 0 | EPSS Ckt | N | 2023
81423 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320113454238 | 2023-09-10 | 830 | 20230911 | 913 | 2214788 | 1483 | Transformer only | Environmental/External | Lightning | 2 | 2966 | 37.9898 | -120.4621 | No | Clear;32-90 F | Transformer | Broken | 23-0114682 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872648 | 0 | EPSS Ckt | N | 2023
81428 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320420056136 | 2023-09-10 | 854 | 20230912 | 1037 | 2215430 | 2983 | Transformer only | Environmental/External | Lightning | 1 | 2983 | 38.0414 | -120.3552 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114886 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872930 | 0 | EPSS Ckt | N | 2023
81434 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320420556107 | 2023-09-10 | 951 | 20230911 | 1928 | 2215406 | 2017 | Transformer only | Environmental/External | Lightning | 3 | 6051 | 38.0405 | -120.3549 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114876 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872919 | 0 | EPSS Ckt | N | 2023
81452 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 2023-09-10 | 1719 | 20230910 | 2018 | 2214865 | 179 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2673 | 251677 | 37.4831 | -119.9631 | No | Clear;32-90 F |  |  | 23-0114711 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872668 | 0 | EPSS Ckt | Y | 2023 | B GRD
81458 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320499155246 | 2023-09-10 | 1942 | 20230911 | 1633 | 2214960 | 1251 | Transformer only | Environmental/External | Lightning | 1 | 1251 | 38.0171 | -120.3275 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0114921 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872952 | 0 | EPSS Ckt | N | 2023
81465 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | FUSE | L1169 | 2023-09-10 | 2048 | 20230910 | 2349 | 2214989 | 181 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 70 | 12670 | 38.0252 | -120.2416 | No | Clear;32-90 F |  |  | 23-0114757 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1872727 | 0 | EPSS Ckt | N | 2023
81475 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 36888 | 2023-09-11 | 115 | 20230911 | 1640 | 2215344 | 925 | Distribution Circuit | Environmental/External | Lightning | 276 | 255300 | 38.0285 | -120.2514 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0114758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1872887 | 0 | EPSS Ckt | Y | 2023 | NONE
81483 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320407056135 | 2023-09-11 | 946 | 20230911 | 1240 | 2215431 | 174 | Transformer only | Environmental/External | Lightning | 2 | 348 | 38.0415 | -120.3596 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0115078 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1873017 | 0 | EPSS Ckt | N | 2023
81493 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 322200535289 | 2023-09-11 | 1310 | 20230911 | 1331 | 2215606 | 21 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 21 | 37.4656 | -119.7434 | No | Partly Cloudy;32-90 F | Pole-Wood | Normal | 23-0115026 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873004 | 0 | EPSS Ckt | N | 2023
81526 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 2023-09-12 | 2006 | 20230913 | 34 | 2217075 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 904 | 242272 | 37.6313 | -120.1536 | No | Clear;32-90 F | Conductor- Overhead | Normal | 23-0115714 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1873433 | 0 | EPSS Ckt | Y | 2023 | N/A
81542 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 321429448365 | 2023-09-14 | 1135 | 20230914 | 2140 | 2218826 | 605 | Transformer only | Equipment Failure/Involved | Electrical Overload | 2 | 1210 | 37.826 | -120.0089 | No | Clear;32-90 F | Transformer | Failed/Faulted | 23-0116733 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874075 | 0 | EPSS Ckt | N | 2023
81543 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 2023-09-14 | 1553 | 20230914 | 1719 | 2219043 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 4214 | 37.5217 | -119.9394 | No | Clear;32-90 F | Other | Broken | 23-0116804 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1874090 | 0 | EPSS Ckt | N | 2023
81575 | YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | TRANSFORMER | 319886551808 | 2023-09-17 | 1310 | 20230917 | 1745 | 2221047 | 275 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 550 | 37.9216 | -120.5401 | No | Partly Cloudy;32-90 F | Transformer (OH) | Failed/Faulted | 23-0117557 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874637 | 0 | EPSS Ckt | N | 2023
81587 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 851902 | 2023-09-18 | 1805 | 20230918 | 2024 | 2221944 | 139 | Distribution Circuit | Animal | Bird found | 2673 | 218506 | 37.4831 | -119.9631 | No | Clear;32-90 F | Transformer (OH) | Normal | 23-0117987 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1874964 | 0 | EPSS Ckt | Y | 2023 | A GRD
81592 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321567437873 | 2023-09-19 | 915 | 20230919 | 1006 | 2222256 | 51 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 51 | 37.5381 | -119.9608 | No | Clear;32-90 F | Secondary | Broken | 23-0118093 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Force Out | 0 | No | No | No | 1875106 | 0 | EPSS Ckt | N | 2023
81600 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321770934816 | 2023-09-19 | 2207 | 20230919 | 2339 | 2222816 | 92 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 92 | 37.4522 | -119.8896 | No | Clear;32-90 F | Fuse | Failed/Faulted | 23-0118477 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875319 | 0 | EPSS Ckt | N | 2023
81606 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 2023-09-21 | 821 | 20230921 | 1147 | 2223839 | 206 | Distribution Circuit | Animal | Squirrel | 2562 | 284650 | 37.8844 | -120.3058 | No | Partly Cloudy;32-90 F | Pothead(Riser Termination) | Normal | 23-0119095 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1875720 | 0 | EPSS Ckt | Y | 2023 | C PHASE & GRD
81661 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 2023-09-28 | 925 | 20230928 | 1055 | 2229334 | 90 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 903 | 81270 | 37.6313 | -120.1536 | No | Clear;32-90 F |  |  | 23-0121950 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1877562 | 0 | EPSS Ckt | Y | 2023 | BC
81702 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | JUMPER | OJ 2 SW/OF MTR# 1006942508 | 2023-10-04 | 1230 | 20231004 | 1430 | 2234680 | 120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 240 | 37.3594 | -119.6036 | No | Clear;32-90 F | Connector or Splice (OH) | Broken | 23-0124387 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1879325 | 0 | EPSS Ckt | N | 2023
81854 | YOSEMITE | STANISLAUS | STANISLAUS-1701 | 162821701 | SWITCH | L6223 | 2023-10-24 | 835 | 20231024 | 1640 | 2250408 | 485 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 485 | 38.1453 | -120.3796 | No | Clear;32-90 F | Switch (OH) | Normal | 23-0131666 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1884470 | 0 | EPSS Ckt | N | 2023
81867 | YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 169700 | 2023-10-26 | 659 | 20231026 | 1117 | 2252111 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1506 | 388548 | 37.8364 | -120.2605 | No | Clear-Drizzle;32-90 F |  |  | 23-0132696 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885102 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
81867 | YOSEMITE | STANISLAUS | PEORIA FLAT-1705 | 163781705 | RECLOSER | 169700 | 2023-10-26 | 659 | 20231026 | 1117 | 2252111 | 258 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1506 | 388548 | 37.8364 | -120.2605 | No | Clear-Drizzle;32-90 F |  |  | 23-0132696 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1885102 | 0 | EPSS Ckt | Y | 2023 | A- C- INST
81902 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 2023-11-01 | 1141 | 20231101 | 1650 | s1887175 | 309 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 722 | 220183 | 38.0064 | -120.3467 | No | Clear;32-90 F |  |  | 23-0126234 | OH | Sus | 31662048 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | Yes | No | No | 1887175 | 0 | EPSS Ckt | Y | 2023 | A/B/C
81925 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 1960 | 2023-11-04 | 336 | 20231104 | 537 | 2259661 | 121 | Distribution Circuit | Animal | Other | 959 | 100240 | 37.4587 | -119.9001 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 23-0135837 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887672 | 0 | EPSS Ckt | Y | 2023 | B PH & GRD
81933 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 321171543701 | 2023-11-05 | 2029 | 20231106 | 415 | 2260698 | 466 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 932 | 37.7014 | -120.096 | No | Overcast;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136076 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1887959 | 0 | EPSS Ckt | N | 2023
81943 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 75413 | 2023-11-06 | 951 | 20231106 | 1147 | 2261480 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 27 | 3132 | 37.5797 | -119.8523 | No | Partly Cloudy;32-90 F |  |  | 23-0136239 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1888176 | 0 | EPSS Ckt | N | 2023
81955 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | RECLOSER | 1960 | 2023-11-07 | 1622 | 20231107 | 2353 | 2263101 | 451 | Distribution Circuit | Company Initiated | Personnel- company | 959 | 20310 | 37.4587 | -119.9001 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 23-0136854 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1888634 | 0 | EPSS Ckt | N | 2023 | C & GRD
82029 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | SWITCH | 299321 | 2023-11-18 | 2000 | 20231118 | 2152 | 2273160 | 112 | Distribution Circuit | 3rd Party | Vehicle | 55 | 6160 | 37.9908 | -120.4618 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken | 23-0140977 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1891648 | 0 | EPSS Ckt | N | 2023
82047 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 2023-11-22 | 625 | 20231122 | 953 | 2275493 | 208 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 139 | 28912 | 38.0064 | -120.3467 | No | Partly Cloudy;32-90 F |  |  | 23-0142140 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892297 | 0 | EPSS Ckt | Y | 2023 | AC
82048 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2023-11-22 | 643 | 20231122 | 916 | 2275497 | 153 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1313 | 200889 | 38.0063 | -120.3474 | No | Partly Cloudy;32-90 F |  |  | 23-0142144 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1892300 | 0 | EPSS Ckt | Y | 2023 | AB
82050 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320400249270 | 2023-11-22 | 1139 | 20231122 | 1147 | 2275716 | 8 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 8 | 37.8536 | -120.3624 | No | Partly Cloudy;32-90 F | Transformer (OH) | Broken | 23-0142336 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Force Out | 0 | No | No | No | 1892362 | 0 | EPSS Ckt | N | 2023
82121 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | SWITCH | 929360 | 2023-12-02 | 1835 | 20231203 | 936 | 2282438 | 901 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2876 | 196819 | 37.4926 | -119.9661 | No | Partly Cloudy;32-90 F |  |  | 23-0144970 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1894599 | 0 | EPSS Ckt | Y | 2023
82146 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321434033592 | 2023-12-06 | 937 | 20231206 | 1646 | 2285038 | 429 | Transformer only | Company Initiated | Personnel- company | 1 | 429 | 37.4202 | -120.0073 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 23-0145850 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895608 | 0 | EPSS Ckt | N | 2023
82148 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 2023-12-06 | 1212 | 20231206 | 2225 | 2285341 | 613 | Transformer only | Vegetation | Tree - fell into line | 1 | 613 | 37.4496 | -119.8923 | No | Partly Cloudy;32-90 F | Service conductor | Broken- wire on ground | 23-0146032 | OH | Sus | 46080161 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895701 | 0 | EPSS Ckt | N | 2023
82149 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320759453760 | 2023-12-06 | 1247 | 20231206 | 1424 | 2285219 | 97 | Transformer only | 3rd Party | Vehicle | 1 | 97 | 37.976 | -120.2375 | No | Overcast;32-90 F | Transformer (OH) | Broken | 23-0145948 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1895661 | 0 | EPSS Ckt | N | 2023
82155 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 10070 | 2023-12-08 | 1059 | 20231208 | 1322 | 2287014 | 143 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 297 | 42471 | 37.5079 | -119.9962 | No | Clear;32-90 F |  |  | 23-0146492 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1896251 | 0 | EPSS Ckt | Y | 2023 | B PH
82195 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 4190 | 2023-12-15 | 1254 | 20231215 | 2000 | 2292622 | 426 | Distribution Circuit | 3rd Party | Vehicle | 2832 | 347077 | 37.5051 | -120.038 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147584 | OH | Sus | 35517751 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1898182 | 0 | EPSS Ckt | Y | 2023 | SGF
82195 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 4190 | 2023-12-15 | 1254 | 20231215 | 2000 | 2292622 | 426 | Distribution Circuit | 3rd Party | Vehicle | 2832 | 347077 | 37.5051 | -120.038 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0147584 | OH | Sus | 35517751 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1898182 | 0 | EPSS Ckt | Y | 2023 | SGF
82282 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | 921 | 2023-12-24 | 659 | 20231224 | 919 | 2299057 | 140 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 75 | 10500 | 38.0203 | -120.3351 | No | Partly Cloudy;32-90 F |  |  | 23-0148740 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1899808 | 0 | EPSS Ckt | N | 2023
82395 | YOSEMITE | YOSEMITE | OAKHURST-1103 | 254421103 | JUMPER | TSB 1 SPAN LD SIDE OF CGC# 322616331511 | 2024-01-11 | 1201 | 20240111 | 1552 | 2312852 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2541 | 37.3629 | -119.5996 | No | Overcast-Strong Winds;32-90 F | Pole-Wood | Deteriorated | 24-0009525 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Force Out | 0 | No | No | No | 1903303 | 0 | EPSS Ckt | N | 2024
82404 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10948 | 2024-01-13 | 713 | 20240113 | 827 | 2314458 | 74 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 46 | 3404 | 37.5608 | -119.9664 | No | Overcast-Rain;32-90 F |  |  | 24-0010415 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1903746 | 0 | EPSS Ckt | N | 2024
82410 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10338 | 2024-01-14 | 852 | 20240114 | 1402 | 2315249 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6200 | 37.2814 | -119.6699 | No | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Together | 24-0010669 | OH | Sus | 46153485 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1903963 | 0 | EPSS Ckt | N | 2024
82438 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320590550575 | 2024-01-19 | 1336 | 20240119 | 1819 | 2319214 | 283 | Transformer only | Equipment Failure/Involved | Underground | 1 | 283 | 37.8874 | -120.2967 | No | Overcast;32-90 F | Secondary | Broken | 24-0012777 | UG | Sus | 46166004 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905126 | 0 | EPSS Ckt | N | 2024
82444 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321648036719 | 2024-01-21 | 11 | 20240121 | 845 | 2320268 | 514 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 514 | 37.5068 | -119.9322 | No | Overcast-Fog;32-90 F | Transformer (OH) | Broken | 24-0013050 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1905320 | 0 | EPSS Ckt | N | 2024
82476 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321485939000 | 2024-01-24 | 1217 | 20240124 | 1320 | 2323152 | 63 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 63 | 37.5681 | -119.9888 | No | Overcast-Drizzle;32-90 F |  |  | 24-0014493 | OH | Sus | 0 | CENTRAL VALLEY | JAN | None | 0 | No | No | No | 1906085 | 0 | EPSS Ckt | N | 2024
82494 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | OCB | 2101/2 | 2024-01-28 | 915 | 20240128 | 1017 | 2326302 | 62 | Distribution Circuit | Animal | Bird found | 3840 | 237324 | 37.5045 | -120.0077 | No | Partly Cloudy;32-90 F | Circuit Breaker | Normal | 24-0015949 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Ground | 0 | No | No | No | 1906921 | 0 | EPSS Ckt | N | 2024 | C GRD INST
82527 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 2024-01-31 | 2054 | 20240131 | 2207 | 2330461 | 73 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 12410 | 37.5637 | -119.8544 | No | Overcast-Drizzle;32-90 F | Conductor- Overhead | Normal | 24-0017692 | OH | Sus | 0 | CENTRAL VALLEY | JAN | Line to Line | 0 | No | No | No | 1908087 | 0 | EPSS Ckt | N | 2024
82623 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2024-02-04 | 1540 | 20240205 | 1443 | 2344386 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 600145 | 37.8306 | -120.2367 | Yes | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020287 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | Yes | No | 1910116 | 0 | EPSS Ckt | N | 2024 | B & C
82655 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2024-02-04 | 1741 | 20240205 | 146 | 2349462 | 485 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 17945 | 37.9718 | -120.2261 | Yes | Overcast-Fog-Rain-Strong Winds;32-90 F |  |  | 24-0021376 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1911209 | 0 | EPSS Ckt | N | 2024
82699 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317470036577 | 2024-02-06 | 1900 | 20240207 | 1150 | 2365525 | 1010 | Transformer only | Unknown Cause | Patrol - not conducted | 7 | 7070 | 37.5019 | -121.3733 | No | Partly Cloudy;32-90 F |  |  | 24-0023751 | OH | Sus | 0 | CENTRAL VALLEY | FEB | None | 0 | No | No | No | 1913135 | 0 | EPSS Ckt | N | 2024
82715 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 2024-02-07 | 1952 | 20240208 | 55 | 2368733 | 303 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 909 | 37.7222 | -120.1193 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0025374 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1914395 | 0 | EPSS Ckt | N | 2024
82728 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 2493 | 2024-02-08 | 651 | 20240209 | 1035 | 2369155 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9984 | 37.5386 | -119.9184 | No | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026402 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915190 | 0 | EPSS Ckt | N | 2024
82729 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 5587 | 2024-02-08 | 707 | 20240209 | 1212 | 2369461 | 1745 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 3490 | 37.3373 | -119.7669 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026047 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915020 | 0 | EPSS Ckt | N | 2024
82731 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | FUSE | 577693 | 2024-02-08 | 737 | 20240209 | 1025 | 2369751 | 1608 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 1608 | 37.3452 | -119.7621 | No | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0026169 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | Yes | No | 1915078 | 0 | EPSS Ckt | N | 2024
82740 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 2841 | 2024-02-08 | 955 | 20240208 | 1316 | 2369554 | 201 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 2410 | 37.5325 | -120.0518 | No | Overcast-Fog;32-90 F |  |  | 24-0026316 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Ground | 0 | No | No | No | 1915147 | 1 | EPSS Ckt | N | 2024
82743 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2024-02-08 | 1139 | 20240208 | 1148 | 2369925 | 9 | Distribution Circuit | Equipment Failure/Involved | Overhead | 448 | 4032 | 37.8306 | -120.2367 | No | Partly Cloudy-Drizzle;32-90 F | Insulator | Broken | 24-0026224 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Force Out | 0 | No | No | No | 1915104 | 0 | EPSS Ckt | N | 2024 | N/A
82758 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2024-02-11 | 1737 | 20240211 | 2202 | 2373450 | 265 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 89 | 23585 | 37.7148 | -120.0964 | No | Clear;32-90 F |  |  | 24-0027654 | OH | Sus | 0 | CENTRAL VALLEY | FEB | Line to Line | 0 | No | No | No | 1916071 | 0 | EPSS Ckt | N | 2024
82881 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L1227 | 2024-03-01 | 1056 | 20240301 | 1142 | 2391984 | 46 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1 | 46 | 37.9327 | -120.2534 | Yes | Overcast-Rain;32-90 F |  |  | 24-0036061 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921304 | 0 | EPSS Ckt | N | 2024
82887 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321523737906 | 2024-03-01 | 1601 | 20240301 | 2002 | 2392564 | 241 | Transformer only | Environmental/External | Lightning | 1 | 241 | 37.5392 | -119.9763 | Yes | Overcast-Rain;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036319 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921399 | 0 | EPSS Ckt | N | 2024
82888 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 2024-03-01 | 1603 | 20240301 | 1640 | 2392495 | 37 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 49 | 1813 | 37.5217 | -119.9394 | Yes | Overcast-Fog-Rain-Lightning;32-90 F |  |  | 24-0036277 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921386 | 0 | EPSS Ckt | N | 2024
82892 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321523737815 | 2024-03-01 | 1848 | 20240302 | 1059 | 2392858 | 971 | Transformer only | Environmental/External | Lightning | 1 | 971 | 37.5365 | -119.9762 | Yes | Overcast-Fog-Rain-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0036452 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1921497 | 0 | EPSS Ckt | N | 2024
82908 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-03-02 | 252 | 20240302 | 1620 | 2394250 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 1314 | 693379 | 38.0063 | -120.3474 | No | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036653 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921697 | 0 | EPSS Ckt | N | 2024 | B- GRD
82910 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2024-03-02 | 315 | 20240302 | 1618 | 2394281 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 20205 | 37.7148 | -120.0964 | No | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036674 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | Yes | No | 1921719 | 0 | EPSS Ckt | N | 2024
82916 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27330 | 2024-03-02 | 659 | 20240302 | 1307 | 2394457 | 368 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2 | 736 | 37.8323 | -120.2135 | No | Overcast-Fog;32-90 F |  |  | 24-0036908 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1921894 | 0 | EPSS Ckt | N | 2024
82926 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320666048460 | 2024-03-03 | 130 | 20240303 | 1444 | 2395683 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3445 | 37.8322 | -120.2697 | No | Overcast-Fog;32-90 F | Transformer (OH) |  | 24-0037100 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922044 | 0 | EPSS Ckt | N | 2024
82926 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320666048460 | 2024-03-03 | 130 | 20240303 | 1444 | 2395683 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3445 | 37.8322 | -120.2697 | No | Overcast-Fog;32-90 F | Transformer (OH) |  | 24-0037100 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1922044 | 0 | EPSS Ckt | N | 2024
83017 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317470036890 | 2024-03-14 | 1210 | 20240314 | 1708 | 2405176 | 298 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 1490 | 37.5105 | -121.3739 | No | Clear;32-90 F |  |  | 24-0042397 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1925223 | 0 | EPSS Ckt | N | 2024
83018 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | TRANSFORMER | 317467836839 | 2024-03-14 | 1210 | 20240314 | 1710 | 2405177 | 300 | Transformer only | Unknown Cause | Patrol - not conducted | 5 | 1500 | 37.509 | -121.3742 | No | Clear;32-90 F |  |  | 24-0042398 | OH | Sus | 0 | CENTRAL VALLEY | MAR | None | 0 | No | No | No | 1925224 | 0 | EPSS Ckt | N | 2024
83020 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 2024-03-14 | 1712 | 20240314 | 1839 | 2405426 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 14790 | 37.5637 | -119.8544 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0042426 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925244 | 0 | EPSS Ckt | N | 2024
83026 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 2024-03-14 | 2352 | 20240315 | 1217 | 2405597 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 272 | 168362 | 38.03 | -120.2447 | No | Clear-Strong Winds;32-90 F | Conductor- Overhead | Normal | 24-0042508 | OH | Sus | 46211869 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1925299 | 0 | EPSS Ckt | N | 2024 | A B C & GRD
83029 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320801954299 | 2024-03-15 | 607 | 20240315 | 1420 | 2405674 | 493 | Transformer only | Vegetation | Tree - fell into line | 3 | 1479 | 37.9912 | -120.2226 | No | Clear;32-90 F | Secondary | Broken- wire on ground | 24-0042532 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Force Out | 0 | No | No | No | 1925324 | 0 | EPSS Ckt | N | 2024
83055 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 27343 | 2024-03-18 | 1619 | 20240318 | 1837 | 2408761 | 138 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 276 | 37.824 | -119.9633 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0043760 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Line | 0 | No | No | No | 1926358 | 0 | EPSS Ckt | N | 2024
83067 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320946044845 | 2024-03-19 | 1615 | 20240320 | 9 | 2409574 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 474 | 37.7329 | -120.1739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044306 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926688 | 0 | EPSS Ckt | N | 2024
83067 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320946044845 | 2024-03-19 | 1615 | 20240320 | 9 | 2409574 | 474 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 474 | 37.7329 | -120.1739 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0044306 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Line to Ground | 0 | No | No | No | 1926688 | 0 | EPSS Ckt | N | 2024
83112 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 2024-03-26 | 100 | 20240326 | 306 | 2414566 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1507 | 186843 | 37.8364 | -120.2605 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0046734 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1928265 | 0 | EPSS Ckt | N | 2024 | ABC
83112 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 2024-03-26 | 100 | 20240326 | 306 | 2414566 | 126 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1507 | 186843 | 37.8364 | -120.2605 | No | Partly Cloudy;32-90 F | Recloser | Malfunctioning | 24-0046734 | OH | Sus | 0 | CENTRAL VALLEY | MAR | Three Phase Fault | 0 | No | No | No | 1928265 | 0 | EPSS Ckt | N | 2024 | ABC
83198 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320897048885 | 2024-04-04 | 1416 | 20240404 | 2250 | 2422605 | 514 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2570 | 37.8423 | -120.1907 | No | Overcast-Fog-Snow-Lightning;Below 32 F | Transformer (OH) | Failed/Faulted | 24-0050975 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1930919 | 0 | EPSS Ckt | N | 2024
83208 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 2841 | 2024-04-05 | 35 | 20240405 | 259 | 2423319 | 144 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 36 | 5184 | 37.5325 | -120.0518 | No | Overcast-Drizzle;32-90 F |  |  | 24-0051110 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931037 | 0 | EPSS Ckt | N | 2024
83215 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-04-05 | 459 | 20240406 | 1259 | 2423415 | 1920 | Distribution Circuit | Vegetation | Tree - fell into line | 1140 | 961052 | 38.0063 | -120.3474 | No | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0051121 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931048 | 0 | EPSS Ckt | N | 2024 | B & C
83244 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 2024-04-05 | 623 | 20240405 | 1713 | 2423551 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 2568 | 389797 | 37.8844 | -120.3058 | No | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0051135 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | Yes | No | 1931059 | 0 | EPSS Ckt | N | 2024 | SGF
83250 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2155 | 2024-04-05 | 823 | 20240406 | 1005 | 2423693 | 1542 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 16 | 24672 | 37.9492 | -120.2562 | No | Overcast-Fog-Snow;32-90 F |  |  | 24-0051720 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931501 | 0 | EPSS Ckt | N | 2024
83252 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | FUSE | 20329 | 2024-04-05 | 828 | 20240406 | 1434 | 2423700 | 1806 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 23 | 41538 | 38.0185 | -120.2184 | No | Overcast-Fog-Snow;Below 32 F |  |  | 24-0051789 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931547 | 0 | EPSS Ckt | N | 2024
83256 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 2024-04-05 | 912 | 20240406 | 7 | 2423866 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 27495 | 37.7148 | -120.0964 | No | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0051467 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | Yes | No | 1931287 | 0 | EPSS Ckt | N | 2024
83274 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 23936 | 2024-04-05 | 1745 | 20240405 | 2114 | 2424768 | 209 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 3 | 627 | 37.7222 | -120.1193 | No | Partly Cloudy;32-90 F |  |  | 24-0051646 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Line | 0 | No | No | No | 1931410 | 0 | EPSS Ckt | N | 2024
83291 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | TRANSFORMER | 320371256507 | 2024-04-06 | 1652 | 20240407 | 1014 | 2425395 | 1042 | Transformer only | Environmental/External | Ice or snow | 1 | 1042 | 38.0516 | -120.3751 | No | Partly Cloudy;32-90 F | Transformer | Contaminated | 24-0051816 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1931563 | 0 | EPSS Ckt | N | 2024
83326 | YOSEMITE | YOSEMITE | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER | OJ 3 POLES S/OF CGC # 323023126726 | 2024-04-10 | 2312 | 20240411 | 206 | 2428173 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 11136 | 37.2291 | -119.4612 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Broken | 24-0053341 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1932594 | 0 | EPSS Ckt | N | 2024
83328 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321764934702 | 2024-04-11 | 1413 | 20240411 | 1714 | 2428718 | 181 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 181 | 37.4496 | -119.8923 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0053682 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1932834 | 0 | EPSS Ckt | N | 2024
83340 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321521733771 | 2024-04-12 | 1520 | 20240412 | 1543 | 2429498 | 23 | Transformer only | Equipment Failure/Involved | Underground | 1 | 23 | 37.4251 | -119.9762 | No | Clear;32-90 F | Secondary | Broken | 24-0054198 | UG | Sus | 46228566 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1933161 | 0 | EPSS Ckt | N | 2024
83384 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10338 | 2024-04-19 | 915 | 20240419 | 1137 | 2434715 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 2840 | 37.2814 | -119.6699 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0056750 | OH | Sus | 0 | CENTRAL VALLEY | APR | Force Out | 0 | No | No | No | 1934917 | 0 | EPSS Ckt | N | 2024
83465 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321768734963 | 2024-04-29 | 1043 | 20240429 | 1400 | 2441629 | 197 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 197 | 37.456 | -119.891 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0059967 | OH | Sus | 0 | CENTRAL VALLEY | APR | Line to Ground | 0 | No | No | No | 1937322 | 0 | EPSS Ckt | N | 2024
83509 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | FUSE | 4618 | 2024-05-04 | 1352 | 20240504 | 1720 | 2445844 | 208 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 11 | 2286 | 37.4886 | -120.0413 | No | Overcast-Rain;32-90 F |  |  | 24-0062164 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1938944 | 1 | EPSS Ckt | N | 2024
83510 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 151918 | 2024-05-04 | 1359 | 20240504 | 1640 | 2445856 | 161 | Distribution Circuit | Animal | Other | 2896 | 466256 | 37.4926 | -119.9657 | No | Overcast-Heavy Rain;32-90 F | Cutout- fuse holder | Normal | 24-0062103 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Multi-Fault | 0 | No | No | No | 1938911 | 0 | EPSS Ckt | N | 2024 | AC TIME
83525 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321424235535 | 2024-05-05 | 1621 | 20240505 | 1738 | 2446548 | 77 | Transformer only | Animal | Other | 1 | 77 | 37.4748 | -120.0083 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0062403 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Ground | 0 | No | No | No | 1939159 | 0 | EPSS Ckt | N | 2024
83543 | YOSEMITE | STANISLAUS | STANISLAUS-1702 | 162821702 | JUMPER | OJ 8SP N/W/OF CGC #320431259717 | 2024-05-08 | 915 | 20240508 | 1059 | 2448546 | 104 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 104 | 38.1434 | -120.3551 | No | Clear;32-90 F | Crossarm- Wood | Deteriorated | 24-0063471 | OH | Sus | 0 | CENTRAL VALLEY | MAY | None | 0 | No | No | No | 1939970 | 0 | EPSS Ckt | N | 2024
83566 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | JUMPER | TSB ES/OF CGC# 320611755029 | 2024-05-10 | 1713 | 20240510 | 2032 | 2450977 | 199 | Distribution Circuit | Animal | Other | 8 | 1592 | 38.0109 | -120.2883 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0064785 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1940745 | 0 | EPSS Ckt | N | 2024
83613 | YOSEMITE | STANISLAUS | PEORIA FLAT-1704 | 163781704 | FUSE | TEMP | 2024-05-17 | 537 | 20240517 | 733 | 2461193 | 116 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 14 | 1472 | 37.9248 | -120.5269 | No | Clear;32-90 F |  |  | 24-0067070 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Line to Line | 0 | No | No | No | 1942232 | 1 | EPSS Ckt | N | 2024
83641 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10315 | 2024-05-22 | 1343 | 20240522 | 1620 | 2465209 | 157 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2512 | 37.4684 | -119.7375 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0068826 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1943535 | 0 | EPSS Ckt | N | 2024
83714 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320063554450 | 2024-05-30 | 1527 | 20240530 | 1542 | 2471104 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 30 | 37.9963 | -120.4781 | No | Clear;32-90 F | Transformer (OH) | Leaking | 24-0071555 | OH | Sus | 0 | CENTRAL VALLEY | MAY | Force Out | 0 | No | No | No | 1945325 | 0 | EPSS Ckt | N | 2024
83743 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 64455 | 2024-06-03 | 917 | 20240603 | 1238 | 2473923 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 804 | 37.4562 | -119.8973 | No | Partly Cloudy;32-90 F | Pole-Wood | Deteriorated | 24-0072484 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1946093 | 0 | EPSS Ckt | N | 2024
83796 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 2024-06-07 | 943 | 20240607 | 1429 | 2479077 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1877 | 273011 | 37.8308 | -120.2369 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0074596 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1947508 | 0 | EPSS Ckt | Y | 2024 | A & GRD
83827 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 10316 | 2024-06-11 | 1625 | 20240611 | 1812 | 2482586 | 107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 4066 | 37.4659 | -119.7355 | No | Clear;32-90 F | Crossarm- Wood | Broken | 24-0075948 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1948500 | 0 | EPSS Ckt | N | 2024
83850 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 2024-06-14 | 1352 | 20240614 | 1958 | 2485701 | 366 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 906 | 196362 | 37.6313 | -120.1536 | No | Clear;32-90 F |  |  | 24-0077174 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | No | No | No | 1949413 | 0 | EPSS Ckt | Y | 2024 | SGF- DCD
83855 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 2024-06-14 | 1939 | 20240615 | 649 | 2485996 | 670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1877 | 395681 | 37.8308 | -120.2369 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0077284 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Line | 0 | No | No | No | 1949448 | 0 | EPSS Ckt | Y | 2024 | AB
83890 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 2024-06-18 | 1221 | 20240618 | 1339 | 2489315 | 78 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 2808 | 37.5512 | -119.9231 | No | Clear;32-90 F | Other | Broken | 24-0078148 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950240 | 0 | EPSS Ckt | N | 2024
83898 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320756055702 | 2024-06-20 | 1150 | 20240620 | 1246 | 2490819 | 56 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 224 | 38.0295 | -120.2387 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0078694 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950615 | 0 | EPSS Ckt | N | 2024
83899 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320288050214 | 2024-06-20 | 1403 | 20240620 | 1522 | 2490914 | 79 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 79 | 37.8789 | -120.4014 | No | Partly Cloudy;32-90 F | Secondary | Broken | 24-0078750 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1950628 | 0 | EPSS Ckt | N | 2024
83920 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 2024-06-22 | 1929 | 20240623 | 205 | 2492728 | 396 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 104948 | 37.6769 | -119.7776 | No | Clear;Above 90 | Recloser | Normal | 24-0079463 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Line to Ground | 0 | Yes | No | No | 1951083 | 0 | EPSS Ckt | Y | 2024 | C INST
83936 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | FUSE | 10703 | 2024-06-24 | 1005 | 20240624 | 1210 | 2493646 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1375 | 37.7197 | -120.2041 | No | Clear;32-90 F | Pole-Wood | Deteriorated | 24-0079699 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Force Out | 0 | No | No | No | 1951367 | 0 | EPSS Ckt | N | 2024
83962 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2024-06-24 | 1604 | 20240625 | 11 | 2494480 | 487 | Distribution Circuit | Environmental/External | Lightning | 611 | 70201 | 37.8306 | -120.2367 | No | Partly Cloudy-Lightning;Above 90 | Transformer (OH) | Failed/Faulted | 24-0079914 | OH | Sus | 0 | CENTRAL VALLEY | JUN | Three Phase Fault | 0 | No | No | No | 1951503 | 0 | EPSS Ckt | Y | 2024 | A-B-C
84033 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 2024-07-01 | 1848 | 20240701 | 2038 | 2501179 | 110 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 743 | 81730 | 37.4963 | -120.0432 | No | Clear;Above 90 |  |  | 24-0082706 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1953394 | 0 | EPSS Ckt | Y | 2024 | A & B INST OC
84053 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 2024-07-04 | 1844 | 20240704 | 2046 | 2505407 | 122 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 37332 | 37.6769 | -119.7776 | No | Clear-Heat Wave;Above 90 | Recloser | Normal | 24-0084099 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954184 | 0 | EPSS Ckt | Y | 2024 | C PHASE- INST OC- DCD
84054 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | FUSE | 4572 | 2024-07-04 | 1848 | 20240706 | 1706 | 2505408 | 2725 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3739 | 261687 | 37.5217 | -119.9394 | No | Clear-Heat Wave;Above 90 | Pole-Wood | Burned/flashed | 24-0084100 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 4630882 | No | No | No | 1954185 | 0 | EPSS Ckt | N | 2024
84056 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 2024-07-04 | 2052 | 20240704 | 2253 | 2505481 | 121 | Distribution Circuit | Company Initiated | Personnel- company | 306 | 31598 | 37.6769 | -119.7776 | No | Clear;Above 90 | Recloser | Normal | 24-0084099 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1954205 | 0 | EPSS Ckt | Y | 2024 | C PHASE- INST OC- DCD
84057 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | SWITCH | 241564 | 2024-07-04 | 2054 | 20240706 | 930 | 2506950 | 2196 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 21 | 5660 | 37.4872 | -119.9618 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0084100 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 27846 | No | No | No | 1954421 | 0 | EPSS Ckt | N | 2024
84076 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | JUMPER | JMPRS 2 POLES SS OF CGC#320400249270 | 2024-07-05 | 2030 | 20240705 | 2114 | 2506592 | 44 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 44 | 37.8531 | -120.3604 | No | Clear-Heat Wave;Above 90 | Other | Burned/flashed | 24-0084451 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1954425 | 0 | EPSS Ckt | N | 2024
84109 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | INTERRUPTER | 128246 | 2024-07-07 | 1540 | 20240707 | 1645 | 2509066 | 65 | Distribution Circuit | Company Initiated | Coordination failure | 31 | 2015 | 37.8399 | -120.228 | No | Clear-Heat Wave;Above 90 | Conductor- Underground | Normal | 24-0084893 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Three Phase Fault | 0 | No | No | No | 1954762 | 0 | EPSS Ckt | N | 2024
84149 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 2024-07-10 | 100 | 20240710 | 233 | 2512023 | 93 | Distribution Circuit | Equipment Failure/Involved | Overhead | 971 | 61143 | 37.8306 | -120.2367 | No | Clear;32-90 F | Regulator | Malfunctioning | 24-0085351 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955448 | 0 | EPSS Ckt | N | 2024 | N/A
84154 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | TRANSFORMER | 321560536095 | 2024-07-10 | 1030 | 20240710 | 1730 | 2512378 | 420 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 420 | 37.4892 | -119.963 | No | Clear;Above 90 | Secondary | Broken | 24-0086036 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1955602 | 0 | EPSS Ckt | N | 2024
84173 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320794354221 | 2024-07-11 | 1659 | 20240712 | 25 | 2514412 | 446 | Transformer only | Equipment Failure/Involved | Overhead | 5 | 2230 | 37.989 | -120.2249 | No | Clear-Heat Wave;32-90 F | Transformer (OH) | Failed/Faulted | 24-0086989 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956063 | 0 | EPSS Ckt | N | 2024
84201 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | RECLOSER | 929360 | 2024-07-13 | 1433 | 20240713 | 1737 | 2516105 | 184 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 2894 | 323922 | 37.4926 | -119.9661 | No | Partly Cloudy-Heat Wave;Above 90 |  |  | 24-0087575 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956492 | 0 | EPSS Ckt | Y | 2024 | GRD
84213 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 2024-07-14 | 738 | 20240714 | 2054 | 2516540 | 796 | Distribution Circuit | Environmental/External | Lightning | 7 | 3102 | 37.1556 | -119.4744 | No | Partly Cloudy-Lightning;32-90 F | Transformer (OH) | Failed/Faulted | 24-0087689 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1956598 | 0 | EPSS Ckt | Y | 2024 | GRD
84233 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320098654405 | 2024-07-17 | 928 | 20240717 | 1013 | 2519294 | 45 | Transformer only | Equipment Failure/Involved | Overhead | 2 | 90 | 37.9949 | -120.466 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0088780 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1957447 | 0 | EPSS Ckt | N | 2024
84258 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 2024-07-22 | 1433 | 20240722 | 1721 | 2523408 | 168 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 306 | 50565 | 37.6769 | -119.7776 | No | Clear;Above 90 |  |  | 24-0090529 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958517 | 0 | EPSS Ckt | Y | 2024 | SGF
84261 | YOSEMITE | YOSEMITE | INDIAN FLAT-1104 | 252691104 | RECLOSER | 5456 | 2024-07-22 | 1902 | 20240722 | 2031 | 2523651 | 89 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 306 | 27234 | 37.6769 | -119.7776 | No | Clear;Above 90 |  |  | 24-0090647 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Ground | 0 | No | No | No | 1958543 | 0 | EPSS Ckt | Y | 2024 | SGF
84292 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | TRANSFORMER | T2324 | 2024-07-26 | 337 | 20240726 | 1315 | 2527133 | 578 | Transformer only | Equipment Failure/Involved | Underground | 7 | 4046 | 37.3418 | -119.7102 | No | Clear;32-90 F | Secondary | Deteriorated | 24-0092230 | UG | Sus | 0 | CENTRAL VALLEY | JUL | Force Out | 0 | No | No | No | 1959621 | 0 | EPSS Ckt | N | 2024
84298 | YOSEMITE | YOSEMITE | OAKHURST-1101 | 254421101 | RECLOSER | 466264 | 2024-07-26 | 1954 | 20240726 | 2155 | 2527945 | 121 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 12463 | 37.3591 | -119.7304 | No | Clear;32-90 F |  |  | 24-0092637 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959859 | 0 | EPSS Ckt | Y | 2024 | BC
84300 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 2024-07-27 | 601 | 20240727 | 1004 | 2528116 | 243 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 513 | 53219 | 37.7155 | -120.2024 | No | Clear;32-90 F |  |  | 24-0092705 | OH | Sus | 0 | CENTRAL VALLEY | JUL | Line to Line | 0 | No | No | No | 1959915 | 0 | EPSS Ckt | Y | 2024 | AB
84370 | YOSEMITE | STANISLAUS | WESTLEY-1103 | 162671103 | JUMPER | 1 E & 5 S/OF OF 20001 | 2024-08-05 | 936 | 20240805 | 1337 | 2534840 | 241 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 241 | 37.5005 | -121.3675 | No | Clear;32-90 F | Pole-Wood | Broken | 24-0095765 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962061 | 0 | EPSS Ckt | N | 2024
84390 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320825849114 | 2024-08-07 | 325 | 20240807 | 340 | 2536136 | 15 | Transformer only | Equipment Failure/Involved | Overhead | 9 | 135 | 37.8488 | -120.2151 | No | Clear;Above 90 | Secondary | Burned/flashed | 24-0096592 | OH | Sus | 31703415 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1962542 | 0 | EPSS Ckt | N | 2024
84402 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2024-08-09 | 323 | 20240810 | 955 | 2538420 | 1832 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 37 | 67784 | 37.9718 | -120.2261 | No | Clear;32-90 F | Insulator | Burned/flashed | 24-0097490 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1963138 | 0 | EPSS Ckt | N | 2024
84441 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | TRANSFORMER | 320773155703 | 2024-08-15 | 1526 | 20240815 | 1551 | 2543095 | 25 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 75 | 38.0295 | -120.233 | No | Clear;32-90 F | Transformer (OH) | Failed/Faulted | 24-0099780 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Force Out | 0 | No | No | No | 1964579 | 0 | EPSS Ckt | N | 2024
84446 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | FUSE | L1413 | 2024-08-16 | 1326 | 20240816 | 1730 | 2543780 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 1972 | 38.0595 | -120.3823 | No | Clear;32-90 F | Transformer (OH) | Broken | 24-0100112 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1964846 | 0 | EPSS Ckt | N | 2024
84541 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 2024-08-29 | 1923 | 20240829 | 2210 | 2555378 | 167 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 513 | 78651 | 37.7155 | -120.2024 | No | Clear;32-90 F |  |  | 24-0105032 | OH | Sus | 0 | CENTRAL VALLEY | AUG | Line to Line | 0 | No | No | No | 1968299 | 0 | EPSS Ckt | Y | 2024 | A&B INSTANT
84574 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-09-04 | 508 | 20240904 | 1206 | 2558879 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 1311 | 292492 | 38.0063 | -120.3474 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0106452 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1969209 | 0 | EPSS Ckt | Y | 2024 | A PH GRD
84577 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | TRANSFORMER | 323122524378 | 2024-09-04 | 1643 | 20240904 | 1858 | 2559599 | 135 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 135 | 37.1654 | -119.4349 | No | Clear;Above 90 | Fuse | Burned Open | 24-0106987 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1969520 | 0 | EPSS Ckt | N | 2024
84659 | YOSEMITE | YOSEMITE | MARIPOSA-2102 | 254452102 | FUSE | 44893 | 2024-09-16 | 806 | 20240916 | 834 | 2569304 | 28 | Distribution Circuit | Animal | Bird found | 1 | 28 | 37.4893 | -119.9629 | No | Partly Cloudy;32-90 F | Conductor- Overhead | Normal | 24-0111351 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1972436 | 0 | EPSS Ckt | N | 2024
84670 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 2024-09-17 | 822 | 20240917 | 943 | s1972807 | 81 | Distribution Circuit | Company Initiated | Personnel- company | 2873 | 192729 | 37.8364 | -120.2605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105710 | OH | Sus | 35465587 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972807 | 0 | EPSS Ckt | Y | 2024 | SGF
84670 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | RECLOSER | 169700 | 2024-09-17 | 822 | 20240917 | 943 | s1972807 | 81 | Distribution Circuit | Company Initiated | Personnel- company | 2873 | 192729 | 37.8364 | -120.2605 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0105710 | OH | Sus | 35465587 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1972807 | 0 | EPSS Ckt | Y | 2024 | SGF
84677 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | OTHER | WIRE DOWN NE OF CGC 100000019375 | 2024-09-18 | 1301 | 20240918 | 1421 | 2571723 | 80 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 76 | 5880 | 37.6024 | -120.1926 | No | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0112553 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | Yes | No | 1973314 | 1 | EPSS Ckt | N | 2024
84679 | YOSEMITE | STANISLAUS | RACETRACK-1704 | 163761704 | TRANSFORMER | 320150054515 | 2024-09-18 | 1611 | 20240919 | 106 | 2571895 | 535 | Transformer only | 3rd Party | Vehicle | 2 | 1070 | 37.9975 | -120.4484 | No | Partly Cloudy;32-90 F | Pole-Wood | Broken | 24-0112753 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Ground | 0 | No | No | No | 1973367 | 0 | EPSS Ckt | N | 2024
84680 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 320884740191 | 2024-09-18 | 1748 | 20240918 | 1917 | 2571965 | 89 | Transformer only | Unknown Cause | Patrol - not conducted | 1 | 89 | 37.6032 | -120.1914 | No | Clear;32-90 F |  |  | 24-0112758 | OH | Sus | 0 | CENTRAL VALLEY | SEP | None | 0 | No | No | No | 1973372 | 0 | EPSS Ckt | N | 2024
84715 | YOSEMITE | STANISLAUS | MIWUK-1701 | 163661701 | RECLOSER | 93062 | 2024-09-24 | 1048 | 20240924 | 1310 | 2576328 | 142 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 166 | 23572 | 38.0205 | -120.2221 | No | Clear;32-90 F |  |  | 24-0114850 | OH | Sus | 0 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | No | No | 1974869 | 0 | EPSS Ckt | Y | 2024 | B & C
84720 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-09-24 | 1745 | 20240925 | 214 | 2576756 | 509 | Distribution Circuit | 3rd Party | Vehicle | 1311 | 299051 | 38.0063 | -120.3474 | No | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0115126 | OH | Sus | 31710024 | CENTRAL VALLEY | SEP | Line to Line | 0 | No | Yes | No | 1974980 | 0 | EPSS Ckt | Y | 2024 | B & C
84755 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | OCB | 1101/2 | 2024-10-01 | 807 | 20241001 | 1314 | 2582011 | 307 | Distribution Circuit | 3rd Party | Other | 2 | 614 | 37.1589 | -119.4057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976818 | 0 | EPSS Ckt | N | 2024 | N/A
84756 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 127906 | 2024-10-01 | 807 | 20241001 | 1314 | 2582084 | 307 | Distribution Circuit | 3rd Party | Other | 7 | 2149 | 37.1556 | -119.4744 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976826 | 0 | EPSS Ckt | Y | 2024 | N/A
84757 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 29336 | 2024-10-01 | 807 | 20241001 | 1314 | 2582086 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1549 | -119.4844 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976828 | 0 | EPSS Ckt | Y | 2024 | N/A
84758 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 222874 | 2024-10-01 | 807 | 20241001 | 1314 | 2582090 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1539 | -119.4886 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976832 | 0 | EPSS Ckt | Y | 2024 | NA
84759 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | RECLOSER | 43806 | 2024-10-01 | 807 | 20241001 | 1314 | 2582094 | 307 | Distribution Circuit | 3rd Party | Other | 3 | 921 | 37.1649 | -119.4385 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976835 | 0 | EPSS Ckt | Y | 2024 | N/A
84760 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | FUSE | BF50039 | 2024-10-01 | 807 | 20241001 | 1314 | 2582254 | 307 | Distribution Circuit | 3rd Party | Other | 4 | 1228 | 37.1679 | -119.4293 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0117650 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1976928 | 0 | EPSS Ckt | N | 2024
84781 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 2024-10-02 | 1406 | 20241002 | 1649 | 2583644 | 163 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 901 | 65309 | 37.6313 | -120.1536 | No | Clear;Above 90 |  |  | 24-0118449 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1977351 | 0 | EPSS Ckt | Y | 2024 | SGF
84820 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 11300 | 2024-10-08 | 1940 | 20241009 | 126 | 2589966 | 346 | Distribution Circuit | Equipment Failure/Involved | Underground | 914 | 277603 | 38.0058 | -120.3473 | No | Clear;32-90 F | Conductor- Underground | Burned/flashed | 24-0120930 | UG | Sus | 31711215 | CENTRAL VALLEY | OCT | Line to Ground | 0 | No | No | No | 1978975 | 0 | EPSS Ckt | Y | 2024 | A GRD
84822 | YOSEMITE | YOSEMITE | SO. CAL EDISON NO. 3-1101 | 258861101 | OCB | 1101/2 | 2024-10-09 | 733 | 20241009 | 1650 | 2590392 | 557 | Distribution Circuit | 3rd Party | Other | 22 | 12254 | 37.1589 | -119.4057 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0121508 | OH | Sus | 0 | CENTRAL VALLEY | OCT | None | 0 | No | No | No | 1979307 | 0 | EPSS Ckt | N | 2024 | NONE
84832 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | TRANSFORMER | 320922849079 | 2024-10-11 | 747 | 20241011 | 810 | 2592028 | 23 | Transformer only | Equipment Failure/Involved | Overhead | 4 | 92 | 37.8474 | -120.1814 | No | Clear;32-90 F | Cutout- fuse holder | Broken | 24-0122088 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Force Out | 0 | No | No | No | 1979658 | 0 | EPSS Ckt | N | 2024
84913 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-10-25 | 712 | 20241025 | 1015 | 2603563 | 183 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 1311 | 161853 | 38.0063 | -120.3474 | No | Clear;32-90 F |  |  | 24-0127686 | OH | Sus | 0 | CENTRAL VALLEY | OCT | Line to Line | 0 | No | No | No | 1983408 | 0 | EPSS Ckt | Y | 2024 | A C
85017 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-11-05 | 2137 | 20241105 | 2303 | 2615002 | 86 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1312 | 109016 | 38.0063 | -120.3474 | Yes | Partly Cloudy;32-90 F | Capacitor | Failed/Faulted | 24-0132293 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1986809 | 0 | EPSS Ckt | Y | 2024 | B
85031 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | RECLOSER | 258550 | 2024-11-08 | 951 | 20241108 | 1319 | 2618940 | 208 | Distribution Circuit | Animal | Squirrel | 2575 | 525926 | 37.8844 | -120.3058 | No | Clear;32-90 F | Conductor- Overhead | Normal | 24-0133532 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1987872 | 0 | EPSS Ckt | Y | 2024 | GRD
85152 | YOSEMITE | STANISLAUS | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 2024-11-22 | 2311 | 20241122 | 2332 | 2635652 | 21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 271 | 5691 | 38.03 | -120.2447 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139344 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Ground | 0 | No | No | No | 1992352 | 0 | EPSS Ckt | Y | 2024 | C- GROUND- INST OC
85160 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9570 | 2024-11-23 | 125 | 20241123 | 216 | 2635739 | 51 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 513 | 25711 | 37.7155 | -120.2024 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139366 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992372 | 0 | EPSS Ckt | Y | 2024 | AB- IOC
85164 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | L2153 | 2024-11-23 | 308 | 20241123 | 535 | 2635785 | 147 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 39 | 5733 | 37.9491 | -120.2657 | No | Overcast-Fog-Heavy Rain;32-90 F |  |  | 24-0139398 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Line to Line | 0 | No | No | No | 1992408 | 0 | EPSS Ckt | N | 2024
85190 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 2024-11-25 | 1244 | 20241125 | 1629 | 2637747 | 225 | Distribution Circuit | 3rd Party | Vehicle | 231 | 48803 | 37.7156 | -120.1933 | No | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0140012 | OH | Sus | 0 | CENTRAL VALLEY | NOV | Three Phase Fault | 0 | No | Yes | No | 1992786 | 0 | EPSS Ckt | N | 2024 | A- B- C
85276 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2024-12-14 | 308 | 20241214 | 548 | 2652908 | 160 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 5920 | 37.9718 | -120.2261 | Yes | Overcast-Drizzle;32-90 F |  |  | 24-0145085 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997388 | 0 | EPSS Ckt | N | 2024
85290 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 2024-12-14 | 730 | 20241214 | 2300 | 2654408 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1312 | 883703 | 38.0063 | -120.3474 | Yes | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145190 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1997497 | 0 | EPSS Ckt | N | 2024 | A GRD
85306 | YOSEMITE | STANISLAUS | CURTIS-1702 | 163351702 | FUSE | 19526 | 2024-12-14 | 807 | 20241214 | 1340 | 2654871 | 333 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 37 | 12321 | 37.9718 | -120.2261 | Yes | Overcast-Heavy Rain-Strong Winds;32-90 F |  |  | 24-0145751 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998083 | 0 | EPSS Ckt | N | 2024
85309 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 2024-12-14 | 810 | 20241214 | 825 | 2654882 | 15 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 231 | 3465 | 37.7156 | -120.1933 | Yes | Overcast-Rain;32-90 F |  |  | 24-0145250 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1997560 | 0 | EPSS Ckt | N | 2024 | A&B TIME OC
85316 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 293732 | 2024-12-14 | 837 | 20241215 | 1845 | 2655481 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 701226 | 37.698 | -120.116 | Yes | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145320 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | No | 1997633 | 0 | EPSS Ckt | N | 2024 | A TIME OC
85340 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | TRANSFORMER | 320931546268 | 2024-12-14 | 1242 | 20241215 | 1458 | 2659640 | 1576 | Transformer only | Vegetation | Tree - fell into line | 2 | 3152 | 37.7731 | -120.1784 | Yes | Overcast-Fog-Rain;32-90 F | Transformer (OH) | Broken | 24-0145783 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998114 | 0 | EPSS Ckt | N | 2024
85346 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 21160 | 2024-12-14 | 1406 | 20241215 | 1515 | 2658466 | 1509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 34969 | 37.7156 | -120.1933 | Yes | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145784 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | Yes | Yes | 1998115 | 0 | EPSS Ckt | N | 2024 | NA
85348 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4629 | 2024-12-14 | 1535 | 20241215 | 1418 | 2659965 | 1363 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 58 | 79054 | 37.7103 | -120.111 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0146304 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Three Phase Fault | 0 | No | No | No | 1998675 | 0 | EPSS Ckt | N | 2024 | NA
85350 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4609 | 2024-12-14 | 1539 | 20241215 | 1431 | 2661706 | 1372 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 71344 | 37.7119 | -120.0982 | Yes | Overcast-Fog-Rain;32-90 F |  |  | 24-0146335 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998704 | 0 | EPSS Ckt | N | 2024 | NA
85352 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321472539107 | 2024-12-14 | 1621 | 20241215 | 1412 | 2660079 | 1311 | Transformer only | Unknown Cause | Patrol - found nothing | 1 | 1311 | 37.5715 | -119.9926 | Yes | Overcast-Rain;32-90 F |  |  | 24-0146204 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1998553 | 0 | EPSS Ckt | N | 2024
85359 | YOSEMITE | STANISLAUS | CURTIS-1704 | 163351704 | RECLOSER | L1413 | 2024-12-14 | 2334 | 20241215 | 1000 | 2660775 | 626 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 28 | 17528 | 38.0595 | -120.3823 | Yes | Partly Cloudy;32-90 F |  |  | 24-0146202 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 1998551 | 0 | EPSS Ckt | N | 2024 | A B
85364 | YOSEMITE | YOSEMITE | MARIPOSA-2101 | 254452101 | JUMPER | WIRE DOWN AT CGC# 321862739465 | 2024-12-15 | 1645 | 20241215 | 2225 | 2661935 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2105 | 37.5821 | -119.8584 | No | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146437 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | Yes | Yes | 1998798 | 0 | EPSS Ckt | N | 2024
85365 | YOSEMITE | YOSEMITE | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 2024-12-16 | 14 | 20241216 | 355 | 2662261 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 906 | 120711 | 37.6313 | -120.1536 | No | Clear;32-90 F | Regulator | Failed/Faulted | 24-0146476 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Multi-Fault | 0 | No | No | No | 1998844 | 0 | EPSS Ckt | N | 2024 | A- C- GRD
85373 | YOSEMITE | YOSEMITE | BEAR VALLEY-2101 | 252192101 | TRANSFORMER | 321323336637 | 2024-12-16 | 1556 | 20241216 | 2234 | 2663390 | 398 | Transformer only | Equipment Failure/Involved | Overhead | 3 | 1194 | 37.5048 | -120.0433 | No | Overcast-Drizzle;32-90 F | Transformer (OH) | Failed/Faulted | 24-0146684 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 1999063 | 0 | EPSS Ckt | N | 2024
85384 | YOSEMITE | STANISLAUS | CURTIS-1705 | 163351705 | TRANSFORMER | 320629652118 | 2024-12-18 | 1406 | 20241218 | 1509 | 2665308 | 63 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 63 | 37.9311 | -120.2828 | No | Partly Cloudy;32-90 F | Fuse | Failed/Faulted | 24-0147007 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Force Out | 0 | No | No | No | 1999650 | 0 | EPSS Ckt | N | 2024
85401 | YOSEMITE | YOSEMITE | COARSEGOLD-2104 | 254432104 | FUSE | 10557 | 2024-12-21 | 107 | 20241221 | 545 | 2667145 | 278 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 5 | 1390 | 37.2799 | -119.6664 | No | Partly Cloudy;32-90 F |  |  | 24-0147284 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000196 | 0 | EPSS Ckt | N | 2024
85409 | YOSEMITE | STANISLAUS | CURTIS-1703 | 163351703 | FUSE | 20419 | 2024-12-22 | 1323 | 20241222 | 2243 | 2667787 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 8687 | 37.8258 | -120.2347 | No | Partly Cloudy;32-90 F | Pole-Wood | Burned/flashed | 24-0147397 | OH | Sus | 0 | CENTRAL VALLEY | DEC | Line to Line | 0 | No | No | No | 2000381 | 0 | EPSS Ckt | N | 2024
85417 | YOSEMITE | STANISLAUS | PEORIA FLAT-1701 | 163781701 | TRANSFORMER | 320384049368 | 2024-12-24 | 549 | 20241224 | 1045 | 2668831 | 296 | Transformer only | Equipment Failure/Involved | Overhead | 1 | 296 | 37.8564 | -120.3681 | No | Overcast-Rain;32-90 F | Jumper | Broken | 24-0147580 | OH | Sus | 46438600 | CENTRAL VALLEY | DEC | Line to Ground | 0 | No | No | No | 2000633 | 0 | EPSS Ckt | N | 2024

## Notes
Question
1b | 1b based off a 1/27/23 snapshot of the HFTD structures, their plat map, and the plat map's consequence ranking in the 2023 WMP.
Plat map ranking methodology is as of 12/23/22.
1c through 1f | These are outages from Jan 1, 2023 to Dec 31, 2024, that occurred within PG&E’s High, Severe, and Extreme plat maps as defined in the 2023 WMP.
Query performed 7/16/25